## (AR) BOQ View (Working)
BOQ
Work Master Code | Gauge Code | Work Group |  |  | Spec. 1 | Spec. 2 | Spec. 3 | Spec. 4 | Spec. 5 | Spec. 6 | Additional Spec. | Reference to | UoM | Total | 861 | [35 empty] | 862 |  |  |  | 863 | [12 empty] | 869 | [5 empty] | 870
|  | W/G(대) | W/G(중) | W/G(소) | [10 empty] | Central Control Building | Laboratory & Inspection Building | Central Maintenance Building | 230KV GIS Main Receiving Substation | Main Substation 01 | EDG Building - MS01 | Chemical Storage Shelter - Utilities | Smoking Shelter - CCB | Parking Sunshade - CCB (1) | Parking Sunshade - Laboratory | Parking Sunshade - OME05 | Parking Sunshade - Maint BD (1) | Parking Sunshade - Maint BD (2) | Parking Sunshade - CCB (2) | Parking Sunshade - CCB (3) | Parking Sunshade - CCB (4) | Parking Sunshade - GIS01 | Parking Sunshade - MS01 | Flare RIO Shelter | Burn Pit RIO Shelter | Evaporation Pond RIO Shelter | Custody Metering RIO Shelter | Aquifer Well A RIO Shelter | Main Substation 02 | EDG Building - Substation 6 | EDG Building - Substation 8 | EDG Building - Facility Security | Chemical Storage Shelter - Exports | Smoking Shelter - LAB01 | Smoking Shelter - Maintenance BD | Smoking Shelter - Sulfur Loading | Smoking Shelter - OME 03 | Smoking Shelter - OME 04 | Smoking Shelter - OME 05 | Aquifer Well B RIO Shelter | EDG Building - Substation 9 | Substation 07 - Utilities | PIB 07 - Utilities | Parking Sunshade - Utilities Area | EDG Building - Substation-07 | OME Building 03 - Import | Substation 06 - Export Area | Substation 09 - Import Area | PIB 06 - Export Area | PIB 09 - Import Area | Chemical Storage Shelter - Import | Parking Sunshade - OME04 | Parking Sunshade - OME03 | Parking Sunshade - PIB06 | Parking Sunshade - PIB09 | Propane Storage Shelter | OME Building 04 - Export | OME Building 05 - Utilities | PIB 03 - SRU/TGTU Train 1 | Parking Sunshade - PIB03 | Parking Sunshade - PIB04 | Parking Sunshade - PIB05 | PIB 04 - SRU/TGTU Train 2 | PIB 05 - SRU/TGTU Train 3 | Sulfur Loading Control Building | Parking Sunshade - Sulfur Loading | SL Drivers Welfare Building | Sulfur Loading Arm Shelter
[15 empty] | 902.10.01 | 905.10.17 | 905.10.18 | 901.10.01 | 901.10.02 | 901.10.04 | 905.10.36 | 905.10.19 | 905.10.22 | 905.10.26 | 905.10.27 | 905.10.28 | 905.10.29 | 905.10.23 | 905.10.24 | 905.10.25 | 905.10.30 | 905.10.31 | 861.90.01 | 861.90.02 | 861.90.03 | 861.90.04 | 861.90.05 | 901.10.02 | 901.10.04 | 901.10.04 | 901.10.04 | 905.10.36 | 905.10.19 | 905.10.19 | 905.10.19 | 905.10.19 | 905.10.19 | 905.10.19 | 861.90.05 | 901.10.04 | 862.90.01 | 862.90.03 | 905.10.34 | 862.90.02 | 905.10.08 | 863.90.01 | 863.90.02 | 863.90.05 | 863.90.06 | 905.10.10 | 905.10.12 | 905.10.11 | 905.10.13 | 905.10.14 | 863.90.07 | 905.10.08 | 905.10.08 | 869.90.01 | 905.10.01 | 905.10.02 | 905.10.03 | 869.90.01 | 869.90.01 | 870.90.01 | 905.10.05 | 905.10.04 | 870.90.03
[15 empty] | 861-B-6105 | 861-B-6107 | 861-B-6120 | 861-B-6130A | 861-B-6130B | 861-B-6131A | 861-B-6170A | 861-B-6172A | 861-B-6174E | 861-B-6174F | 861-B-6174G | 861-B-6174H | 861-B-6174I | 861-B-6174V | 861-B-6174W | 861-B-6174X | 861-B-6174Y | 861-B-6174Z | 861-B-6173A | 861-B-6173B | 861-B-6173C | 861-B-6173D | 860-B-6073A | 861-B-6130C | 863-B-6331A | 870-B-7031A | 861-B-6131B | 863-B-6370A | 861-B-6172B | 861-B-6172C | 870-B-7072 | 863-B-6372B | 863-B-6372A | 861-B-6172D | 860-B-6073B | 863-B-6331B | 862-B-6230 | 862-B-6250 | 862-B-6274A | 862-B-6231 | 863-B-6300B | 863-B-6330A | 863-B-6330B | 863-B-6350A | 863-B-6350B | 863-B-6370B | 863-B-6374A | 863-B-6374B | 863-B-6374C | 863-B-6374D | 863-B-6373 | 863-B-6300A | 862-B-6200 | 869-B-6950A | 869-B-6974A | 869-B-6974B | 869-B-6974C | 869-B-6950B | 869-B-6950C | 870-B-7005 | 870-B-7074A | 870-B-7088 | 870-B-7073
[15 empty] | 36350.56 | 1761.68
[14 empty] | 4125.646 | 3987.212 | 138.434
[14 empty] | 38112.24 | 5126.96 | 1761.82 | 1670.84 | 8060.46 | 2559.26 | 204.41 | 59.75 | 22.43 | 13.97 | 18.51 | 12.22 | 18.51 | 18.51 | 12.22 | 3.49 | 3.49 | 5.24 | 6.99 | 46.17 | 36.72 | 37.27 | 41.91 | 38.52 | 2525.03 | 203.58 | 201.67 | 255.25 | 59.75 | 22.43 | 22.43 | 22.43 | 22.43 | 22.43 | 22.43 | 38.52 | 203.33 | 1162.2 | 900.1 | 14.51 | 263.94 | 1288.7 | 1383.68 | 1362.87 | 734 | 774.31 | 66.44 | 6.99 | 21.6 | 12.35 | 6.17 | 447.26 | 1288.48 | 1279.96 | 619.18 | 6.17 | 6.17 | 6.17 | 619.18 | 619.18 | 1201.49 | 24.69 | 80.68 | 514.39
[14 empty] | 1388.667 | 46.174 | 7.496 | 603.351 | 141.024 | 11.626 | 0.798 | 14.293 | 1.957 | 17.649 | 5.496 | 13.25 | 5.496 | 5.496 | 15.557 | 3.374 | 3.374 | 5.81 | 7.762 | 7.466 | 5.195 | 5.195 | 6.785 | 5.51 | 11.626 | 0.798 | 0.798 | 0.906 | 14.293 | 1.957 | 1.957 | 1.957 | 1.957 | 1.957 | 1.957 | 5.51 | 0.798 | 1.018 | 0.22 | 3.649 | 1.711 | 5.402 | 1.173 | 0.6 | 0.22 | 0.22 | 15.115 | 7.555 | 6.35 | 3.504 | 1.704 | 83.623 | 5.402 | 5.402 | 0.22 | 1.704 | 1.704 | 1.704 | 0.22 | 0.22 | 0.22 | 7.395 | 0.109 | 245.698
[14 empty] | 4125.646 | 697.797 | 163.192 | 114.681 | 998.991 | 197.949 | 18.624 | 3.107 | 1.32 | 1.525 | 1.537 | 1.335 | 1.537 | 1.537 | 1.335 | 0.381 | 0.381 | 0.572 | 0.763 | 3.09 | 2.535 | 2.639 | 2.836 | 10.543 | 281.259 | 18.43 | 18.695 | 33.518 | 3.107 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 10.543 | 18.677 | 121.216 | 82.049 | 1.235 | 27.587 | 155.825 | 149.114 | 158.729 | 62.225 | 67.466 | 3.385 | 0.763 | 1.793 | 1.025 | 0.512 | 32.429 | 167.938 | 147.692 | 51.003 | 0.512 | 0.512 | 0.512 | 51.003 | 51.003 | 126.209 | 2.049 | 6.34 | 35.164 | 0 | 0
[14 empty] | 10.82% | 13.61% | 9.263% | 6.864% | 12.39% | 7.735% | 9.111% | 5.2% | 5.885% | 10.92% | 8.304% | 10.92% | 8.304% | 8.304% | 10.92% | 10.92% | 10.92% | 10.92% | 10.92% | 6.693% | 6.904% | 7.081% | 6.767% | 27.37% | 11.14% | 9.053% | 9.27% | 13.13% | 5.2% | 5.885% | 5.885% | 5.885% | 5.885% | 5.885% | 5.885% | 27.37% | 9.186% | 10.43% | 9.116% | 8.511% | 10.45% | 12.09% | 10.78% | 11.65% | 8.478% | 8.713% | 5.095% | 10.92% | 8.301% | 8.3% | 8.298% | 7.251% | 13.03% | 11.54% | 8.237% | 8.298% | 8.298% | 8.298% | 8.237% | 8.237% | 10.5% | 8.299% | 7.858% | 6.836%
A01ZZ001-00004 |  | Earth Work | - | Excavation | Soil, Mech. | D ≤ 2.0M | [5 empty] | A-01 | M3 | 39524.63 | 4726.58 | 1468.7 | 2367.18 | 7579.9 | 3239.99 | 237.23 | 103.21 | 28.49 | 49.6 | 51.41 | 43.4 | 51.41 | 51.41 | 43.4 | 12.4 | 12.4 | 18.6 | 24.8 | 50.38 | 41.74 | 44.47 | 45.72 | 43.79 | 2925.33 | 232.62 | 233.55 | 277.06 | 103.21 | 28.49 | 28.49 | 28.49 | 28.49 | 28.49 | 28.49 | 43.79 | 232.97 | 1152.11 | 802.68 | 65.28 | 298.71 | 1135.73 | 1454.29 | 1410.59 | 645.24 | 661.35 | 94.66 | 24.8 | 59.98 | 34.27 | 17.14 | 1208.17 | 1135.49 | 1135.49 | 525.88 | 17.14 | 17.14 | 17.14 | 525.88 | 525.88 | 918.38 | 68.54 | 95.62 | 921.37
A01ZZ001-00005 |  | Earth Work | - | Excavation | Soil, Mech. | 2.0M < D ≤ 4.0M | [5 empty] | A-01 | M3 | 9278.79 | 2159.71 |  | 0.67 | 5938.07 | 200.95 | 2.03 | [17 empty] | 185.31 | 2.03 | 2.03 | [9 empty] | 2.03 | 29.51 | 21.5 | 17.95 |  |  | 331.75 | 13.75 | 189.58 | 24 | [8 empty] | 20 |  |  |  | 20 | 20 | 1.26 |  |  | 96.66
A01ZZ003-00001 |  | Earth Work | - | Backfill | Re-use, Soil | [5 empty] | - General Fill as defined in SAES-A-114 - Compaction: Min. 90% of Max.Modified Proctor Density or Min. 70% of Relative Density | A-02, A-03 | M3 | 20280.65 | 1988.62 | 417.24 | 831.02 | 7570.16 | 1659.4 | 73.82 | 13.9 |  | 34.46 | 30.77 | 30.16 | 30.77 | 30.77 | 30.16 | 8.62 | 8.62 | 12.92 | 17.23 | 1.89 | 4.03 | 5.91 | 1.89 | 3.77 | 1405.51 | 73.24 | 73.58 | 86.76 | 13.9 | [6 empty] | 3.77 | 73.38 | 490.05 | 324.89 | 67.31 | 91.62 | 440.79 | 612.73 | 599.57 | 247.44 | 237.29 | 15.44 | 17.23 | 35.9 | 20.51 | 10.26 | 203.1 | 440.72 | 448.73 | 201.29 | 10.26 | 10.26 | 10.26 | 201.29 | 201.29 | 355.8 | 41.02 | 33.13 | 376.2
A01ZZ003-00003 | A | Earth Work | - | Backfill | Purchased, Soil | [5 empty] | - Selected Fill as defined in SAES-A-114 - Compaction: Min. 95% of Max.Modified Proctor Density or Min. 85% of Relative Density - Generally THK 150mm under SOGs and Tie Girders |  | M3 | 1580.55 | [36 empty] | 178.2 |  |  |  | 236.31 | 222.87 | 219.33 | [8 empty] | 236.31 | 236.31 | [6 empty] | 251.22
A01ZZ003-00003 | B | Earth Work | - | Backfill | Purchased, Soil | [5 empty] | - Controlled Low-Strength Material (CLSM) |  | M3 | 1629.93 | 963.93 | [35 empty] | 29 | 20 |  |  |  | 331 | 13 | 189 | 24 | [8 empty] | 20 |  |  |  | 20 | 20
A01ZZ004-00001 |  | Earth Work | - | Disposal | Soil | [5 empty] | - Disposal Distance from Site to be defined at Construction stage | A-04 | M3 | 27805.89 | 3933.74 | 1045.09 | 1489.42 | 6322.05 | 1782.74 | 155.4 | 89.31 | 28.49 | 15.14 | 20.64 | 13.24 | 20.64 | 20.64 | 13.24 | 3.78 | 3.78 | 5.68 | 7.57 | 48.59 | 37.97 | 38.55 | 43.83 | 40.01 | 1706.38 | 153.86 | 153.28 | 178.33 | 89.31 | 28.49 | 28.49 | 28.49 | 28.49 | 28.49 | 28.49 | 40.01 | 151.86 | 691.89 | 498.68 | 15.92 | 187.29 | 695.3 | 1173.7 | 825.12 | 586.67 | 447.73 | 79.22 | 7.57 | 24.08 | 13.76 | 6.88 | 999.95 | 695.13 | 687.13 | 344.3 | 6.88 | 6.88 | 6.88 | 344.3 | 344.3 | 565 | 27.52 | 62.51 | 637.79
A01ZZ009-00001 |  | Earth Work | - | Crushed Stone | [6 empty] | - DIA=25mm~60mm, for TR Area in Substations |  | M3 | 241.1 |  |  |  |  | 102.3 | [18 empty] | 102.3 | [12 empty] | 9.7 |  |  |  |  | 15.4 | 11.4
A01ZZ011-00001 |  | Earth Work | - | Anti Termite Treatment | [6 empty] | - for Buildings and Shelters |  | M2 | 33427.32 | 4029.63 | 2141.2 | 4211.82 | 4647.27 | 1050 | 130 | 100 | 24.01 | [10 empty] | 48 | 28.32 | 28.32 | 40.32 | 32.64 | 1050 | 130 | 130 | 180 | 100 | 24.01 | 24.01 | 24.01 | 24.01 | 24.01 | 24.01 | 32.64 | 130 | 975.38 | 907.2 |  | 180 | 1173 | 1125.38 | 1125.38 | 760.32 | 823.2 | 100 |  |  |  |  | 1412.09 | 1173 | 1173 | 587.6 |  |  |  | 587.6 | 587.6 | 1240.2 |  | 57.5 | 1030.64
A01ZZ012-00001 |  | Earth Work | - | PE Sheet (Vapor Barrier) | [6 empty] | - THK=0.25mm - under SOGs (Grade Slab, Walkway, Ramp, Stoop) | A-05 | M2 | 61013.8 | 6453.08 | 3057.51 | 5658.28 | 13720.84 | 2421.3 | 297.81 | 224.65 | 72.66 | [10 empty] | 65.53 | 44.12 | 45.37 | 56.25 | 48.46 | 2264.89 | 304.15 | 299.68 | 399.32 | 224.65 | 72.66 | 72.66 | 72.66 | 72.66 | 72.66 | 72.66 | 48.46 | 295.29 | 1691.51 | 1515.5 |  | 330.44 | 1931.26 | 2128.45 | 2078.27 | 1296.08 | 1359.95 | 225.75 |  |  |  |  | 1657.26 | 1930.08 | 1930.08 | 1017.13 |  |  |  | 1017.13 | 1017.13 | 2020.87 |  | 184.27 | 1244.38
A03AD029-00003 |  | Concrete Work | Substructure Work | Anchor Bolt (Installation only) | M20 | [5 empty] | - L=460mm | J-02 | EA | 936 |  | 0 | 320 | 112 |  |  | 40 | [11 empty] | 48 | 48 | 48 | 48 | 48 |  |  |  |  | 40 | [6 empty] | 48 | [5 empty] | 32 |  |  |  |  | 40 | [5 empty] | 32 | 32
A03AD029-00005 |  | Concrete Work | Substructure Work | Anchor Bolt (Installation only) | M24 | [5 empty] | - L=530mm | J-02 | EA | 812 | [8 empty] | 64 | 48 | 56 | 48 | 48 | 56 | 16 | 16 | 24 | 32 | [13 empty] | 16 | 16 | 16 |  |  |  |  | 32 | [7 empty] | 32 | 56 | 32 | 16 | 68 |  |  |  | 16 | 16 | 16 |  |  |  | 64 |  | 8
A03AD029-00006 |  | Concrete Work | Substructure Work | Anchor Bolt (Installation only) | M30 | [5 empty] | - L=620mm | J-02 | EA | 24 |  |  | 24
A03AD029-00008 |  | Concrete Work | Substructure Work | Anchor Bolt (Installation only) | M36 | [5 empty] | - L=720mm |  | EA | 216 | [50 empty] | 72 | [11 empty] | 144
A03AD029-00017 |  | Concrete Work | Substructure Work | Anchor Bolt (Installation only) | M27 | [5 empty] | - L=570mm |  | EA | 64 |  |  | 64
A03AD030-00002 |  | Concrete Work | Substructure Work | Chemical Anchor Bolt | Including injected Chemical material | M12 | [6 empty] | EA | 1934 |  |  |  |  | 216 | 128 | [17 empty] | 216 | 128 | 128 | [9 empty] | 128 | 222 |  |  | 144 |  | 356 | 268
A03AD032-00006 |  | Concrete Work | Substructure Work | Structural Concrete | Cement Type-5 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa |  |  |  |  | - F'c=35MPa - Cement Type-5 |  | M3 | 18459.22 | 2239.88 | 882.31 | 1370.85 | 3578.9 | 1609.05 | 97.2 | 59.75 | 22.43 | 13.97 | 18.51 | 12.22 | 18.51 | 18.51 | 12.22 | 3.49 | 3.49 | 5.24 | 6.99 | 46.17 | 36.72 | 37.27 | 41.91 | 38.52 | 688.63 | 97.26 | 98.19 | 105.7 | 59.75 | 22.43 | 22.43 | 22.43 | 22.43 | 22.43 | 22.43 | 38.52 | 97.01 | 506.6 | 391.28 | 14.51 | 112.01 | 532.5 | 637.96 | 611.04 | 326.76 | 345.29 | 66.44 | 6.99 | 21.6 | 12.35 | 6.17 | 368.74 | 532.28 | 524.28 | 270.52 | 6.17 | 6.17 | 6.17 | 270.52 | 270.52 | 531.42 | 24.69 | 50.25 | 512.24
A03AD034-00004 |  | Concrete Work | Substructure Work | Lean Concrete (including Form work) | Cement Type-1 | 10MPa < F'c (Cylinder Strength) ≤ 20MPa |  |  |  |  | - F'c=14MPa - Cement Type-1 | B-02 | M3 | 2831.88 | 352.93 | 171.09 | 300.51 | 368.96 | 147.31 | 15.27 | 11.22 | 3.63 | 1.6 | 2.45 | 1.4 | 2.45 | 2.45 | 1.4 | 0.4 | 0.4 | 0.6 | 0.8 | 3.27 | 2.2 | 2.27 | 2.81 | 2.42 | 99.04 | 15.62 | 15.6 | 18.81 | 11.22 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 2.42 | 15.18 | 83 | 75.77 | 1.63 | 16.88 | 96.6 | 104.89 | 101.96 | 64.82 | 68 | 12.36 | 0.8 | 2.86 | 1.63 | 0.82 | 78.82 | 96.54 | 96.54 | 50.85 | 0.82 | 0.82 | 0.82 | 50.85 | 50.85 | 100.74 | 3.26 | 9.21 | 62.23
A03AD035-00001 |  | Concrete Work | Substructure Work | Form Work (3 times in use) | Flat Form | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [5 empty] | B-03 | M2 | 33917.67 | 3331.49 | 761.24 | 1219.64 | 8241.71 | 3716.17 | 291.14 | 131.2 | 48.11 | 44.16 | 34.56 | 38.64 | 34.56 | 34.56 | 38.64 | 11.04 | 11.04 | 16.56 | 22.08 | 60.15 | 54.7 | 59.54 | 56.06 | 56.8 | 1717.43 | 280.2 | 291.14 | 318.52 | 131.2 | 48.11 | 48.11 | 48.11 | 48.11 | 48.11 | 48.11 | 56.8 | 281.66 | 1014.03 | 652.2 | 37.44 | 345.37 | 919.47 | 1336.47 | 1238.38 | 545.02 | 595.77 | 142.53 | 22.08 | 40.32 | 23.04 | 11.52 | 457.68 | 918.85 | 909.53 | 450.97 | 11.52 | 11.52 | 11.52 | 450.97 | 450.97 | 783.56 | 46.08 | 107.34 | 704.12
A03AD036-00001 |  | Concrete Work | Substructure Work | Form Work (1 time in use) | Flat Form | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [6 empty] | M2 | 5085.38 | 218.77 | 201.25 | 57.06 | 439.68 | 1712 | 45.21 | 17.4 |  | 2.88 | 2.16 | 2.52 | 2.16 | 2.16 | 2.52 | 0.72 | 0.72 | 1.08 | 1.44 | 6.72 | 7.4 | 7.7 | 7.02 | 7.32 | 148.89 | 42.82 | 45.21 | 35.37 | 17.4 | [6 empty] | 7.32 | 44.27 | 275.75 | 87.63 | 1.44 | 52.03 | 73.49 | 401.23 | 356.53 | 79.87 | 82.81 | 18 | 1.44 | 2.52 | 1.44 | 0.72 | 30.68 | 72.87 | 72.87 | 64.18 | 0.72 | 0.72 | 0.72 | 64.18 | 64.18 | 154.62 | 2.88 | 16.67 | 18.02
A03AD037-00002 |  | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 400MPa<Fy≤470MPa |  |  |  |  | - Fy=420MPa |  | TON | 1360.391 | 267.483 | -0.006 | 87.467 | 382.939 | 56.327 | 6.777 | 3.039 | 0 | 1.525 | 1.537 | 1.335 | 1.537 | 1.537 | 1.335 | 0.381 | 0.381 | 0.572 | 0.763 | 3.062 | 2.507 | 2.611 | 2.808 | 10.515 | 56.327 | 6.585 | 6.854 | 8.576 | 3.039 | 0 | 0 | 0 | 0 | 0 | 0 | 10.515 | 6.832 | 46.987 | 22.358 | 1.235 | 7.773 | 50.134 | 61.548 | 0.002 | 18.103 | -0.002 | 3.314 | 0.763 | 1.793 | 1.025 | 0.512 | 20.684 | 52.813 | 45.339 | 15.436 | 0.512 | 0.512 | 0.512 | 15.436 | 15.436 | 38.072 | 2.049 | 2.887 | -0.002
A03AD037-00006 |  | Concrete Work | Substructure Work | Rebar Work | Deformed Bar (Epoxy Coat.) | 400MPa<Fy≤470MPa |  |  |  |  | - Fy=420MPa | B-04 | TON | 174.05 |  | 54.97 | [5 empty] | 1.32 | [20 empty] | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | [8 empty] | 55.13 |  | 19.58 | [17 empty] | 35.13
A03AD038-00001 | A | Concrete Work | Substructure Work | Welded Wire Fabric | DIA≤6mm | [5 empty] | - Mesh Size=150x150 - MW18.7xMW18.7 | B-05 | M2 | 33456.09 | 4873.5 |  | 4804.27 | 4680.35 | 1255.26 | 175.16 | 180.42 | 39.19 | [15 empty] | 1255.26 | 175.16 | 175.16 | 255.59 | 180.42 | 39.19 | 39.19 | 39.19 | 39.19 | 39.19 | 39.19 |  | 175.16 | 1242.75 | 1183.65 |  | 236.45 | 1504.41 | 1400.16 |  | 1032.38 |  | 197.64 |  |  |  |  | 1060.92 | 1504.41 | 1504.41 | 802.74 |  |  |  | 802.74 | 802.74 | 1579 |  | 141.65
A03AD038-00001 | C | Concrete Work | Substructure Work | Welded Wire Fabric | DIA≤6mm | [5 empty] | - Mesh Size=150x150 - MW18.7xMW18.7 - Epoxy Coated Type (applicable when Epoxy Coated Rebar is applied) |  | M2 | 5755.75 |  | 2707.19 | [40 empty] | 1376.52 |  | 1091.4 | [17 empty] | 580.64
A03AD043-00001 | A | Concrete Work | Substructure Work | Expansion Joint (w/ Ready-Made Cover) | w/ Flexible Joint Filler, Sealant, Ready-Made Cover Profile w/ Fixing Accessories | [5 empty] | - THK=25mm - for Int. Floor | B-07 | M | 76.8 |  |  |  |  | 15 | [18 empty] | 15 | [12 empty] | 15.6 |  |  |  |  | 15.6 | 15.6
A03AD043-00001 | B | Concrete Work | Substructure Work | Expansion Joint (w/ Ready-Made Cover) | w/ Flexible Joint Filler, Sealant, Ready-Made Cover Profile w/ Fixing Accessories | [5 empty] | - THK=30mm - for Int. Floor | B-07 | M | 144.1 | 56.2 |  |  | 87.9
A03AD044-00001 | A | Concrete Work | Substructure Work | Isolation Joint (Separation Joint) | w/ Flexible Joint Filler, Sealant | [5 empty] | - THK=12mm around SOG | B-06 | M | 11115.99 | 945.81 | 406.05 | 1140.6 | 1353.82 | 330.6 | 150.4 | 86.1 | 19.6 | [15 empty] | 330.6 | 149.28 | 155.14 | 171.37 | 86.1 | 19.6 | 19.6 | 19.6 | 19.6 | 19.6 | 19.6 |  | 160.68 | 329.86 | 430.36 |  | 169.35 | 355.39 | 359.67 | 355.55 | 374.2 | 405.72 | 46.1 |  |  |  |  | 128.66 | 355.39 | 355.39 | 303.45 |  |  |  | 303.45 | 303.45 | 601.95 |  | 72.1 | 262.2
A03AD044-00001 | B | Concrete Work | Substructure Work | Isolation Joint (Separation Joint) | w/ Flexible Joint Filler, Sealant | [5 empty] | - THK=25mm around Equip. Foundation | B-06 | M | 231.32 |  |  |  |  | 50.48 | 14.6 | [17 empty] | 50.48 | 16 | 11.88 | 33.14 | [8 empty] | 16 |  |  |  | 16.14 | [10 empty] | 22.6
A03AD046-00001 | A | Concrete Work | Substructure Work | Water Stop | PVC Type | [5 empty] | - W=200mm (applicable only to GIS Substation) | B-08 | M | 334.02 |  |  |  | 334.02
A03AD046-00001 | B | Concrete Work | Substructure Work | Water Stop | PVC Type | [5 empty] | - W=150mm |  | M | 774.81 |  |  | 63.7 |  |  | 53.91 | [18 empty] | 49.92 | 55.78 | 62.83 | [8 empty] | 61.32 | 49.6 |  |  | 53.91 |  | 90.24 | 81.28 | [7 empty] | 117.12 | [11 empty] | 35.2
A03AD046-00003 |  | Concrete Work | Substructure Work | Water Stop | Expandable Rubber Type | [5 empty] | - Expansible Water Stop (Swelling Waterstop Bar) |  | M | 20.3 |  | 20.3
A03AD049-00001 |  | Concrete Work | Substructure Work | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | Hot-Dip Galvanized Steel | Galv.: ASTM A123 | [6 empty] | TON | 11.78 |  |  |  | 1.628 |  | 1.095 | [18 empty] | 1.121 | 1.121 | 0.534 | [8 empty] | 1.118 | 0.963 |  |  | 0.359 |  | 1.817 | 1.814 | [7 empty] | 0.036 | [11 empty] | 0.174
A03AE032-00004 |  | Concrete Work | Mass Concrete Work | Structural Concrete | Cement Type-1 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ |  |  |  | - F'c=35MPa - Cement Type-1 |  | M3 | 1723.39 |  |  |  |  | 301.08 | [18 empty] | 1153.07 | [12 empty] | 76.74 |  |  |  |  | 86.84 | 92.94 | [16 empty] | 12.72
A03AE034-00004 |  | Concrete Work | Mass Concrete Work | Lean Concrete (including Form work) | Cement Type-1 | 10MPa < F'c (Cylinder Strength) ≤ 20MPa |  |  |  |  | - F'c=14MPa - Cement Type-1 |  | M3 | 61.32 |  |  |  |  | 7.84 | [18 empty] | 48.19 | [12 empty] | 1.52 |  |  |  |  | 1.51 | 1.95 | [16 empty] | 0.31
A03AE035-00001 |  | Concrete Work | Mass Concrete Work | Form Work (3 times in use) | Flat Form | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [6 empty] | M2 | 2912.86 |  |  |  |  | 216.55 | [18 empty] | 2207.4 | [12 empty] | 130.41 |  |  |  |  | 162.72 | 176.56 | [16 empty] | 19.22
A03AE036-00001 |  | Concrete Work | Mass Concrete Work | Form Work (1 time in use) | Flat Form | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [6 empty] | M2 | 1863.54 |  |  |  |  | 68.13 | [18 empty] | 1631.24 | [12 empty] | 53.25 |  |  |  |  | 44.5 | 52.78 | [16 empty] | 13.64
A03AE037-00002 |  | Concrete Work | Mass Concrete Work | Rebar Work | Deformed Bar (Non-Coat.) | 400MPa<Fy≤470MPa |  |  |  |  | - Fy=420MPa |  | TON | 178.632 |  |  |  |  | 42.362 | [18 empty] | 123.202 | [12 empty] | 5.515 |  |  |  |  | 6.842 | 0.005 | [16 empty] | 0.706
A03AE037-00006 |  | Concrete Work | Mass Concrete Work | Rebar Work | Deformed Bar (Epoxy Coat.) | 400MPa<Fy≤470MPa |  |  |  |  | - Fy=420MPa |  | TON | 6.81 | [42 empty] | 6.81
A03AF029-00003 |  | Concrete Work | Superstructure Work | Anchor Bolt (Installation only) | M20 | [5 empty] | - for Crane Girder in OME / Roof PFs in GIS - L=460mm |  | EA | 116 |  | 20 |  | 96
A03AF029-00006 |  | Concrete Work | Superstructure Work | Anchor Bolt (Installation only) | M30 | [5 empty] | - for Roof Truss in CCB - L=620mm |  | EA | 16 | 16
A03AF029-00017 |  | Concrete Work | Superstructure Work | Anchor Bolt (Installation only) | M27 | [5 empty] | - for Crane Girder in GIS - L=570mm |  | EA | 152 |  |  |  | 152
A03AF030-00003 |  | Concrete Work | Superstructure Work | Chemical Anchor Bolt | Including injected Chemical material | M16 | [6 empty] | EA | 1142 | 80 | 48 |  | 256 | 56 | [13 empty] | 8 | 4 | 4 | 8 | 8 | 56 |  |  | 16 | [7 empty] | 8 |  | 36 | 38 |  |  | 62 | 36 | 36 | 38 | 38 | [5 empty] | 10 | 62 | 62 | 36 |  |  |  | 36 | 36 | 40 |  | 16 | 8
A03AF032-00006 |  | Concrete Work | Superstructure Work | Structural Concrete | Cement Type-5 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa |  |  |  |  | - F'c=35MPa - Cement Type-5 | B-01 | M3 | 17747.36 | 2887.08 | 879.51 | 299.99 | 4481.56 | 649.13 | 92.5 | [17 empty] | 683.33 | 92.27 | 92.76 | 124.2 | [8 empty] | 92.27 | 578.86 | 508.82 |  | 124.98 | 756.2 | 658.88 | 658.89 | 407.24 | 429.02 | [5 empty] | 2.08 | 756.2 | 755.68 | 348.66 |  |  |  | 348.66 | 348.66 | 657.35 |  | 30.43 | 2.15
A03AF036-00001 |  | Concrete Work | Superstructure Work | Form Work (1 time in use) | Flat Form | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [5 empty] | B-03 | M2 | 127756.79 | 17240.14 | 6668.61 | 2702.24 | 29782.63 | 4673.38 | 890.55 | [17 empty] | 5129.38 | 887.7 | 893.84 | 1185.28 | [8 empty] | 887.7 | 4546.34 | 4096.68 |  | 1197.59 | 5113.1 | 5150.81 | 5150.99 | 3500.55 | 3674.66 | [5 empty] | 27.62 | 5113.1 | 5111.6 | 2883.31 |  |  |  | 2883.31 | 2883.31 | 5192.02 |  | 261.58 | 28.77
A03AF036-00002 |  | Concrete Work | Superstructure Work | Form Work (1 time in use) | Circular Form | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [6 empty] | M2 | 126.61 | 126.61
A03AF037-00002 |  | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 400MPa<Fy≤470MPa |  |  |  |  | - Fy=420MPa | B-04 | TON | 2393.213 | 430.314 | 108.228 | 27.214 | 616.052 | 99.26 | 11.821 | 0.068 | [11 empty] | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 101.73 | 11.821 | 11.821 | 23.893 | 0.068 | [6 empty] | 0.028 | 11.821 | 68.714 | 59.691 |  | 19.152 | 105.691 | 80.724 | 96.782 | 44.122 | 47.888 | 0.071 |  |  |  |  | 1 | 115.125 | 102.353 | 35.567 |  |  |  | 35.567 | 35.567 | 87.431 |  | 3.453 | 0.036
A03AF041-00001 | A | Concrete Work | Superstructure Work | Expansion Joint (w/ Galvanized Steel Cover) | w/ Flexible Joint Filler, Sealant, Galv. Steel Cover w/ Galv. Steel Angle, Fixing Accessories | [5 empty] | - THK=25mm for Roof Parapet | B-07 | M | 76.8 |  |  |  |  | 15 | [18 empty] | 15 | [12 empty] | 15.6 |  |  |  |  | 15.6 | 15.6
A03AF041-00001 | B | Concrete Work | Superstructure Work | Expansion Joint (w/ Galvanized Steel Cover) | w/ Flexible Joint Filler, Sealant, Galv. Steel Cover w/ Galv. Steel Angle, Fixing Accessories | [5 empty] | - THK=30mm for Roof Parapet | B-07 | M | 144.1 | 56.2 |  |  | 87.9
A03AF041-00001 | C | Concrete Work | Superstructure Work | Expansion Joint (w/ Galvanized Steel Cover) | w/ Flexible Joint Filler, Sealant, Galv. Steel Cover w/ Galv. Steel Angle, Fixing Accessories | [5 empty] | - THK=25mm for Exposed Ceiling | B-07 | M | 76.8 |  |  |  |  | 15 | [18 empty] | 15 | [12 empty] | 15.6 |  |  |  |  | 15.6 | 15.6
A03AF041-00001 | D | Concrete Work | Superstructure Work | Expansion Joint (w/ Galvanized Steel Cover) | w/ Flexible Joint Filler, Sealant, Galv. Steel Cover w/ Galv. Steel Angle, Fixing Accessories | [5 empty] | - THK=30mm for Exposed Ceiling | B-07 | M | 144.1 | 56.2 |  |  | 87.9
A03AF043-00001 | A | Concrete Work | Superstructure Work | Expansion Joint (w/ Ready-Made Cover) | w/ Flexible Joint Filler, Sealant, Ready-Made Cover Profile w/ Fixing Accessories | [5 empty] | - THK=25mm for Int.&Ext. Wall | B-07 | M | 117.7 |  |  |  |  | 28 | [18 empty] | 28 | [12 empty] | 20.5 |  |  |  |  | 20.6 | 20.6
A03AF043-00001 | B | Concrete Work | Superstructure Work | Expansion Joint (w/ Ready-Made Cover) | w/ Flexible Joint Filler, Sealant, Ready-Made Cover Profile w/ Fixing Accessories | [5 empty] | - THK=30mm for Int.&Ext. Wall | B-07 | M | 121.8 | 19.5 |  |  | 102.3
A03AF049-00001 |  | Concrete Work | Superstructure Work | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | Hot-Dip Galvanized Steel | Galv.: ASTM A123 | [6 empty] | TON | 6.958 | 1.013 | 0.092 |  | 3.693 | 0.198 | 0.188 | [17 empty] | 0.198 | 0.188 | 0.188 | 0.192 | [8 empty] | 0.188 | 0.015 | 0.015 |  | 0.188 | 0.158 | 0.015 | 0.015 | 0.015 | 0.015 | [6 empty] | 0.158 | 0.158 | 0.015 |  |  |  | 0.015 | 0.015 | 0.015 |  | 0.008
A03AG032-00006 |  | Concrete Work | Equipment Foundation Work | Structural Concrete | Cement Type-5 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa |  |  |  |  | - F'c=35MPa - Cement Type-5 |  | M3 | 182.27 | [5 empty] | 14.71 | [18 empty] | 14.05 | 10.72 | 25.35 | [8 empty] | 14.05 |  |  |  | 26.95 | [10 empty] | 76.44
A03AG034-00004 |  | Concrete Work | Equipment Foundation Work | Lean Concrete (including Form work) | Cement Type-1 | 10MPa < F'c (Cylinder Strength) ≤ 20MPa |  |  |  |  | - F'c=14MPa - Cement Type-1 | B-02 | M3 | 9.74 | [5 empty] | 0.93 | [18 empty] | 0.9 | 0.7 | 1.15 | [8 empty] | 0.9 |  |  |  | 1.01 | [10 empty] | 4.15
A03AG035-00001 |  | Concrete Work | Equipment Foundation Work | Form Work (3 times in use) | Flat Form | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [5 empty] | B-03 | M2 | 194.13 | [5 empty] | 18.18 | [18 empty] | 18.98 | 15.83 | 32.68 | [8 empty] | 18.98 |  |  |  | 36.4 | [10 empty] | 53.08
A03AG036-00001 |  | Concrete Work | Equipment Foundation Work | Form Work (1 time in use) | Flat Form | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [6 empty] | M2 | 88.65 | [5 empty] | 4.48 | [18 empty] | 4.68 | 3.9 | 8.18 | [8 empty] | 4.68 |  |  |  | 4.87 | [10 empty] | 57.86
A03AG037-00002 |  | Concrete Work | Equipment Foundation Work | Rebar Work | Deformed Bar (Non-Coat.) | 400MPa<Fy≤470MPa |  |  |  |  | - Fy=420MPa |  | TON | 12.55 | [5 empty] | 0.026 | [18 empty] | 0.024 | 0.02 | 1.049 | [8 empty] | 0.024 |  |  |  | 0.662 | [10 empty] | 10.745
A03AH056-00001 |  | Concrete Work | Concrete Protective Coating (U/G) | Bitumen/Bituminous/Asphalt Coating | [6 empty] | - 2 coats, to conform to APCS-3 or 10, or MasterSeal 550 | A-08 | M2 | 63036.33 | 8206.25 | 1836.67 | 2963.46 | 19505.27 | 8014.46 | 337.34 | 39 |  | 67.2 | 74.64 | 58.8 | 74.64 | 74.64 | 58.8 | 16.8 | 16.8 | 25.2 | 33.6 | 4.08 | 8.02 | 8.02 | 4.08 | 4.08 | 7312.19 | 326.32 | 330.6 | 298.47 | 39 | [6 empty] | 4.08 | 329.3 | 1012.61 | 647.2 | 64.16 | 387.24 | 1215.04 | 1250.49 | 1181.18 | 534.54 | 536.14 | 73.44 | 33.6 | 87.08 | 49.76 | 24.88 | 550.78 | 1215.04 | 1215.04 | 426.68 | 24.88 | 24.88 | 24.88 | 426.68 | 426.68 | 806.12 | 99.52 | 85.3 | 540.68
A03AH059-00001 |  | Concrete Work | Concrete Protective Coating (U/G) | Sheet Membrane | Adhesive Rubber Sheet or Bitumen Polyethylene Laminated Waterproofing Membrane | [5 empty] | - THK=4mm, 2-Layers, only for GIS Substation (Q'ty does not mean the total Q'ty of membranes. Q'ty means the required area.) |  | M2 | 11448.29 |  | 4.14 | 516.88 | 2156.92 | 4145.44 | 96.93 | [17 empty] | 3973.79 | 91.39 | 94.58 | [9 empty] | 92.63 |  |  |  | 128.31 | [10 empty] | 147.28
A03AH060-00001 |  | Concrete Work | Concrete Protective Coating (U/G) | Memebrane Protection Board | Bitumen Impregnated Fiberboard | [5 empty] | - THK=15mm - Specific material to be defined during detail eng. |  | M2 | 10213.81 |  | 4.14 | 516.88 | 2140.65 | 3062.73 | 96.93 | [17 empty] | 2891.08 | 91.39 | 94.58 | [9 empty] | 92.63 | 229.69 |  |  | 128.31 |  | 348.58 | 349.72 | [7 empty] | 147.28 | [8 empty] | 19.22
A03AJ058-00001 |  | Concrete Work | Concrete Protective Coating (A/G) | Epoxy Coating (Epoxy Resin Based Coating) | [6 empty] | - 2 coats, to conform to APCS-1B | A-09 | M2 | 3476.94 | 132.04 | 164.29 | 79.92 | 87.32 | 545.6 | 41 | [11 empty] | 41 | [5 empty] | 545.6 | 41 | 41 | 15.27 | [8 empty] | 41 | 315.98 | 43.49 |  | 40.77 | 40.1 | 443.44 | 393.42 | 60 | 43.74 | [6 empty] | 40.1 | 40.1 | 42.87 |  |  |  | 42.87 | 42.87 | 89.88 |  | 22.27
A03AK064-00003 |  | Concrete Work | Precast Concrete Work | PC Slab/Roof Panel | Hollow Core Slab | Including Supply and Install Work w/ All Items to Complete the Work | 150mm<THK≤200mm |  |  |  | [Not Applicable to SACE] - THK=(200)mm for 132kV GIS Substation |  | M3 | 29.76 |  |  |  | 29.76
A04AL069-00001 |  | Finishing Work | Masonry Work | Reinforced Concrete Block | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 50mm<THK≤100mm |  |  |  |  | - THK=100mm |  | M2 | 557.83 | 24.16 | 49.71 | 138.78 | 163.27 | [36 empty] | 53.05 | [10 empty] | 53.05 | 53.05 | [6 empty] | 22.76
A04AL069-00002 | A | Finishing Work | Masonry Work | Reinforced Concrete Block | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 100mm<THK≤200mm |  |  |  |  | - THK=200mm | C-01 | M2 | 23864.95 | 3250.69 | 2146.85 | 5724.24 | 398.73 | 206.57 | 52.78 | 34.56 | [11 empty] | 24.42 | 19.91 | 19.91 | 22.66 | 20.9 | 206.57 | 52.78 | 52.78 | 59.63 | 34.56 | [6 empty] | 20.9 | 52.78 | 209.44 | 763.51 |  | 61.88 | 1827.98 | 232.4 | 232.4 | 724 | 747.4 | 34.8 | [5 empty] | 1827.98 | 1827.98 | 420.17 |  |  |  | 420.17 | 420.17 | 1539.94 |  | 172.51
A04AL069-00002 | B | Finishing Work | Masonry Work | Reinforced Concrete Block | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 100mm<THK≤200mm |  |  |  |  | - THK=200mm - Decorative Concrete Block only for Smoking Shelters |  | M2 | 133.07 | [7 empty] | 19.01 | [20 empty] | 19.01 | 19.01 | 19.01 | 19.01 | 19.01 | 19.01
A04AM077-00001 |  | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | [6 empty] | D-01, D-02 | M2 | 13648.28 | 1249.52 | 1904.66 | 744 |  |  | 57.5 | 34.56 | 15.55 | [10 empty] | 48.84 | 39.82 | 39.82 | 45.32 | 41.8 |  | 57.5 | 57.5 |  | 34.56 | 15.55 | 15.55 | 15.55 | 15.55 | 15.55 | 15.55 | 41.8 | 57.5 |  | 624.94 |  | 67.5 | 1637.01 |  |  | 559.49 | 581.22 | 46.8 | [5 empty] | 1637.01 | 1637.01 | 489.36 |  |  |  | 489.36 | 489.36 | 716.62 |  | 109.05
A04AM077-00002 |  | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint (Textured Type) | [6 empty] | D-01, D-02, D-03 | M2 | 27559.45 | 1545.6 |  |  | 7644.54 | 2895.9 | 328.45 | [17 empty] | 2895.9 | 328.45 | 328.45 | 489.24 | [8 empty] | 328.45 | 1681.73 | 730.25 |  | 361.45 |  | 1978.98 | 1944.06 | 666.93 | 688.34 | [8 empty] | 558.8 |  |  |  | 558.8 | 558.8 | 929.28 |  | 117.05
A04AM078-00001 | A | Finishing Work | Painting Work | Internal Wall Painting | Acrylic Emulsion Paint | [6 empty] | D-01, D-02 | M2 | 54662.1 | 4525.29 | 2804.07 | 8794.02 | 8985.05 | 1545.47 | 359.4 | [17 empty] | 1545.47 | 357.9 | 361.15 | 464.92 | [8 empty] | 359.4 | 1470.07 | 1221.6 |  | 473.05 | 3702.03 | 1644.31 | 1644.31 | 1155.5 | 1184.97 | [6 empty] | 3702.03 | 3702.03 | 816.21 |  |  |  | 816.21 | 816.21 | 2077.87 |  | 133.56
A04AM078-00001 | B | Finishing Work | Painting Work | Internal Wall Painting | Acrylic Emulsion Paint | [5 empty] | - 2-coats of Non-conductive & Fire Retardant White Color Paint - for Telecoms Room or TE Cable Stub-up Area |  | M2 | 2490.77 | 503.74 | 86.33 | 243.06 | 113.29 | [32 empty] | 48.04 | 154.05 |  |  | 120.21 | 48.04 | 48.04 | 139.14 | 149.08 | [6 empty] | 120.21 | 120.21 | 144.54 |  |  |  | 144.54 | 144.54 | 163.71
A04AM078-00004 |  | Finishing Work | Painting Work | Internal Wall Painting | Acid/Alkaline Resistant Paint | [6 empty] | D-01 | M2 | 4830.94 | 417.44 | 707.41 |  | 105.44 | 159.69 |  | 196.8 | [16 empty] | 159.69 |  |  |  | 196.8 | [8 empty] | 170.65 | 407.5 |  |  |  | 219.61 | 219.61 | 349.28 | 373.42 | 196.8 | [7 empty] | 239.25 |  |  |  | 239.25 | 239.25 | 233.05
A04AM078-00005 | A | Finishing Work | Painting Work | Internal Wall Painting | Epoxy Paint | [5 empty] | - under Raised Floor | D-01 | M2 | 1912.6 | 357.29 | 17.06 | 198.46 | 362.11 | [33 empty] | 188.8 | [5 empty] | 169.9 | 179.1 | [8 empty] | 107.14 |  |  |  | 107.14 | 107.14 | 118.46
A04AM079-00001 |  | Finishing Work | Painting Work | Ceiling Painting | Acrylic Emulsion Paint | [6 empty] | D-01, D-02 | M2 | 20326.27 | 1091.29 | 608.43 |  | 4956.42 | 1404.08 | 169 | [17 empty] | 1404.08 | 169 | 169 | 239.31 | [8 empty] | 169 | 1302.2 | 536.44 |  | 234 | 652.23 | 1506.06 | 1506.06 | 487.83 | 505.48 | [6 empty] | 652.23 | 652.23 | 420.58 |  |  |  | 420.58 | 420.58 | 650.16
A04AM079-00004 |  | Finishing Work | Painting Work | Ceiling Painting | Acid/Alkaline Resistant Paint | [6 empty] | D-01 | M2 | 68.92 | [59 empty] | 68.92
A04AM080-00005 |  | Finishing Work | Painting Work | Floor Painting | Anti-Dust Paint | [7 empty] | M2 | 6508.55 | 2343.6 | 25.3 | 243.65 | 977.64 | [33 empty] | 618 | [5 empty] | 495.72 | 555.38 | [8 empty] | 288.9 |  |  |  | 288.9 | 288.9 | 382.56
A04AM080-00006 | A | Finishing Work | Painting Work | Floor Painting | Epoxy Paint | [5 empty] | - Non-slip type | D-01 | M2 | 10621.44 | 216.05 | 167.51 | 285.84 | 1241.07 | 844.22 | 168.24 | 2.74 | 44.26 | [10 empty] | 59.36 | 36.4 | 36.4 | 50.4 | 41.44 | 844.22 | 168.24 | 168.24 | 214.8 | 2.74 | 44.26 | 44.26 | 44.26 | 44.26 | 44.26 | 44.26 | 41.44 | 168.24 | 714.75 | 34.87 |  | 218.01 | 86.09 | 850.45 | 850.45 | 34.87 | 35.03 | 4.24 |  |  |  |  | 1074.77 | 86.09 | 86.09 | 63.32 |  |  |  | 63.32 | 63.32 | 243.24 |  |  | 1045.12
A04AM080-00006 | B | Finishing Work | Painting Work | Floor Painting | Epoxy Paint | [5 empty] | - Non-slip type w/ Epoxy Hardener (for Mech. Room & Workshop) |  | M2 | 9480.13 | 473.49 | 330 | 1671.66 | 3331.89 | 187.5 | [18 empty] | 187.5 | [12 empty] | 229.95 | 187.2 |  |  | 417.99 | 225 | 225 | 187.2 | 180 | [6 empty] | 417.99 | 417.99 | 182.6 |  |  |  | 182.6 | 182.6 | 261.97
A04AM080-00010 |  | Finishing Work | Painting Work | Floor Painting | White Strips for Parking Place | [5 empty] | - W=120mm |  | M | 1152.1 | [8 empty] | 162 | 62.7 | 128.5 | 62.7 | 62.7 | 144 | 24 | 24 | 48 | 77.1 | [20 empty] | 39.9 | [7 empty] | 60 | 68.4 | 34.2 | 17.1 |  |  |  |  | 17.1 | 17.1 | 17.1 |  |  |  | 85.5
A04AM080-00011 |  | Finishing Work | Painting Work | Floor Painting | Chemical Resistant Paint | [7 empty] | M2 | 572 | [6 empty] | 236 | [20 empty] | 236 | [17 empty] | 100
A04AM081-00007 | A | Finishing Work | Painting Work | Skirt Painting | Epoxy Paint | H<150mm |  |  |  |  | - H=100mm | D-01 | M | 4645.29 | 151.92 | 124.7 | 545.6 | 942.92 | 219.4 | 59.5 | [17 empty] | 219.4 | 59 | 59.7 | 66.6 | [8 empty] | 59.5 | 204.85 | 101 |  | 66.5 | 246.2 | 229.05 | 229.05 | 98.8 | 99.7 | [6 empty] | 246.2 | 246.2 | 77.1 |  |  |  | 77.1 | 77.1 | 138.2
A04AM081-00010 |  | Finishing Work | Painting Work | Skirt Painting | Chemical Resistant Paint | H<150mm |  |  |  |  | - H=100mm |  | M | 120 | [6 empty] | 40 | [20 empty] | 40 | [17 empty] | 40
A04AN082-00002 |  | Finishing Work | Tile Work | Wall Tile | Glazed Ceramic Tile | w/ Mortar Bond Coat or Adhesive |  |  |  |  | - Tile Size=W300mm x L300mm x THK9.5mm (Exact size to be defined at Construction stage) | E-01 | M2 | 1619 | 216.35 | 221.69 | 403.27 | [37 empty] | 182.76 | [10 empty] | 182.76 | 182.76 | [6 empty] | 164.44 |  | 64.97
A04AN083-00001 |  | Finishing Work | Tile Work | Floor Tile | Ceramic Tile | Non-Slip Type, w/ Mortar Bond Coat or Adhesive |  |  |  |  | - Tile Size=W300mm x L300mm x THK12.5mm (Exact size to be defined at Construction stage) | E-01 | M2 | 2768.31 | 860.97 | 111.75 | 226.8 | [37 empty] | 500.98 | [10 empty] | 500.98 | 500.98 | [6 empty] | 46.35 |  | 19.5
A04AN083-00002 |  | Finishing Work | Tile Work | Floor Tile | Acid/Alkaline Resistant Tile | Non-Slip Type, w/ Mortar Bond Coat or Adhesive |  |  |  |  | - Tile Size to be defined at Construction stage | E-02 | M2 | 1444.65 | 160.63 | 515.1 |  | 75.63 | 33.58 | [31 empty] | 30.75 | 102 |  |  |  | 50 | 50 | 77.4 | 87.6 | [8 empty] | 66 |  |  |  | 66 | 66 | 63.96
A04AN083-00004 |  | Finishing Work | Tile Work | Floor Tile | Vinyl Tile | w/ Mortar Bond Coat or Adhesive |  |  |  |  | - Tile Size=W300mm x L300mm (Exact size to be defined at Construction stage) | E-03 | M2 | 4380.12 | 875.77 | 955.95 | 1858.95 | [37 empty] | 135.76 | [10 empty] | 135.76 | 135.76 | [6 empty] | 254.54 |  | 27.63
A04AN084-00001 |  | Finishing Work | Tile Work | Skirt Tile | Unglazed Ceramic Tile | w/ Mortar Bond Coat or Adhesive | H<150mm |  |  |  | - H=100mm, Coved Tile | E-01 | M | 2066.61 | 384.77 | 106.84 | 169.74 | [37 empty] | 434.2 | [10 empty] | 434.2 | 434.2 | [6 empty] | 80.06 |  | 22.6
A04AN084-00007 |  | Finishing Work | Tile Work | Skirt Tile | Acid/Alkaline Resistant Tile | w/ Mortar Bond Coat or Adhesive | H<150mm |  |  |  | - H=100mm, Coved Tile | E-02 | M | 689.03 | 52.13 | 187.6 |  | 36.1 | 22.8 | [18 empty] | 22.8 | [12 empty] | 23 | 56 |  |  |  | 29.8 | 29.8 | 47.8 | 51.2 | [8 empty] | 33 |  |  |  | 33 | 33 | 31
A04AN084-00013 |  | Finishing Work | Tile Work | Skirt Tile | Vinyl Tile | w/ Mortar Bond Coat or Adhesive | H<150mm |  |  |  | - H=100mm, Coved Type | E-04 | M | 4490.08 | 679.07 | 746.3 | 1215.23 | 251.22 | [33 empty] | 173.2 |  |  | 137.3 |  |  | 154.3 | 163.5 | [6 empty] | 137.3 | 137.3 | 98.34 |  |  |  | 98.34 | 98.34 | 359.54 |  | 40.8
A04AP085-00001 | A | Finishing Work | Waterproofing Work | Liquid Waterproofing | for Internal Floor Area | Min. 2 Coats | [5 empty] | F-01 | M2 | 644.87 | 77.35 | 76.86 | 157.42 | [37 empty] | 93.3 | [10 empty] | 93.3 | 93.3 | [6 empty] | 33.84 |  | 19.5
A04AP085-00001 | B | Finishing Work | Waterproofing Work | Liquid Waterproofing | for Internal Floor Area | Min. 2 Coats |  |  |  |  | - only for GIS Substation - Cementitious Elastomeric Impermeable Membrane |  | M2 | 1876.34 |  |  |  | 1876.34
A04AP085-00002 | A | Finishing Work | Waterproofing Work | Liquid Waterproofing | for Internal Wall Area | Min. 2 Coats | [5 empty] | F-01 | M2 | 1252.77 | 167.76 | 185.04 | 172.48 | [37 empty] | 182.76 | [10 empty] | 182.76 | 182.76 | [6 empty] | 131.81 |  | 47.4
A04AP085-00002 | B | Finishing Work | Waterproofing Work | Liquid Waterproofing | for Internal Wall Area | Min. 2 Coats |  |  |  |  | - only for GIS Substation - Cementitious Elastomeric Impermeable Membrane |  | M2 | 1760.17 |  |  | 148.03 | 1612.14
A04AQ038-00001 |  | Finishing Work | Roof Work | Welded Wire Fabric | DIA≤6mm | [5 empty] | - Mesh Size=150x150 - MW9xMW9 | B-05 | M2 | 26282.62 | 4032.44 | 2046.57 |  | 4647.27 | 1050 | 134.64 | [17 empty] | 1050 | 134.64 | 134.64 | 185.44 | [8 empty] | 134.64 | 994.5 | 922.14 |  | 185.44 | 1191.56 | 1147.5 | 1147.5 | 773.9 | 837.4 | [6 empty] | 1191.56 | 1191.56 | 600.96 |  |  |  | 600.96 | 600.96 | 1286.4 |  | 60
A04AQ086-00002 | A | Finishing Work | Roof Work | Roof Screed | Light-Weight Concrete Screed | w/o Welded Wire Fabric | 50mm≤Min. THK<75mm |  |  |  | - Min. THK=50mm, Slope=2% | G-03 | M3 | 5757.97 | 1250.06 | 528.59 |  | 973.38 | 210 | 20.2 | [17 empty] | 210 | 20.2 | 20.2 | 31.52 | [8 empty] | 20.2 | 275.41 | 147.55 |  | 53.78 | 202.57 | 229.51 | 229.51 | 123.83 | 133.98 | [6 empty] | 202.57 | 202.57 | 96.16 |  |  |  | 96.16 | 96.16 | 373.06 |  | 10.8
A04AQ088-00004 |  | Finishing Work | Roof Work | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation | 100mm≤THK |  |  |  |  | - THK=120mm - Polyisocyanurate Foam(or equivalent) w/ R-30 | G-02 | M2 | 26282.62 | 4032.44 | 2046.57 |  | 4647.27 | 1050 | 134.64 | [17 empty] | 1050 | 134.64 | 134.64 | 185.44 | [8 empty] | 134.64 | 994.5 | 922.14 |  | 185.44 | 1191.56 | 1147.5 | 1147.5 | 773.9 | 837.4 | [6 empty] | 1191.56 | 1191.56 | 600.96 |  |  |  | 600.96 | 600.96 | 1286.4 |  | 60
A04AQ096-00001 | A | Finishing Work | Roof Work | Metal Coping for Parapet | Galvanized Steel Coping | w/ Fixing Accessories, Sealant |  |  |  |  | - THK=1mm, W=150mm |  | M2 | 1186.23 | 77.28 | 69.86 |  | 175.51 | 59.5 | 16.1 | [17 empty] | 59.5 | 16.1 | 16.1 | 19.6 | [8 empty] | 16.1 | 56.86 | 45.29 |  | 18.9 | 52.5 | 63.86 | 63.86 | 40.53 | 42.91 | [6 empty] | 52.5 | 52.5 | 34.79 |  |  |  | 34.79 | 34.79 | 54.32 |  | 12.18
A04AQ096-00001 | B | Finishing Work | Roof Work | Metal Coping for Parapet | Galvanized Steel Coping | w/ Fixing Accessories, Sealant |  |  |  |  | - THK=1mm, W=325mm |  | M2 | 98.59 | 29.79 |  |  | 28.57 | 7.95 | [18 empty] | 7.95 | [12 empty] | 8.11 |  |  |  |  | 8.11 | 8.11
A04AQ097-00001 |  | Finishing Work | Roof Work | Flashing along Roof Corner | Galvanized Steel Flashing | w/ Fixing Accessories, Sealant |  |  |  |  | - THK=Min. 0.7mm, H=600/700/800/900mm |  | M2 | 2497.81 | 299.88 | 179.68 |  | 397.4 | 139.2 | 28.59 | [17 empty] | 139.2 | 28.59 | 28.59 | 32.88 | [8 empty] | 28.59 | 115.11 | 76.92 |  | 33.42 | 89.4 | 127.11 | 127.11 | 68.76 | 72.84 | [6 empty] | 89.4 | 89.4 | 58.98 |  |  |  | 58.98 | 58.98 | 108.64 |  | 20.16
A04AQ310-00001 |  | Finishing Work | Roof Work | Waterproofing Membrane | EPDM(or Equivalent) | w/ Accessories |  |  |  |  | - THK=1.52mm, Single Ply | G-01 | M2 | 28426.81 | 4268.57 | 2174.5 |  | 4969.51 | 1149.38 | 160.85 | [17 empty] | 1149.38 | 130.31 | 130.31 | 344.79 | [8 empty] | 162.72 | 1095.33 | 991.37 |  | 218.32 | 1270.53 | 1258.33 | 1258.33 | 835.78 | 902.96 | [6 empty] | 1270.53 | 1270.53 | 654.04 |  |  |  | 654.04 | 654.04 | 1372.54 |  | 79.82
A04AR098-00001 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: M2) | Fire Protective Rating: N/A | w/ Hardware & Accessories |  |  |  |  | - N/A ■REVISION | H-01 | M2 | 155.11 | 6.45 | 3.87 | 68.8 | [37 empty] | 25.33 | [10 empty] | 25.33 | 25.33
A04AR098-00002 | A | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: M2) | Fire Protective Rating: 0.5-hr | w/ Hardware & Accessories | [6 empty] | M2 | 65.79 | 29.67 | 8.17 | 4.3 | [56 empty] | 23.65
A04AR098-00002 | C | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: M2) | Fire Protective Rating: 0.5-hr | w/ Hardware & Accessories |  |  |  |  | - 0.75-hr ■REVISION |  | M2 | 2.15 | 2.15
A04AR098-00004 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: M2) | Fire Protective Rating: 1.5-hrs | w/ Hardware & Accessories |  |  |  |  | - 1.5-hr ■REVISION |  | M2 | 116.09 | 21.84 | 3.24 | [23 empty] | 5.75 | 11.84 | [9 empty] | 9 | 18.72 |  | 12.25 | [13 empty] | 9 |  |  |  | 9 | 9 | 6.45
A04AR098-00006 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: M2) | Fire Protective Rating: 3-hrs | w/ Hardware & Accessories |  |  |  |  | - 3.0-hr ■REVISION |  | M2 | 40.85 |  |  |  | 2.15 | [36 empty] | 12.9 | [10 empty] | 12.9 | 12.9
A04AR099-00001 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm ■REVISION | H-01 | EA | 41 | 3 |  | 23 | [37 empty] | 5 | [10 empty] | 5 | 5
A04AR099-00002 | A | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2150mm ■REVISION |  | EA | 6 |  | 1 | 5
A04AR099-00002 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2700mm ■REVISION |  | EA | 9 | [40 empty] | 3 | [10 empty] | 3 | 3
A04AR099-00003 | A | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 0.5-hr, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm - 0.33-hr ■REVISION |  | EA | 27 | 12 | 2 | 2 | [56 empty] | 11
A04AR099-00003 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 0.5-hr, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm - 0.75-hr ■REVISION |  | EA | 1 | 1
A04AR099-00004 | A | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 0.5-hr, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2150mm - 0.33-hr ■REVISION |  | EA | 1 | 1
A04AR099-00004 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 0.5-hr, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2150mm - 0.75-hr ■REVISION |  | EA | 1 |  | 1
A04AR099-00007 | A | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm - 1.5-hr ■REVISION |  | EA | 3 | [59 empty] | 3
A04AR099-00007 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1200mm x 2700mm - 1.5-hr ■REVISION |  | EA | 1 |  | 1
A04AR099-00007 | C | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2400mm - 1.5-hr ■ADD |  | EA | 1 | 1
A04AR099-00008 | A | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2150mm - 1.5-hr ■REVISION |  | EA | 2 | 2
A04AR099-00008 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2700mm - 1.5-hr ■REVISION |  | EA | 4 | 2 | [36 empty] | 2
A04AR099-00008 | C | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=3000mm x 3000mm - 1.5-hr ■REVISION |  | EA | 5 | [36 empty] | 1 | 1 | [15 empty] | 1 |  |  |  | 1 | 1
A04AR099-00008 | D | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=3200mm x 3700mm - 1.5-hr ■REVISION |  | EA | 1 | [26 empty] | 1
A04AR099-00008 | E | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=2300mm x 2500mm - 1.5-hr ■ADD |  | EA | 1 | [25 empty] | 1
A04AR099-00008 | F | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories | [6 empty] | EA | 1 | [39 empty] | 1
A04AR099-00011 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 3-hrs, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm - 3.0-hr ■REVISION |  | EA | 19 |  |  |  | 1 | [36 empty] | 6 | [10 empty] | 6 | 6
A04AR100-00001 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | Fire Protective Rating: N/A | w/ Hardware & Accessories |  |  |  |  | - N/A - Fire rated Vision panel : 200mm x 600mm - w/ Fire rated glazing ■REVISION |  | M2 | 9 |  |  | 9
A04AR100-00002 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | Fire Protective Rating: 0.5-hr | w/ Hardware & Accessories |  |  |  |  | - 0.33-hr w/ Fire rated glazing - Fire rated Vision panel : 200mm x 600mm - w/ Fire rated glazing ■REVISION |  | M2 | 15.05 | 15.05
A04AR100-00004 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | Fire Protective Rating: 1.5-hrs | w/ Hardware & Accessories |  |  |  |  | - 1.5-hr w/ Fire rated glazing - Fire rated Vision panel : 200mm x 600mm - w/ Fire rated glazing ■REVISION |  | M2 | 2.15 | 2.15
A04AR101-00002 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: N/A, Double Door | w/ Hardware & Accessories | [6 empty] | EA | 1 |  |  | 1
A04AR101-00003 | A | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 0.5-hr, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm - 0.33-hr - Fire rated Vision panel : 200mm x 600mm - w/ Fire rated glazing ■REVISION |  | EA | 7 | 7
A04AR101-00007 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 1.5-hrs, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm - 1.5-hr - Fire rated Vision panel : 200mm x 600mm - w/ Fire rated glazing ■REVISION |  | EA | 1 | 1
A04AR102-00001 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | Fire Protective Rating: N/A | w/ Hardware & Accessories |  |  |  |  | - N/A - Panic Bar included ■REVISION | H-01, H-01A | M2 | 91.42 |  | 16.17 | 27.95 | [34 empty] | 4.3 |  |  | 8.6 |  |  | 4.3 | 4.3 | [6 empty] | 8.6 | 8.6 | 2.15 |  |  |  | 2.15 | 2.15 |  |  | 2.15
A04AR102-00002 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | Fire Protective Rating: 0.5-hr | w/ Hardware & Accessories |  |  |  |  | - 0.33-hr - Panic Bar included ■REVISION |  | M2 | 19.91 | 4.86 | [39 empty] | 2.15 | [10 empty] | 2.15 | 2.15 | [6 empty] | 8.6
A04AR102-00002 | C | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | Fire Protective Rating: 0.5-hr | w/ Hardware & Accessories |  |  |  |  | - 0.75-hr - Panic Bar included ■REVISION |  | M2 | 19.35 | 2.15 | 2.15 | [35 empty] | 2.15 | [5 empty] | 2.15 | 2.15 | [8 empty] | 2.15 |  |  |  | 2.15 | 2.15 | 2.15
A04AR102-00004 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | Fire Protective Rating: 1.5-hrs | w/ Hardware & Accessories |  |  |  |  | - 1.5-hr - Panic Bar included ■REVISION | H-01, H-01A | M2 | 185.55 | 4.86 |  |  |  | 2.15 | [18 empty] | 2.15 |  | 4.3 | 4.3 | [9 empty] | 21.77 | 29.07 |  | 4.3 |  | 2.15 | 2.15 | 4.3 | 4.3 | [8 empty] | 20.47 |  |  |  | 20.47 | 20.47 | 38.34
A04AR102-00006 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | Fire Protective Rating: 3-hrs | w/ Hardware & Accessories |  |  |  |  | - 3.0-hr - Panic Bar included ■REVISION |  | M2 | 172.18 |  | 6.45 |  | 152.27 | [36 empty] | 2.15 | [10 empty] | 2.15 | 2.15 | [6 empty] | 7.01
A04AR103-00001 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: N/A, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm - Panic Bar included ■REVISION |  | EA | 38 |  | 3 | 13 | [34 empty] | 2 |  |  | 4 |  |  | 2 | 2 | [6 empty] | 4 | 4 | 1 |  |  |  | 1 | 1 |  |  | 1
A04AR103-00002 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: N/A, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2700mm - Panic Bar included ■REVISION |  | EA | 2 |  | 2
A04AR103-00003 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 0.5-hr, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm - 0.33-hr - Panic Bar included ■REVISION |  | EA | 7 | [40 empty] | 1 | [10 empty] | 1 | 1 | [6 empty] | 4
A04AR103-00003 | C | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 0.5-hr, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm - 0.75-hr - Panic Bar included ■REVISION |  | EA | 9 | 1 | 1 | [35 empty] | 1 | [5 empty] | 1 | 1 | [8 empty] | 1 |  |  |  | 1 | 1 | 1
A04AR103-00004 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 0.5-hr, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2700mm - 0.33-hr - Panic Bar included ■REVISION |  | EA | 1 | 1
A04AR103-00007 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H = 1000 mm x 2150 mm - 1.5-hr - Panic Bar included ■REVISION | H-01, H-01A | EA | 51 |  |  |  |  | 1 | [18 empty] | 1 |  | 2 | 2 | [9 empty] | 7 | 9 |  | 2 |  | 1 | 1 | 2 | 2 | [8 empty] | 5 |  |  |  | 5 | 5 | 6
A04AR103-00008 | A | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H = 1800 mm x 2700 mm - 1.5-hr - Panic Bar included ■REVISION | H-01, H-01A | EA | 11 | 1 | [36 empty] | 2 | [15 empty] | 2 |  |  |  | 2 | 2 | 2
A04AR103-00008 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H = 2400 mm x 2800 mm - 1.5-hr - Panic Bar included ■REVISION |  | EA | 2 | [36 empty] | 1 | [22 empty] | 1
A04AR103-00008 | C | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H = 3000 mm x 3000 mm - 1.5-hr - Panic Bar included ■REVISION |  | EA | 1 | [59 empty] | 1
A04AR103-00011 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 3-hrs, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H = 1000 mm x 2150 mm - 3.0-hr - Panic Bar included ■REVISION |  | EA | 38 |  | 3 |  | 31 | [36 empty] | 1 | [10 empty] | 1 | 1 | [6 empty] | 1
A04AR103-00012 | A | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 3-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H = 1800 mm x 2700 mm - 3.0-hr - Panic Bar included ■REVISION |  | EA | 4 |  |  |  | 3 | [55 empty] | 1
A04AR103-00012 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 3-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H = 3000 mm x 3000 mm - 3.0-hr - Panic Bar included ■REVISION |  | EA | 2 |  |  |  | 2
A04AR103-00012 | C | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: 3-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H = 5200 mm x 5100 mm - 3.0-hr - Panic Bar included ■REVISION |  | EA | 2 |  |  |  | 2
A04AR104-00001 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | Fire Protective Rating: N/A | w/ Hardware & Accessories |  |  |  |  | - N/A - Panic Bar included - Non Fire rated Vision Panel : 200mm x 600mm - w/ Fire rated glazing ■REVISION |  | M2 | 17.63 |  |  | 17.63
A04AR104-00002 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | Fire Protective Rating: 0.5-hr | w/ Hardware & Accessories |  |  |  |  | - 0.75-hr - Panic Bar included - Fire rated Vision Panel : 200mm x 600mm - w/ Fire rated glazing ■REVISION |  | M2 | 14.02 | 2.15 | 11.87
A04AR104-00004 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | Fire Protective Rating: 1.5-hrs | w/ Hardware & Accessories |  |  |  |  | - 1.5-hr - Panic Bar included - Fire rated Vision Panel : 200mm x 600mm - w/ Fire rated glazing ■REVISION |  | M2 | 4.32 |  |  | 4.32
A04AR105-00002 | A | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: N/A, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2150mm - Panic Bar included - Non Fire rated Vision Panel : 200mm x 600mm - w/ Fire rated glazing ■REVISION |  | EA | 4 |  |  | 4
A04AR105-00002 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: N/A, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2400mm - Panic Bar included - Non Fire rated Vision Panel : 200mm x 600mm - w/ Fire rated glazing ■REVISION |  | EA | 1 |  |  | 1
A04AR105-00003 | B | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 0.5-hr, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm - 0.75-hr - Panic Bar included - Fire rated Vision Panel : 200mm x 600mm - w/ Fire rated glazing ■REVISION |  | EA | 2 | 1 | 1
A04AR105-00004 | C | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 0.5-hr, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2700mm - 0.75-hr - Panic Bar included - Fire rated Vision Panel : 200mm x 600mm - w/ Fire rated glazing ■REVISION |  | EA | 2 |  | 2
A04AR105-00008 |  | Finishing Work | Door & Window Work | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2400mm - 1.5-hr - Panic Bar included - Fire rated Vision Panel : 200mm x 600mm - w/ Fire rated glazing ■REVISION |  | EA | 1 |  |  | 1
A04AR106-00004 | A | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: M2) | Fire Protective Rating: 1.5-hrs | w/ Hardware & Accessories |  |  |  |  | - 1.5-hr - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category L-Ⅰ as per SAES-M-009 ■REVISION |  | M2 | 82.44 | 9 |  |  |  | 9 | [18 empty] | 9 | [17 empty] | 9 | 9 | 18.72 | 18.72
A04AR106-00004 | B | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: M2) | Fire Protective Rating: 1.5-hrs | w/ Hardware & Accessories |  |  |  |  | - 1.5-hr - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category L-Ⅱ as per SAES-M-009 ■REVISION |  | M2 | 25.5 | [5 empty] | 7.5 | [18 empty] | 9 | [10 empty] | 9
A04AR106-00004 | C | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: M2) | Fire Protective Rating: 1.5-hrs | w/ Hardware & Accessories |  |  |  |  | - 1.5-hr - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category M-Ⅱ as per SAES-M-009 ■REVISION |  | M2 | 81 | [40 empty] | 27 | [10 empty] | 27 | 27
A04AR107-00008 | A | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2700mm - 1.5-hr - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category L-Ⅰ as per SAES-M-009 ■REVISION |  | EA | 4 | [43 empty] | 2 | 2
A04AR107-00008 | B | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=3000mm x 3000mm - 1.5-hr - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category L-Ⅰ as per SAES-M-009 ■REVISION |  | EA | 7 | 1 |  |  |  | 1 | [18 empty] | 1 | [17 empty] | 1 | 1 | 1 | 1
A04AR107-00008 | C | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=3000mm x 3000mm - 1.5-hr - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category L-Ⅱ as per SAES-M-009 ■REVISION |  | EA | 2 | [24 empty] | 1 | [10 empty] | 1
A04AR107-00008 | D | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=2400mm x 2700mm - 1.5-hr - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category M-Ⅱ as per SAES-M-009 ■REVISION |  | EA | 6 | [40 empty] | 2 | [10 empty] | 2 | 2
A04AR107-00008 | E | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=3000mm x 3000mm - 1.5-hr - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category M-Ⅱ as per SAES-M-009 ■REVISION |  | EA | 3 | [40 empty] | 1 | [10 empty] | 1 | 1
A04AR107-00008 | F | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=2500mm x 3000mm - 1.5-hr - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category L-Ⅱ as per SAES-M-009 ■ADD |  | EA | 1 | [5 empty] | 1
A04AR108-00004 | A | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | Fire Protective Rating: 1.5-hrs | w/ Hardware & Accessories |  |  |  |  | - 1.5-hr - Panic Bar included - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category L-Ⅰ as per SAES-M-009 ■REVISION | H-01, H-01A, H-02, H-03A, H-03B | M2 | 175.94 | 38.92 | 9 |  |  | 19.62 | [18 empty] | 19.62 | [17 empty] | 19.62 | 19.62 | 24.77 | 24.77
A04AR108-00004 | B | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | Fire Protective Rating: 1.5-hrs | w/ Hardware & Accessories |  |  |  |  | - 1.5-hr - Panic Bar included - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category L-Ⅱ as per SAES-M-009 ■REVISION | H-01, H-01A, H-02, H-03A, H-03B | M2 | 25.8 |  | 12.9 |  |  |  | 4.3 | [18 empty] | 4.3 | [10 empty] | 4.3
A04AR108-00004 | C | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | Fire Protective Rating: 1.5-hrs | w/ Hardware & Accessories |  |  |  |  | - 1.5-hr - Panic Bar included - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category M-Ⅱ as per SAES-M-009 ■REVISION |  | M2 | 29.16 |  | 29.16
A04AR109-00007 | A | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm - 1.5-hr - Panic Bar included - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category L-Ⅰ as per SAES-M-009 ■REVISION | H-01, H-01A, H-02, H-03A, H-03B | EA | 43 | 5 |  |  |  | 6 | [18 empty] | 6 | [17 empty] | 6 | 6 | 7 | 7
A04AR109-00007 | B | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm - 1.5-hr - Panic Bar included - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category L-Ⅱ as per SAES-M-009 ■REVISION | H-01, H-01A, H-02, H-03A, H-03B | EA | 12 |  | 6 |  |  |  | 2 | [18 empty] | 2 | [10 empty] | 2
A04AR109-00007 | C | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm - 1.5-hr - Panic Bar included - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category M-Ⅱ as per SAES-M-009 ■REVISION | H-01, H-01A, H-02, H-03A, H-03B | EA | 24 | [40 empty] | 8 | [10 empty] | 8 | 8
A04AR109-00008 | A | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2150mm - 1.5-hr - Panic Bar included - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category L-Ⅰ as per SAES-M-009 ■REVISION | H-01, H-01A, H-02, H-03A, H-03B | EA | 1 | 1
A04AR109-00008 | B | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2700mm - 1.5-hr - Panic Bar included - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category L-Ⅰ as per SAES-M-009 ■REVISION | H-01, H-01A, H-02, H-03A, H-03B | EA | 9 | 5 | [42 empty] | 2 | 2
A04AR109-00008 | C | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=2400mm x 2800mm - 1.5-hr - Panic Bar included - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category L-Ⅰ as per SAES-M-009 ■REVISION | H-01, H-01A, H-02, H-03A, H-03B | EA | 4 |  |  |  |  | 1 | [18 empty] | 1 | [17 empty] | 1 | 1
A04AR109-00008 | D | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2700mm - 1.5-hr - Panic Bar included - Refer to Blast Loads for Buildings described in Reference Spec - Door Performance Category M-Ⅱ as per SAES-M-009 ■REVISION | H-01, H-01A, H-02, H-03A, H-03B | EA | 6 |  | 6
A04AR109-00008 | E | Finishing Work | Door & Window Work | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | Fire Protective Rating: 1.5-hrs, Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H = 3,000 mm x 3,000 mm | H-01, H-01A, H-02, H-03A, H-03B | EA | 1 |  | 1
A04AR118-00001 |  | Finishing Work | Door & Window Work | Glass Door w/ SST Frame (UoM: M2) | w/ Hardware & Accessories | [5 empty] | - Fire Protective Rating : 1.5-hrs ■REVISION |  | M2 | 15.36 | 15.36
A04AR119-00001 |  | Finishing Work | Door & Window Work | Glass Door w/ SST Frame (UoM: EA) | Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2400mm - Fire Protective Rating : 1.5-hrs ■REVISION |  | EA | 1 | 1
A04AR119-00002 | A | Finishing Work | Door & Window Work | Glass Door w/ SST Frame (UoM: EA) | Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2400mm - Fire Protective Rating : 1.5-hrs - Panic Bar included ■REVISION |  | EA | 2 | 2
A04AR119-00002 | B | Finishing Work | Door & Window Work | Glass Door w/ SST Frame (UoM: EA) | Double Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1800mm x 2700mm - Fire Protective Rating : 1.5-hrs - Panic Bar included ■REVISION |  | EA | 1 | 1
A04AR122-00001 |  | Finishing Work | Door & Window Work | Wood Door w/ Wood Frame (UoM: M2) | w/ Hardware & Accessories | [5 empty] | ■REVISION |  | M2 | 328.77 |  | 62.3 | 103.2 | [37 empty] | 48.88 | [10 empty] | 48.88 | 48.88 | [6 empty] | 6.45 |  | 10.18
A04AR123-00001 | A | Finishing Work | Door & Window Work | Wood Door w/ Wood Frame (UoM: EA) | Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2150mm ■REVISION |  | EA | 149 |  | 28 | 48 | [37 empty] | 22 | [10 empty] | 22 | 22 | [6 empty] | 3 |  | 4
A04AR123-00001 | B | Finishing Work | Door & Window Work | Wood Door w/ Wood Frame (UoM: EA) | Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=750mm x 2100mm ■REVISION |  | EA | 4 | [40 empty] | 1 | [10 empty] | 1 | 1 | [8 empty] | 1
A04AR123-00001 | C | Finishing Work | Door & Window Work | Wood Door w/ Wood Frame (UoM: EA) | Single Door | w/ Hardware & Accessories |  |  |  |  | - W x H=1000mm x 2100mm ■REVISION |  | EA | 1 |  | 1
A04AR126-00001 |  | Finishing Work | Door & Window Work | Steel Roll Up Door w/ Steel Frame (UoM: M2) | Fire Protective Rating: N/A, Motorized Type | w/ Hardware & Accessories |  |  |  |  | ■REVISION |  | M2 | 96.75 |  |  | 96.75
A04AR127-00001 | A | Finishing Work | Door & Window Work | Steel Roll Up Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Motorized Type | w/ Hardware & Accessories |  |  |  |  | - W x H=3600mm x 4000mm ■REVISION |  | EA | 5 |  |  | 5
A04AR127-00001 | B | Finishing Work | Door & Window Work | Steel Roll Up Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Motorized Type | w/ Hardware & Accessories |  |  |  |  | - W x H=5500mm x 4500mm ■REVISION |  | EA | 1 |  |  | 1
A04AR151-00001 |  | Finishing Work | Door & Window Work | Master Key System | Three Levels Master Key | w/ Accessories (Key Box, Key Tag and ETC) | [6 empty] | SET | 35 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [11 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | 1 | 1 | 1 |  |  |  | 1 | 1 | 1 |  | 1
A04AR152-00003 | A | Finishing Work | Door & Window Work | Steel Window (UoM: M2) | Fire Protective Rating: 1-hr | w/ Hardware & Accessories | [6 empty] | M2 | 28.21 | 25.91 | [58 empty] | 2.3
A04AR152-00003 | B | Finishing Work | Door & Window Work | Steel Window (UoM: M2) | Fire Protective Rating: 1-hr | w/ Hardware & Accessories |  |  |  |  | - 2-hr Fire Rated Window ■REVISION |  | M2 | 93.75 | 93.75
A04AR153-00002 | B | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 0.5-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=750mm x 1150mm - 0.75-hr Fire Rated Window ■REVISION |  | EA | 1 |  | 1
A04AR153-00002 | C | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 0.5-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=1200mm x 1150mm - 0.75-hr Fire Rated Window ■REVISION |  | EA | 2 | 2
A04AR153-00002 | D | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 0.5-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=1200mm x 1400mm - 0.75-hr Fire Rated Window ■REVISION |  | EA | 3 | 3
A04AR153-00002 | E | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 0.5-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=1500mm x 1150mm - 0.75-hr Fire Rated Window ■REVISION |  | EA | 3 |  | 3
A04AR153-00002 | F | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 0.5-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=2000mm x 1150mm - 0.75-hr Fire Rated Window ■REVISION |  | EA | 4 | 4
A04AR153-00002 | G | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 0.5-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=2000mm x 1400mm - 0.75-hr Fire Rated Window ■REVISION |  | EA | 2 | 2
A04AR153-00002 | H | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 0.5-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=3000mm x 1150mm - 0.75-hr Fire Rated Window ■REVISION |  | EA | 1 |  | 1
A04AR153-00003 | B | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 1-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=2000mm x 1150mm - 2-hr Fire Rated Window ■REVISION |  | EA | 1 | [59 empty] | 1
A04AR153-00003 | J | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 1-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=3280mm x 1700mm - 2-hr Fire Rated Window ■ADD |  | EA | 1 | 1
A04AR153-00003 | K | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 1-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=2780mm x 1700mm - 2-hr Fire Rated Window ■ADD |  | EA | 2 | 2
A04AR153-00003 | L | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 1-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=5844mm x 1400mm - 2-hr Fire Rated Window ■ADD |  | EA | 4 | 4
A04AR153-00003 | M | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 1-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=4580mm x 1400mm - 2-hr Fire Rated Window ■ADD |  | EA | 1 | 1
A04AR153-00003 | N | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 1-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=9430mm x 1400mm - 2-hr Fire Rated Window ■ADD |  | EA | 2 | 2
A04AR153-00003 | O | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 1-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=4709mm x 1400mm - 2-hr Fire Rated Window ■ADD |  | EA | 2 | 2
A04AR153-00003 | P | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 1-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=2180mm x 1400mm - 2-hr Fire Rated Window ■ADD |  | EA | 1 | 1
A04AR153-00003 | Q | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 1-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=3330mm x 1400mm - 2-hr Fire Rated Window ■ADD |  | EA | 1 | 1
A04AR153-00003 | R | Finishing Work | Door & Window Work | Steel Window (UoM: EA) | Fire Protective Rating: 1-hr | w/ Hardware & Accessories |  |  |  |  | - W x H=6500mm x 1400mm - 2-hr Fire Rated Window ■ADD |  | EA | 2 | 2
A04AR158-00001 |  | Finishing Work | Door & Window Work | Aluminum Window (UoM: M2) | Fire Protective Rating: N/A | w/ Hardware & Accessories |  |  |  |  | ■REVISION | H-07 | M2 | 60.49 |  |  | 57.04 | [58 empty] | 3.45
A04AR159-00001 | A | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | w/ Hardware & Accessories |  |  |  |  | - W x H=1500mm x 1150mm ■REVISION | H-07 | EA | 2 | [61 empty] | 2
A04AR159-00001 | B | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | w/ Hardware & Accessories |  |  |  |  | - W x H=1600mm x 1150mm ■REVISION |  | EA | 22 |  |  | 22
A04AR159-00001 | C | Finishing Work | Door & Window Work | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A | w/ Hardware & Accessories |  |  |  |  | - W x H=2400mm x 1150mm ■REVISION |  | EA | 6 |  |  | 6
A04AR315-00001 | A | Finishing Work | Door & Window Work | Curtain Wall System (UoM: M2) | w/ Hardware & Accessories | [5 empty] | ■REVISION | H-07 | M2 | 8.1 |  | 8.1
A04AR315-00001 | B | Finishing Work | Door & Window Work | Curtain Wall System (UoM: M2) | w/ Hardware & Accessories | [5 empty] | - 0.75-hr Fire Rated ■REVISION |  | M2 | 21.35 | 21.35
A04AR316-00001 | A | Finishing Work | Door & Window Work | Curtain Wall System (UoM: EA) | w/ Hardware & Accessories | [5 empty] | - W x H=3000mm x 2700mm - Aluminum Glazed Curtain Walling System ■REVISION |  | EA | 1 |  | 1
A04AR316-00001 | B | Finishing Work | Door & Window Work | Curtain Wall System (UoM: EA) | w/ Hardware & Accessories | [5 empty] | - W x H=3820mm x 2700mm - 0.75-hr Fire Rated - Aluminum Glazed Curtain Walling System ■REVISION |  | EA | 1 | 1
A04AR316-00001 | C | Finishing Work | Door & Window Work | Curtain Wall System (UoM: EA) | w/ Hardware & Accessories | [5 empty] | - W x H=4090mm x 2700mm - 0.75-hr Fire Rated - Aluminum Glazed Curtain Walling System ■REVISION |  | EA | 1 | 1
A04AS168-00001 |  | Finishing Work | Exterior/Interior Finish Work | Screed | w/o Welded Wire Fabric | THK<50mm |  |  |  |  | - THK=50mm incl. Tile Thickness | I-01 | M2 | 13068.01 | 1220.52 | 1642.57 | 2129.77 | 257.26 | 862.5 | [18 empty] | 862.5 | [12 empty] | 745.5 | 196.2 |  |  | 666.74 | 900.45 | 900.45 | 165 | 181.5 | [6 empty] | 666.74 | 666.74 | 116.1 |  |  |  | 116.1 | 116.1 | 597.9 |  | 57.37
A04AS168-00003 |  | Finishing Work | Exterior/Interior Finish Work | Screed | w/o Welded Wire Fabric | 75mm≤THK |  |  |  |  | - THK=(TBD)mm ★ADD (PSS01/Trench) |  | M2 | 25.85 | [50 empty] | 25.85
A04AS170-00001 |  | Finishing Work | Exterior/Interior Finish Work | Carpet Tile | [6 empty] | - Tile Size=W450mm x L450mm (Exact size to be defined at Construction stage) | I-03 | M2 | 234.38 | 31.85 | 35.82 | 44.02 | [37 empty] | 30 | [10 empty] | 30 | 30 | [6 empty] | 22.45 |  | 10.24
A04AS172-00002 |  | Finishing Work | Exterior/Interior Finish Work | Entrance Floor Mats and Frame | Embedded Type | [5 empty] | - Matwell at Entrance Door | I-22 | M2 | 28.5 | 3.24 | 6.06 | 4.32 | [37 empty] | 3 |  |  |  |  | 3.48 | [5 empty] | 3 | 3 | [6 empty] | 1.8 |  | 0.6
A04AS173-00001 |  | Finishing Work | Exterior/Interior Finish Work | Steel Trowel Finish | [6 empty] | - for Exposed Conc. Surface |  | M2 | 18315.62 | 2847.62 | 385.26 | 1876.14 | 5284.51 | 187.5 | 130 | 100 | 24.01 | [15 empty] | 187.5 | 130 | 130 | 180 | 100 | 24.01 | 24.01 | 24.01 | 24.01 | 24.01 | 24.01 |  | 130 | 229.95 | 711 |  | 180 | 504.08 | 225 | 225 | 595.32 | 641.48 | 100 | [5 empty] | 504.08 | 504.08 | 471.5 |  |  |  | 471.5 | 471.5 | 644.53
A04AS173-00002 |  | Finishing Work | Exterior/Interior Finish Work | Steel Trowel Finish | Brushed(Broom) Finish | [7 empty] | M2 | 7549.14 | 312.33 | 464.03 | 554.81 | 648.03 | 205.7 | 78.7 | 93.11 | 39.63 | [15 empty] | 205.7 | 78.7 | 78.7 | 100.74 | 93.11 | 39.63 | 39.63 | 39.63 | 39.63 | 39.63 | 39.63 |  | 78.7 | 267.93 | 311.21 |  | 92.7 | 330.73 | 275.4 | 250.72 | 306.83 | 303.13 | 95.2 | [5 empty] | 330.73 | 330.73 | 226.68 |  |  |  | 226.68 | 226.68 | 499.61 |  | 84.41 | 120
A04AS174-00002 | A | Finishing Work | Exterior/Interior Finish Work | Raised Floor | Top Finish: Anti-Static Vinyl Tile | 600mm x 600mm / 600mm<H≤1000mm |  |  |  |  | - H=1000mm | I-02 | M2 | 5255.21 | 2343.6 | 25.3 | 243.65 | [34 empty] | 523.8 | [5 empty] | 408.12 | 461.48 | [8 empty] | 288.9 |  |  |  | 288.9 | 288.9 | 382.56
A04AS174-00003 |  | Finishing Work | Exterior/Interior Finish Work | Raised Floor | Top Finish: Anti-Static Vinyl Tile | 600mm x 600mm / 1000mm<H≤1500mm |  |  |  |  | - H=1500mm ★ADD (GIS) |  | M2 | 977.64 |  |  |  | 977.64
A04AS176-00009 | A | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | Rigid Insulation | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 1-Layer Gypsumboard THK=16mm |  |  | - Insulation THK=110mm - Rigid Insulation to be R-19 & Non-Combustible - incl. THK 0.25 PE Sheet to External Side | I-06 | M2 | 16644.38 | 1799.3 | 777.28 | 773.16 |  | 1003.68 | 266.8 | [17 empty] | 1003.68 | 266.8 | 266.8 | 321.3 | [8 empty] | 266.8 | 567.02 | 817.92 |  | 367.2 | 967.62 | 669.68 | 669.68 | 721.36 | 769.64 | [6 empty] | 967.62 | 967.62 | 494.16 |  |  |  | 494.16 | 494.16 | 851.15 |  | 79.79
A04AS176-00009 | B | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | Rigid Insulation | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 1-Layer Gypsumboard THK=16mm |  |  | - Insulation THK=110mm - Rigid Insulation to be R-19 & Non-Combustible - incl. THK 0.25 PE Sheet to External Side - THK.16mm Calcium Silicate Board to be used instead of Gypsum Board | I-06 | M2 | 3460.65 | 322.05 | 205.52 | 156.74 |  | 304.64 | [18 empty] | 304.64 | [12 empty] | 185.86 | 85.2 |  |  | 182.74 | 185.6 | 185.6 | 85.2 | 85.2 | [6 empty] | 182.74 | 182.74 | 195.96 |  |  |  | 195.96 | 195.96 | 218.3
A04AS176-00009 | C | Finishing Work | Exterior/Interior Finish Work | Plasterboard Dry Liner System | Rigid Insulation | for Wall To External Side | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | 1-Layer Gypsumboard THK=16mm |  |  | - Insulation THK=110mm - Rigid Insulation to be R-19 & Non-Combustible - incl. THK 0.25 PE Sheet to External Side - Moisture resistant type |  | M2 | 401.98 | 141.95 | 29.68 | [38 empty] | 41.06 | [10 empty] | 41.06 | 41.06 | [6 empty] | 56.6 |  | 50.57
A04AS177-00027 |  | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Fixed Type) | Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides | Mineral Wool (Rock Wool) | Including Supporting Frame(Stud) & Accessories | 1-Layer Gypsumboard THK=16mm |  |  | - 1-hr Gypsum Encasement Fireproofing applied only to CCB - No insulation to be applied - 2-layer THK15 Type X Gypsum Boards (or equiv.) to be applied to One Side |  | M2 | 224 | 224
A04AS178-00006 |  | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Removable Type) | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides | Glass Wool (Fiberglass) | Including Supporting Frame(Stud) & Accessories | 1-Layer Gypsumboard THK=16mm |  |  | - Insulation THK=50mm (Thickness of Insulation to be defined during Detailed Engineering) | I-11 | M2 | 365.6 | 171.2 |  | 194.4
A04AS178-00009 | B | Finishing Work | Exterior/Interior Finish Work | Gypsumboard Partition Wall (Removable Type) | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides | w/o Insulation | Including Supporting Frame(Stud) & Accessories | 1-Layer Gypsumboard THK=16mm |  |  | - Partition Wall ■ADD |  | M2 | 253.24 |  |  | 253.24
A04AS179-00001 |  | Finishing Work | Exterior/Interior Finish Work | Cubicle Partition | for Toilet | w/ Accessories |  |  |  |  | - H=(2100)mm - incl. Door for Each Compartment |  | M | 175.54 | 21.9 | 16.9 | 41.28 | [37 empty] | 26.4 | [10 empty] | 26.4 | 26.4 | [6 empty] | 9.64 |  | 6.62
A04AS190-00002 |  | Finishing Work | Exterior/Interior Finish Work | Acoustic Tiled Ceiling System | T-Bar System | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  |  |  |  | - Tile Size=600mm x 600mm | I-07 | M2 | 11658.32 | 3091.11 | 1458.68 | 2029.39 | 949.24 | [33 empty] | 497.08 |  |  | 459.56 |  |  | 386.62 | 436.06 | [6 empty] | 459.56 | 459.56 | 264.42 |  |  |  | 264.42 | 264.42 | 619.67 |  | 18.53
A04AS191-00002 |  | Finishing Work | Exterior/Interior Finish Work | Moisture Resistant Tiled Ceiling System | T-Bar System | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  |  |  |  | - Tile Size=600mm x 600mm | I-08 | M2 | 1225.8 | 149.57 | 156.97 | 296.58 | [37 empty] | 170.7 | [10 empty] | 170.7 | 170.7 | [6 empty] | 71.27 |  | 39.31
A04AS194-00002 |  | Finishing Work | Exterior/Interior Finish Work | Rigid Insulation | for Exposed Ceiling Structure of Cable Room | w/ Accessories | 50mm≤THK<75mm |  |  |  | - THK=50mm - Non-combustible Insulation w/ Aluminum Foil |  | M2 | 822.42 |  |  |  | 822.42
A04AS195-00001 | B | Finishing Work | Exterior/Interior Finish Work | Pre-Fabricated Canopy | Steel Canopy | w/ Supporting Frame, Accessories |  |  |  |  | - W x L x Min. D=900mm x 1900mm x 200mm ★ADD (CCR02) |  | EA | 2 | [61 empty] | 2
A04AS314-00001 |  | Finishing Work | Exterior/Interior Finish Work | Plywood w/ Fire Retardant Paint | [6 empty] | - Thk19 Plywood w/ 2-coats of Non-Conductive & 2hrs Fire Retardant White Color Paint |  | M2 | 725.35 | 106.39 | 36.85 | 47.09 | 26.11 | 21.48 | [18 empty] | 21.48 | [12 empty] | 21.48 | 21.84 |  |  | 18.55 | 21.48 | 21.48 | 19.4 | 25.99 | [6 empty] | 18.55 | 18.55 | 65.71 |  |  |  | 65.71 | 65.71 | 81.5
A04AT198-00001 |  | Finishing Work | Plastering Work | Plastering | for External Masonry Wall | [5 empty] | - THK=20mm | I-05 | M2 | 1182.19 |  |  | 744 |  |  |  | 69.12 | [11 empty] | 24.42 | 19.91 | 19.91 | 22.66 | 20.9 |  |  |  |  | 69.12 | [6 empty] | 20.9 |  |  | 5.68 | [5 empty] | 5.68 | 5.68 | 34.8 | [7 empty] | 2.79 |  |  |  | 2.79 | 2.79 | 4.99 |  | 106.05
A04AT198-00002 |  | Finishing Work | Plastering Work | Plastering | for Internal Masonry Wall | [5 empty] | - THK=16mm | I-05 | M2 | 40640.07 | 3761.04 | 2860.91 | 12209.97 | 2344.82 | 396.84 | 92.6 | 147.3 | [16 empty] | 396.84 | 91.1 | 94.35 | 103.12 | 147.3 | [7 empty] | 92.6 | 449.48 | 1185.5 |  | 105.85 | 3034.71 | 463.88 | 463.88 | 1125.15 | 1154.79 | 147.3 | [5 empty] | 3034.71 | 3034.71 | 647.65 |  |  |  | 647.65 | 647.65 | 1681.37 |  | 77
A04AV205-00001 |  | Finishing Work | Misc. Work | Roof Drain (for Building) | Cast Iron Type | DIA=100mm | [6 empty] | EA | 195 | 24 | 9 |  | 26 | 8 | 3 | [17 empty] | 8 | 3 | 3 | 3 | [8 empty] | 3 | 7 | 10 |  | 3 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 8 | 8 | 6 |  |  |  | 6 | 6 | 10 |  | 1
A04AV205-00002 |  | Finishing Work | Misc. Work | Roof Drain (for Building) | Cast Iron Type | DIA=150mm | [6 empty] | EA | 18 |  |  | 18
A04AV206-00001 |  | Finishing Work | Misc. Work | Roof Drain (for Shelter) | Cast Iron Type | DIA=100mm | [6 empty] | EA | 33 |  | 2 |  | 4 |  |  | 1 | 1 | [10 empty] | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [10 empty] | 1 |  |  |  |  | 3 | [11 empty] | 8
A04AV207-00001 |  | Finishing Work | Misc. Work | Downspout | Galvanized Steel Type | w/ Fixing Accessories | DIA=100mm |  |  |  | - Color Coated Downspout | I-13 | M | 1834.81 | 231.6 | 56.36 |  | 321.45 | 56.4 | 17.85 | 5.35 | 2.5 | [10 empty] | 3.65 | 3.65 | 3.65 | 3.65 | 3.65 | 56.4 | 17.85 | 17.85 | 21 | 5.35 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3.65 | 17.85 | 51.8 | 72.5 |  | 20.55 | 66 | 59.2 | 59.2 | 58 | 58 | 5.35 |  |  |  |  | 37.5 | 66 | 66 | 43.5 |  |  |  | 43.5 | 43.5 | 75 |  | 4.1 | 140.4
A04AV207-00002 |  | Finishing Work | Misc. Work | Downspout | Galvanized Steel Type | w/ Fixing Accessories | DIA=150mm | [5 empty] | M | 180 |  |  | 180
A04AV208-00001 |  | Finishing Work | Misc. Work | Water Collection Box | Galvanized Steel Type | w/ Fixing Accessories | [6 empty] | EA | 195 | 24 | 9 |  | 26 | 8 | 3 | [17 empty] | 8 | 3 | 3 | 3 | [8 empty] | 3 | 7 | 10 |  | 3 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 8 | 8 | 6 |  |  |  | 6 | 6 | 10 |  | 1
A04AV209-00001 |  | Finishing Work | Misc. Work | Splash Block | Precast Concrete Block Type | [7 empty] | EA | 246 | 24 | 11 | 18 | 30 | 8 | 3 | 1 | 1 | [10 empty] | 1 | 1 | 1 | 1 | 1 | 8 | 3 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 7 | 10 |  | 3 | 8 | 8 | 8 | 8 | 8 | 1 |  |  |  |  | 3 | 8 | 8 | 6 |  |  |  | 6 | 6 | 10 |  | 1 | 8
A04AV210-00002 |  | Finishing Work | Misc. Work | Natural Ventilator | w/ Fixing Accessories | 600mm≤DIA<800mm |  |  |  |  | - DIA=(600)mm |  | EA | 4 | [6 empty] | 2 | [20 empty] | 2
A04AV212-00002 |  | Finishing Work | Misc. Work | Chain Link Fence (Fixed Type) | Self-Standing Type w/ Steel Frame | w/ Fixing Accessories | 2000mm≤H<2500mm |  |  |  | - H=2425mm (H is Total Fence Height) - Saudi Aramco Type V Fence for Chemical Storage Shelters | H-04B | M | 20.4 | [6 empty] | 7.6 | [20 empty] | 7.6 | [17 empty] | 5.2
A04AV212-00003 |  | Finishing Work | Misc. Work | Chain Link Fence (Fixed Type) | Self-Standing Type w/ Steel Frame | w/ Fixing Accessories | 2500mm≤H<3000mm |  |  |  | - H=2775mm (H is Total Fence Height) - Saudi Aramco Type Ⅳ Fence for Substation TR Area - incl. Fencing Footings | H-04A | M | 854.79 |  |  |  | 165.09 | 183 | [18 empty] | 181.8 | [12 empty] | 85.27 |  |  |  |  | 100.56 | 102.07 | [16 empty] | 37
A04AV212-00006 |  | Finishing Work | Misc. Work | Chain Link Fence (Fixed Type) | Self-Standing Type w/ Stainless Steel Frame | w/ Fixing Accessories | 2000mm≤H<2500mm |  |  |  | - H=2450mm (H is Total Fence Height) - General Type Fence for Laboratory ■ADD |  | M | 38.2 |  | 38.2
A04AV214-00001 | A | Finishing Work | Misc. Work | Chain Link Fence Single Gate | Self-Standing Type, Single | w/ Frame, Fixing Accessories |  |  |  |  | - W x H=1200mm x 2750mm - Saudi Aramco Type Ⅳ | H-04A | EA | 17 |  |  |  |  | 5 | [18 empty] | 5 | [12 empty] | 2 |  |  |  |  | 2 | 2 |  |  | 1
A04AV214-00001 | B | Finishing Work | Misc. Work | Chain Link Fence Single Gate | Self-Standing Type, Single | w/ Frame, Fixing Accessories |  |  |  |  | - W x H=1200mm x 2125mm - Saudi Aramco Type V Fence for Chemical Storage Shelters - w/ One Panice Bar & Lock |  | EA | 2 | [6 empty] | 1 | [20 empty] | 1
A04AV215-00001 | A | Finishing Work | Misc. Work | Chain Link Fence Double Gate | Self-Standing Type, Double | w/ Frame, Fixing Accessories |  |  |  |  | - W x H=4850mm x 2750mm - Saudi Aramco Type Ⅳ | H-04A | EA | 10 | [36 empty] | 3 |  |  |  |  | 3 | 3 | [16 empty] | 1
A04AV215-00001 | B | Finishing Work | Misc. Work | Chain Link Fence Double Gate | Self-Standing Type, Double | w/ Frame, Fixing Accessories |  |  |  |  | - W x H=2400mm x 2425mm - Saudi Aramco Type V Fence for Chemical Storage Shelters - w/ One Panice Bar & Lock | H-04B | EA | 3 | [6 empty] | 1 | [20 empty] | 1 | [17 empty] | 1
A04AV215-00001 | D | Finishing Work | Misc. Work | Chain Link Fence Double Gate | Self-Standing Type, Double | w/ Frame, Fixing Accessories |  |  |  |  | - W x H=2900mm x 2750mm - Saudi Aramco Type Ⅳ |  | EA | 8 |  |  |  |  | 4 | [18 empty] | 4
A04AV215-00002 |  | Finishing Work | Misc. Work | Chain Link Fence Double Gate | Frame Type, Double | w/ Frame, Fixing Accessories |  |  |  |  | - W x H=1800mm x 2450mm - General Fence Gate for Laboratory (■ADD) |  | EA | 4 |  | 4
A04AV219-00002 |  | Finishing Work | Misc. Work | Steel Bollard | Removable Type | w/ Paint, Concrete Fill |  |  |  |  | - DIA=114mm - Exposed H=1000mm - incl. Embedded Steel Pipe, Foundation | I-18 | EA | 472 | 37 | 39 | 50 | 39 | 15 |  | 4 | [16 empty] | 15 |  |  |  | 4 | [8 empty] | 28 | 18 |  |  | 16 | 20 | 27 | 19 | 19 | [6 empty] | 16 | 16 | 19 |  |  |  | 19 | 19 | 20 |  | 13
A04AV220-00001 | A | Finishing Work | Misc. Work | Building Signage | [6 empty] | - ES1: External Signage as per TE-786915 | I-19 | SET | 44 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [10 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 |  |  |  | 1 | 1 | 1 |  | 1 | 1
A04AV221-00001 | A | Finishing Work | Misc. Work | Room Signage | [6 empty] | - IS1: Internal Signage as per TE-786915 |  | SET | 463 | 36 | 61 | 94 | 14 | 4 | 2 | [17 empty] | 4 | 2 | 2 | 2 | [8 empty] | 2 | 4 | 12 |  | 2 | 45 | 4 | 4 | 12 | 12 | [6 empty] | 45 | 45 | 7 |  |  |  | 7 | 7 | 28 |  | 6
A04AV223-00001 |  | Finishing Work | Misc. Work | Wheel Stop | Concrete Type | w/ Painting, Fixing Accessories | [5 empty] | I-20 | EA | 148 | [9 empty] | 20 |  | 20 | 20 | [25 empty] | 12 | [8 empty] | 22 | 10 | 4 |  |  |  |  | 4 | 4 | 4 |  |  |  | 28
A04AV225-00001 | C | Finishing Work | Misc. Work | Mirror w/ Shelf | Stainless Steel, Surface Mounted Type | [5 empty] | - W x H=2000mm x 750mm ★ADD (OME) |  | EA | 3 | [40 empty] | 1 | [10 empty] | 1 | 1
A04AV225-00001 | D | Finishing Work | Misc. Work | Mirror w/ Shelf | Stainless Steel, Surface Mounted Type | [5 empty] | - W x H=2650mm x 750mm ★ADD (OME) |  | EA | 3 | [40 empty] | 1 | [10 empty] | 1 | 1
A04AV225-00001 | E | Finishing Work | Misc. Work | Mirror w/ Shelf | Stainless Steel, Surface Mounted Type | [5 empty] | - W x H=1500mm x 750mm ★ADD (OME) |  | EA | 4 | [40 empty] | 1 | [10 empty] | 1 | 1 | [6 empty] | 1
A04AV225-00001 | F | Finishing Work | Misc. Work | Mirror w/ Shelf | Stainless Steel, Surface Mounted Type | [5 empty] | - W x H=2100mm x 750mm ★ADD (OME) |  | EA | 1 | [61 empty] | 1
A04AV225-00001 | G | Finishing Work | Misc. Work | Mirror w/ Shelf | Stainless Steel, Surface Mounted Type | [5 empty] | - W x H=2200mm x 750mm ★ADD (LAB) |  | EA | 1 |  | 1
A04AV225-00001 | H | Finishing Work | Misc. Work | Mirror w/ Shelf | Stainless Steel, Surface Mounted Type | [5 empty] | - W x H=500mm x 750mm ★ADD (for disabled toilet) |  | EA | 4 | 1 | 2 | 1
A04AV225-00001 | I | Finishing Work | Misc. Work | Mirror w/ Shelf | Stainless Steel, Surface Mounted Type | [5 empty] | - W x H=4600mm x 750mm ★ADD (CCR01) |  | EA | 2 | 2
A04AV225-00001 | K | Finishing Work | Misc. Work | Mirror w/ Shelf | Stainless Steel, Surface Mounted Type | [5 empty] | - W x H=2950mm x 750mm ■ADD (CEN) |  | EA | 1 |  |  | 1
A04AV225-00001 | L | Finishing Work | Misc. Work | Mirror w/ Shelf | Stainless Steel, Surface Mounted Type | [5 empty] | - W x H=2150mm x 750mm ■ADD (CEN) |  | EA | 2 |  |  | 2
A04AV225-00001 | M | Finishing Work | Misc. Work | Mirror w/ Shelf | Stainless Steel, Surface Mounted Type | [5 empty] | - W x H=1400mm x 750mm ■ADD (LAB) |  | EA | 1 |  | 1
A04AV226-00001 |  | Finishing Work | Misc. Work | Liquid Soap Dispensers | Stainless Steel, Surface Mounted Type | [7 empty] | EA | 46 | 9 | 5 | [38 empty] | 9 | [10 empty] | 9 | 9 | [6 empty] | 2 |  | 3
A04AV227-00001 |  | Finishing Work | Misc. Work | Soap Dish | Stainless Steel, Surface Mounted Type | [7 empty] | EA | 19 |  | 5 | 14
A04AV229-00001 |  | Finishing Work | Misc. Work | Coat & Hat Hooks | Stainless Steel, Surface Mounted Type | [5 empty] | - HSH, Hat Shelf & Coat Hanger, based on Furniture Schedule - 900mm (W) x 600mm (D) Wall mounted metal wire shelf (chrome finish) with coat rod |  | EA | 73 | 13 | 4 | 19 | [37 empty] | 10 | [10 empty] | 10 | 10 | [6 empty] | 4 |  | 3
A04AV230-00001 |  | Finishing Work | Misc. Work | Electric Hand Dryer | Surface Mounted Type | [5 empty] | [Not Applicable to SACE: by HVAC] - AD, Air Dryer - As selected and approved by Company |  | EA | 18 | 2 | 4 | [38 empty] | 3 | [10 empty] | 3 | 3 | [6 empty] | 2 |  | 1
A04AV231-00001 | A | Finishing Work | Misc. Work | Paper Tower Dispenser | Stainless Steel, Surface Mounted Type | [7 empty] | EA | 8 |  |  | 8
A04AV231-00001 | B | Finishing Work | Misc. Work | Paper Tower Dispenser | Stainless Steel, Surface Mounted Type | [5 empty] | - AT, Automatic Tissue Paper Dispenser - As selected and approved by Company |  | EA | 3 |  | 2 | [57 empty] | 1
A04AV232-00001 |  | Finishing Work | Misc. Work | Paper Towel Dispenser and Waste Receptacle | Stainless Steel, Recessed Type | [7 empty] | EA | 10 | 2 | [39 empty] | 2 | [10 empty] | 2 | 2 | [6 empty] | 1 |  | 1
A04AV233-00001 |  | Finishing Work | Misc. Work | Toilet Tissue Dispenser | Stainless Steel, Surface Mounted Type | [5 empty] | - TTD, Toilet Tissue Dispenser - As selected and approved by Company during EPC |  | EA | 75 | 11 | 8 | 19 | [37 empty] | 10 | [10 empty] | 10 | 10 | [6 empty] | 4 |  | 3
A04AV237-00001 | B | Finishing Work | Misc. Work | Waste Bin | Stainless Steel | [5 empty] | - B1, Small Trash Basket – SST - 15 litres (for Enclosed & Open Plan Offices) |  | EA | 106 | 16 | 47 | [38 empty] | 14 | [10 empty] | 14 | 14 | [6 empty] | 1
A04AV237-00001 | C | Finishing Work | Misc. Work | Waste Bin | Stainless Steel | [5 empty] | - B2, Large Trash Basket Trash Basket – SST - 150 litres (for Break Room only) |  | EA | 10 | 1 | 2 | [38 empty] | 2 | [10 empty] | 2 | 2 | [6 empty] | 1
A04AV246-00001 |  | Finishing Work | Misc. Work | Non Slip Nosing | Adhesive Vinyl/Rubber Type | [7 empty] | M | 3.6 | [45 empty] | 3.6
A04AV246-00002 | B | Finishing Work | Misc. Work | Non Slip Nosing | Adhesive PVC Type | [5 empty] | DECORATIVE RUSTICATION GROOVE ■ADD |  | M | 60.6 | [61 empty] | 60.6
A04AV246-00002 | C | Finishing Work | Misc. Work | Non Slip Nosing | Adhesive PVC Type | [5 empty] | EXTERIOR CORNICE MOULDING W/ADHESIVE (100(D)X100(H)) ■ADD |  | M | 107.4 | [61 empty] | 107.4
A04AV249-00001 |  | Finishing Work | Misc. Work | Plant Box | [6 empty] | - PB, Plant Box, Pot with Plant - Plant to be suitable for indoor condition |  | EA | 9 | 9
A04BA253-00001 |  | Finishing Work | Furniture Installation | Automatic Counter Top Tea/Coffee Machine | [6 empty] | - CBM, Coffee Brewing Machine - Commercial Quality |  | EA | 13 | 1 | 2 | 2 | [37 empty] | 2 | [10 empty] | 2 | 2 | [6 empty] | 1 |  | 1
A04BA254-00001 | A | Finishing Work | Furniture Installation | Benches | [6 empty] | - BN, Bench, Lacquered Hardwood Locker Room Bench - 300mm (W) x 400mm (H) - UoM shall be 'LOT' instead of 'EA'. |  | EA | 12 | 1 | 2 | 2 | [37 empty] | 2 | [10 empty] | 2 | 2 | [6 empty] | 1
A04BA254-00001 | B | Finishing Work | Furniture Installation | Benches | [6 empty] | - BN2, Bench - Fixed Anodized Aluminum Bench w/ Back Rest 2000mm (W) |  | EA | 21 | [7 empty] | 3 | [20 empty] | 3 | 3 | 3 | 3 | 3 | 3
A04BA258-00001 | A | Finishing Work | Furniture Installation | Chairs | [6 empty] | - CH1, Ralley high back desk/work chair, w/ outerback, w/ arm, pneumatic, fabric G2 - As selected and approved by Company |  | EA | 183 | 10 | 48 | 80 | 1 | [36 empty] | 14 | [10 empty] | 14 | 14 | [6 empty] | 2
A04BA258-00001 | B | Finishing Work | Furniture Installation | Chairs | [6 empty] | - CH2, Ralley sled-base guest chair, mid- back with arm - As selected and approved by Company during EPC |  | EA | 191 | 42 | 25 | 80 | [37 empty] | 14 | [10 empty] | 14 | 14 | [6 empty] | 2
A04BA258-00001 | C | Finishing Work | Furniture Installation | Chairs | [6 empty] | - CH3, Chair - Mid-Back sled base guest chairs – armless |  | EA | 236 | 12 | 18 | 44 | 6 | 4 | [18 empty] | 4 | [12 empty] | 4 | 6 |  |  | 29 | 4 | 4 | 6 | 6 | [6 empty] | 29 | 29 | 3 |  |  |  | 3 | 3 | 16 |  | 6
A04BA258-00001 | D | Finishing Work | Furniture Installation | Chairs | [6 empty] | - CH4, Ralley Mid-Back rally work chair based on Furniture Schedule - Mid-Back rally work chair |  | EA | 38 |  | 14 | [38 empty] | 8 | [10 empty] | 8 | 8
A04BA260-00001 | A | Finishing Work | Furniture Installation | Desk | [6 empty] | - D1, Desk, one pedestal, back panel, grommet, based on Furniture Schedule - 765mm (D) x 1780mm (W) |  | EA | 35 |  | 4 | 16 | [37 empty] | 5 | [10 empty] | 5 | 5
A04BA260-00001 | B | Finishing Work | Furniture Installation | Desk | [6 empty] | - D2, Desk, one pedestal, back panel, grommet, with keyboard, based on Furniture Schedule - 765mm (D) x 1780mm (W) |  | EA | 35 |  | 4 | 16 | [37 empty] | 5 | [10 empty] | 5 | 5
A04BA260-00001 | C | Finishing Work | Furniture Installation | Desk | [6 empty] | - D3, L-Shape Desk each with 2 movable low height moveable drawers (one with 3 units & another one with 2 units) - 1830mm (W) x 765mm (D) x side desk 1985mm (W) |  | EA | 124 | 6 | 40 | 59 | 1 | [36 empty] | 6 | [10 empty] | 6 | 6
A04BA260-00001 | D | Finishing Work | Furniture Installation | Desk | [6 empty] | - D4, Radius end table, special freestanding - 1525mm (W) x 765mm (D) |  | EA | 26 | 3 | 4 | 13 | [37 empty] | 2 | [10 empty] | 2 | 2
A04BA260-00001 | E | Finishing Work | Furniture Installation | Desk | [6 empty] | - D5, Desk, no pedestal, back panel, grommet - 1145mm (W) x 765mm (D) |  | EA | 8 | 3 |  | 3 | [56 empty] | 2
A04BA260-00001 | F | Finishing Work | Furniture Installation | Desk | [6 empty] | - D6, Desk, no pedestal, back panel, grommet - 1905mm (W) x 765mm (D) |  | EA | 8 | 3 |  | 3 | [56 empty] | 2
A04BA260-00001 | G | Finishing Work | Furniture Installation | Desk | [6 empty] | - D7, Corner worksurface, laminated top with keyboard - 1145mm (W) x 765mm (D) |  | EA | 8 | 3 |  | 3 | [56 empty] | 2
A04BA260-00001 | H | Finishing Work | Furniture Installation | Desk | [6 empty] | - D8, Desk, No pedestal, Grommet - 2000mm (W) x 600mm (D) x 720mm (H) |  | EA | 1 | [59 empty] | 1
A04BA262-00001 |  | Finishing Work | Furniture Installation | Desk Top Computer & Monitor | [6 empty] | - DD, Drawing Display |  | EA | 30 |  |  |  | 2 | 2 | [18 empty] | 2 | [12 empty] | 2 | 4 |  |  |  | 2 | 2 | 4 | 4 | [8 empty] | 2 |  |  |  | 2 | 2
A04BA267-00001 | A | Finishing Work | Furniture Installation | Filing Drawers | [6 empty] | - FC, Filing Cabinet – Vertical file, 5 drawer, legal size, hanging file, lockable - 455mm (W) x 730mm (D) x 1515mm (H) |  | EA | 112 | 6 | 31 | 24 | 2 | 2 | [18 empty] | 2 | [12 empty] | 2 |  |  |  | 13 | 2 | 2 | [8 empty] | 13 | 13
A04BA267-00001 | B | Finishing Work | Furniture Installation | Filing Drawers | [6 empty] | - FC1, Pedestal, full height, with two boxes and one file drawer - 385mm (W) x 765mm (D) |  | EA | 59 | 11 | 4 | 32 | 2 | [36 empty] | 2 | [10 empty] | 2 | 2 | [6 empty] | 4
A04BA269-00001 |  | Finishing Work | Furniture Installation | Half Height Locker | [6 empty] | - L, Locker - Double tier lockers with locking option 305mm (W) x 450mm (D) x 1830mm (H) |  | EA | 378 | 38 | 50 | 80 | [37 empty] | 68 | [10 empty] | 68 | 68 | [6 empty] | 6
A04BA271-00001 |  | Finishing Work | Furniture Installation | Information Board | [6 empty] | - BO2, Notice board - Notice board A1 size |  | EA | 9 |  |  | 3 | 1 | 1 | [18 empty] | 1 | [12 empty] | 1 |  |  |  |  | 1 | 1
A04BA273-00001 |  | Finishing Work | Furniture Installation | Kitchen Sink | [6 empty] | - SK, Sink - Commercial Quality, w/ 4 nos of cabinets for base & top, Sink and Cabinets to be stainless steel - UoM shall be 'LOT' instead of 'EA'. |  | EA | 13 | 1 | 2 | 2 | [37 empty] | 2 | [10 empty] | 2 | 2 | [6 empty] | 1 |  | 1
A04BA275-00001 |  | Finishing Work | Furniture Installation | Metal Cabinet | [6 empty] | - SU-AR, Acid Resistant Cabinets, - Cabinets shall be acid resistant - 1000mm (W) x 500mm (D) x 1500mm (H) |  | EA | 17 | 1 |  |  | 1 | 1 | [18 empty] | 1 | [12 empty] | 1 | 2 |  |  |  | 1 | 1 | 2 | 2 | [8 empty] | 1 |  |  |  | 1 | 1 | 1
A04BA276-00001 |  | Finishing Work | Furniture Installation | Microwave Oven | [6 empty] | - MW, Microwave Oven - Commercial Quality, 1000W |  | EA | 13 | 1 | 2 | 2 | [37 empty] | 2 | [10 empty] | 2 | 2 | [6 empty] | 1 |  | 1
A04BA279-00001 | A | Finishing Work | Furniture Installation | Quartz Clock | [6 empty] | - C1, Wall Clock - As selected and approved by Company |  | EA | 58 | 6 | 10 | 19 | 1 | [36 empty] | 7 | [10 empty] | 7 | 7 | [6 empty] | 1
A04BA279-00001 | B | Finishing Work | Furniture Installation | Quartz Clock | [6 empty] | - C2, Prayer Clock - As selected and approved by Company |  | EA | 9 | 1 | 2 | 1 | [37 empty] | 1 | [10 empty] | 1 | 1 | [6 empty] | 1 |  | 1
A04BA281-00001 |  | Finishing Work | Furniture Installation | Refrigerator | [6 empty] | - REF, Refrigerator - Commercial Quality – 0.51 m³ (18 ft³) |  | EA | 31 | 2 | 2 | 2 | [37 empty] | 8 | [10 empty] | 8 | 8 | [6 empty] | 1
A04BA283-00001 | A | Finishing Work | Furniture Installation | Sofa | [6 empty] | - SO1, One-Seater Sofa - Type to Company approval |  | EA | 4 | 4
A04BA283-00001 | B | Finishing Work | Furniture Installation | Sofa | [6 empty] | - SO2, Two-Seater Sofa - Type to Company approval |  | EA | 6 | 4 |  | 2
A04BA284-00001 | A | Finishing Work | Furniture Installation | Storage Cabinets(Bookcase) | [6 empty] | - BCU1, Bookcase Unit, Open, w/ 4 adjustable shelves - 915mm (W) x 380mm (D) x 1830mm (H) |  | EA | 120 | 17 | 20 | 54 | [37 empty] | 9 | [10 empty] | 9 | 9 | [6 empty] | 2
A04BA284-00001 | B | Finishing Work | Furniture Installation | Storage Cabinets(Bookcase) | [6 empty] | - BCU2, Bookcase Unit, Open, w/ 2 rows - 3000mm (L) x 305mm (D) x 610mm (H) |  | EA | 6 |  | 1 | 2 | [37 empty] | 1 | [10 empty] | 1 | 1
A04BA284-00001 | C | Finishing Work | Furniture Installation | Storage Cabinets(Bookcase) | [6 empty] | - BCU2A, Bookcase Unit, Open, w/ 2 rows - 2900mm (L) x 305mm (D) x 610mm (H) |  | EA | 2 | 2
A04BA284-00001 | D | Finishing Work | Furniture Installation | Storage Cabinets(Bookcase) | [6 empty] | - BCU2B, Bookcase Unit, Open, w/ 2 rows - 1700mm (L) x 305mm (D) x 610mm (H) |  | EA | 1 | [59 empty] | 1
A04BA284-00001 | E | Finishing Work | Furniture Installation | Storage Cabinets(Bookcase) | [6 empty] | - BCU2C, Bookcase Unit, Open, w/ 2 rows - 800mm (L) x 305mm (D) x 610mm (H) |  | EA | 1 | [61 empty] | 1
A04BA284-00001 | F | Finishing Work | Furniture Installation | Storage Cabinets(Bookcase) | [6 empty] | - BCU3, Bookcase Unit, Open, w/ 5 rows, Heavy Duty Steel - 305mm (D) x 1980mm (H) - UoM shall be 'LOT' instead of 'EA'. |  | EA | 11 | 1 | 1 | 8 | [56 empty] | 1
A04BA284-00001 | G | Finishing Work | Furniture Installation | Storage Cabinets(Bookcase) | [6 empty] | - BCU4, Bookcase Unit, Open, w/ 3 rows, Heavy Duty Steel - To be matched with 'BCU3' - 305mm (D) x 1000mm (H) - UoM shall be 'LOT' instead of 'EA'. |  | EA | 1 | 1
A04BA284-00001 | H | Finishing Work | Furniture Installation | Storage Cabinets(Bookcase) | [6 empty] | - BCU2D, Bookcase Unit, Open, w/ 2 rows - 1000mm (L) x 305mm (D) x 610mm (H) |  | EA | 1 |  | 1
A04BA286-00001 | A | Finishing Work | Furniture Installation | Table | [6 empty] | - CO1, Coffee Table - Type to Company Approval |  | EA | 4 | 3 |  | 1
A04BA286-00001 | B | Finishing Work | Furniture Installation | Table | [6 empty] | - CT, Conference Table - Conference Table for 18 seats |  | EA | 2 | 1 | 1
A04BA286-00001 | C | Finishing Work | Furniture Installation | Table | [6 empty] | - T1, Table - 1400mm diameter table with enamel painted steel legs |  | EA | 26 | 6 |  | 4 | [34 empty] | 2 |  |  | 1 |  |  | 2 | 2 | [6 empty] | 1 | 1 | 1 |  |  |  | 1 | 1 | 4
A04BA286-00001 | D | Finishing Work | Furniture Installation | Table | [6 empty] | - T2, Conference Table (10 Person), based on Furniture Schedule - 4no. 1200mm (W) x 700mm (D) squared conference tops w/ 2no. 1400mm dia. half round extensions. - Table tops supported on standard and shared legs |  | EA | 3 | [40 empty] | 1 | [10 empty] | 1 | 1
A04BA286-00001 | E | Finishing Work | Furniture Installation | Table | [6 empty] | - T3, Table, based on Furniture Schedule - 4 leg straight table 1800mm x 800mm |  | EA | 15 |  | 3 | [38 empty] | 4 | [10 empty] | 4 | 4
A04BA286-00001 | F | Finishing Work | Furniture Installation | Table | [6 empty] | - T4, Table, based on Furniture Schedule - 4 leg straight desk 1200mm x 800mm – heavy duty to station centralized printer |  | EA | 18 |  | 3 | 6 | 1 | 1 | [18 empty] | 1 | [12 empty] | 1 |  |  |  | 1 | 1 | 1 | [8 empty] | 1 | 1
A04BA286-00001 | G | Finishing Work | Furniture Installation | Table | [6 empty] | - T7, Table, based on Furniture Schedule - 4 leg straight table 800mm x 800mm |  | EA | 3 | [61 empty] | 3
A04BA286-00001 | H | Finishing Work | Furniture Installation | Table | [6 empty] | - CT1, Conference Table - Conference Table for 14 seats |  | EA | 2 |  |  | 2
A04BA289-00001 |  | Finishing Work | Furniture Installation | Visitors Chairs | [6 empty] | - WRC, Waiting Room Chair - Commercial Quality, 1 row w/ 6 seats |  | EA | 2 | [59 empty] | 2
A04BA292-00001 |  | Finishing Work | Furniture Installation | Water Cooler | [6 empty] | - DIS, Water Dispenser - Commercial Quality |  | EA | 11 | 1 | 2 | 2 | [37 empty] | 2 | [10 empty] | 2 | 2
A04BA293-00001 | A | Finishing Work | Furniture Installation | White Board | [6 empty] | - BO1, White Board - Magnetic white board with 4 erasers and 32 markers – 4 colours |  | EA | 56 | 1 | 4 | 21 | 1 | 1 | [18 empty] | 1 | [12 empty] | 1 |  |  |  | 8 | 1 | 1 | [8 empty] | 8 | 8
A04BA293-00001 | B | Finishing Work | Furniture Installation | White Board | [6 empty] | - DEB, Dry Erase Board, Blank dry erase surface board w/ aluminum frame and eraser tray - 600mm(W) x 900mm(H) |  | EA | 8 | 4 | 1 | 2 | [56 empty] | 1
A04BA294-00001 | A | Finishing Work | Furniture Installation | Rack | [6 empty] | - SH, Shoe Rack - for 60 people, 5 rows - 3750mm (W) x 350mm (D) x 1500mm (H) - UoM shall be 'LOT' instead of 'EA'. |  | EA | 1 |  |  | 1
A04BA294-00001 | B | Finishing Work | Furniture Installation | Rack | [6 empty] | - SH1, Shoe Rack - for 60 people, 4 rows - 3750mm (W) x 350mm (D) x 1200mm (H) - UoM shall be 'LOT' instead of 'EA'. |  | EA | 1 | 1
A04BA294-00001 | C | Finishing Work | Furniture Installation | Rack | [6 empty] | - SH2, Shoe Rack - for 60 people, 5 rows - 3000mm (W) x 350mm (D) x 1500mm (H) - UoM shall be 'LOT' instead of 'EA'. |  | EA | 3 | [40 empty] | 1 | [10 empty] | 1 | 1
A04BA294-00001 | D | Finishing Work | Furniture Installation | Rack | [6 empty] | - SH3, Shoe Rack - for 12 people, 6 rows - 500mm (W) x 350mm (D) x 1800mm (H) - UoM shall be 'LOT' instead of 'EA'. |  | EA | 2 | [59 empty] | 1 |  | 1
A04BA294-00001 | E | Finishing Work | Furniture Installation | Rack | [6 empty] | - SH4, Shoe Rack - for 48 people, 6 rows - 2000mm (W) x 350mm (D) x 1200mm (H) - UoM shall be 'LOT' instead of 'EA'. |  | EA | 1 |  | 1
A04BA294-00001 | F | Finishing Work | Furniture Installation | Rack | [6 empty] | - SH5, Shoe Rack - for 12 people, 4 rows - 750mm (W) x 350mm (D) x 1200mm (H) - UoM shall be 'LOT' instead of 'EA'. |  | EA | 1 |  | 1
A04BA296-00001 | A | Finishing Work | Furniture Installation | Others | [6 empty] | - CR, Credenza - 1585mm (W) x 520mm (D) x 800mm (H) |  | EA | 12 | 3 | 1 | 5 | [37 empty] | 1 | [10 empty] | 1 | 1
A04BA296-00001 | B | Finishing Work | Furniture Installation | Others | [6 empty] | - DH, Drawing Hanger - Commercial Quality – moveable |  | EA | 20 |  | 1 |  | 2 | 1 | [18 empty] | 1 | [12 empty] | 1 | 2 |  |  | 1 | 1 | 1 | 2 | 2 | [6 empty] | 1 | 1 | 1 |  |  |  | 1 | 1
A04BA296-00001 | C | Finishing Work | Furniture Installation | Others | [6 empty] | - HDSS1, Heavy Duty Shelf - steel - 410mm (D) x 2010mm (H) - 3 shelves per row - UoM shall be 'LOT' instead of 'EA'. |  | EA | 41 | 3 | 5 | 11 | [37 empty] | 6 | [10 empty] | 6 | 6 | [6 empty] | 4
A04BA296-00001 | D | Finishing Work | Furniture Installation | Others | [6 empty] | - HDSS2, Heavy Duty Shelf - steel - 410mm (D) x 2010mm (H) - 3 shelves per row - UoM shall be 'LOT' instead of 'EA'. |  | EA | 7 |  |  | 7
A04BA296-00001 | E | Finishing Work | Furniture Installation | Others | [6 empty] | - HDSS3, Heavy Duty Shelf - steel - 1195mm (W) x 1020mm (H) x 2010mm (L) - UoM shall be 'LOT' instead of 'EA'. |  | EA | 7 |  |  | 7
A04BA296-00001 | F | Finishing Work | Furniture Installation | Others | [6 empty] | - ICM, Ice Maker - Commercial Quality |  | EA | 13 | 1 | 2 | 2 | [37 empty] | 2 | [10 empty] | 2 | 2 | [6 empty] | 1 |  | 1
A04BA296-00001 | G | Finishing Work | Furniture Installation | Others | [6 empty] | - K, Kettle - Commercial Quality |  | EA | 13 | 1 | 2 | 2 | [37 empty] | 2 | [10 empty] | 2 | 2 | [6 empty] | 1 |  | 1
A04BA296-00001 | H | Finishing Work | Furniture Installation | Others | [6 empty] | - PD, Podium - Commercial Quality – 510mm (W) x 510mm (D) x 1220mm (H) |  | EA | 7 | 1 | 1 | 2 | [37 empty] | 1 | [10 empty] | 1 | 1
A04BA296-00001 | I | Finishing Work | Furniture Installation | Others | [6 empty] | - PWS, Projector w/ Screen - Commercial Quality, Movable Screen |  | EA | 7 | 1 | 1 | 2 | [37 empty] | 1 | [10 empty] | 1 | 1
A04BA296-00001 | J | Finishing Work | Furniture Installation | Others | [6 empty] | - SB, Smart Board - Commercial Quality |  | EA | 11 | 2 | 1 | 5 | [37 empty] | 1 | [10 empty] | 1 | 1
A04BA296-00001 | K | Finishing Work | Furniture Installation | Others | [6 empty] | - SU, Storage Unit - Double door storage Unit - 800mm (W) x 400mm (D) x 1600mm (H) |  | EA | 24 | 16 |  | 8
A04BA296-00001 | L | Finishing Work | Furniture Installation | Others | [6 empty] | - TV1, TV - 2035mm LED screen |  | EA | 5 | 1 | 1 | 3
A04BA296-00001 | M | Finishing Work | Furniture Installation | Others | [6 empty] | - ELS, Electric Stove-ceramic built-in - Commercial quality |  | EA | 12 | 1 | 2 | 2 | [37 empty] | 2 | [10 empty] | 2 | 2 | [6 empty] | 1
A04BA296-00001 | N | Finishing Work | Furniture Installation | Others | [6 empty] | - EXH, Extractor Hood - Commercial Quality - The followings to be included: 1. Hood 2. Total exhuast duct system from hood to outdoor incl. SST duct, exhaust fan, MGD 3. I/O points for fan-off & MGD-close - UoM shall be 'LOT' instead of 'EA'. |  | EA | 12 | 1 | 2 | 2 | [37 empty] | 2 | [10 empty] | 2 | 2 | [6 empty] | 1
A04BA296-00001 | O | Finishing Work | Furniture Installation | Others | [6 empty] | - AST, Ashtray - Fixed Concrete Ashtray 300mm (W) x 300mm (D) x 600mm (H) |  | EA | 21 | [7 empty] | 3 | [20 empty] | 3 | 3 | 3 | 3 | 3 | 3
A04BD308-00001 |  | Finishing Work | Work for Ergonomic/Sustainable Design | Ergonomic Designed Area | for Floor | [5 empty] | - Detailed requirements to be defined during Detailed Engineering |  | M2 | 1886.62 | 1743.52 | [58 empty] | 143.1
A04BD308-00002 |  | Finishing Work | Work for Ergonomic/Sustainable Design | Ergonomic Designed Area | for Wall | [5 empty] | - Detailed requirements to be defined during Detailed Engineering |  | M2 | 1573.5 | 1418.4 | [58 empty] | 155.1
A04BD308-00003 |  | Finishing Work | Work for Ergonomic/Sustainable Design | Ergonomic Designed Area | for Ceiling | [5 empty] | - Detailed requirements to be defined during Detailed Engineering |  | M2 | 1886.62 | 1743.52 | [58 empty] | 143.1
A05ZZ199-00005 |  | Cladding Work | - | Single Metal Sheet | Corrugated Galvanized Steel Sheet | for Wall | w/ Accessories, Flashing |  |  |  | - THK=0.5mm |  | M2 | 341.52 | [18 empty] | 67.8 | 48.67 | 48.67 | 62.4 | 56.99 | [11 empty] | 56.99
A05ZZ199-00006 |  | Cladding Work | - | Single Metal Sheet | Corrugated Galvanized Steel Sheet | for Roof | w/ Accessories, Flashing |  |  |  | - THK=0.5mm |  | M2 | 958.79 |  | 114.4 | [16 empty] | 63.8 | 40.02 | 40.02 | 54.52 | 45.24 | [11 empty] | 45.24 | [15 empty] | 555.55
A05ZZ200-00025 |  | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | Glass Wool (Fiberglass) | for Wall | w/ Accessories, Flashing | 50mm≤THK<70mm |  | - THK=50mm - R-16 | I-10C | M2 | 440.58 | [6 empty] | 116.6 | 13.44 | [19 empty] | 116.6 | 13.44 | 13.44 | 13.44 | 13.44 | 13.44 | 13.44 | [11 empty] | 113.3
A05ZZ200-00027 |  | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | Glass Wool (Fiberglass) | for Wall | w/ Accessories, Flashing | 100mm≤THK<150mm |  | - THK=120mm - R-16 |  | M2 | 2629.84 |  |  | 2629.84
A05ZZ200-00029 |  | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | Glass Wool (Fiberglass) | for Roof | w/ Accessories, Flashing | 50mm≤THK<70mm |  | [Not Applicable to SACE] - THK=50mm - R-19 |  | M2 | 999.98 | [62 empty] | 999.98
A05ZZ200-00031 |  | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | Glass Wool (Fiberglass) | for Roof | w/ Accessories, Flashing | 100mm≤THK<150mm |  | - THK=100mm - R-19 | I-10D | M2 | 555.48 | [6 empty] | 112.36 | 31.36 | [19 empty] | 112.36 | 31.36 | 31.36 | 31.36 | 31.36 | 31.36 | 31.36 | [11 empty] | 111.24
A05ZZ200-00032 |  | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | Glass Wool (Fiberglass) | for Roof | w/ Accessories, Flashing | 150mm≤THK |  | - THK=200mm - R-19 |  | M2 | 5122.3 |  |  | 5122.3
A05ZZ203-00001 |  | Cladding Work | - | Fabric Roof | Fabric Type | for Car Parking Shelter | w/ Accessories |  |  |  | - Commercial Grade |  | M2 | 2890.8 | [8 empty] | 402 | 180 | 258 | 180 | 180 | 360 | 60 | 60 | 120 | 154.8 | [20 empty] | 108 | [7 empty] | 144 | 198 | 90 | 36 |  |  |  |  | 36 | 36 | 36 |  |  |  | 252
A05ZZ204-00001 |  | Cladding Work | - | Gutter | Galvanized Steel Eave Gutter w/ Coating | w/ Accessories |  |  |  |  | - THK=Min. 0.7mm |  | M | 452.6 |  | 28.6 | 181 |  |  |  | 10.6 | 5.6 | [10 empty] | 11 | 6.9 | 6.9 | 9.4 | 7.8 |  |  |  |  | 10.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 7.8 | [10 empty] | 10.3 |  |  |  |  | 43.2 | [11 empty] | 79.3
F01AB000-00004 |  | Building/Shelter Fire Proofing Work | Lightweight Cementitious | - | 2 hr. rating (UL 1709) | [5 empty] | - Fireproofing Application including Related Materials shall be as per Manufacturer's Recommendations and Personnel trained & certified by Manufacturer - Profiled Type to be applied when Steel Depth is greater than 200mm (Others: Non-profiled Type) - Refer to TA-683511-001 (Fireproofing Details) |  | M2 | 761.178 | [50 empty] | 761.178
S01AA001-00001 |  | Main Steel Structure Fabrication Work | Shelter/Building | Heavy Steel - Standard (Weight≥90KG/M) | [6 empty] | - Steel for W- and WT- sections, plate girders: Grade 50 conforming to ASTM A992/A992M - Steel for M, S, HP, C, MC, L shapes: Grade 36 conforming to ASTM A36/A36M - Incl. H/S Bolts&Nuts, Common Bolts&Nuts | J-01 | TON | 549.71 | 37.686 |  | 241.603 | 59.003 | 0.295 |  | 7.476 |  | 3.23 | 2.853 | 2.826 | 2.853 | 2.853 | 2.826 | 0.807 | 0.807 | 1.211 | 1.615 | 0.31 | 0.311 | 0.311 | 0.311 | 0.311 | 0.295 |  |  |  | 7.476 | [6 empty] | 0.311 |  |  |  | 1.902 |  | 4.332 |  |  |  |  | 7.857 | 1.615 | 3.329 | 1.902 | 0.951 | 25.792 | 4.332 | 4.332 |  | 0.951 | 0.951 | 0.951 |  |  |  | 3.804 |  | 109.129
S01AA002-00001 |  | Main Steel Structure Fabrication Work | Shelter/Building | Medium Steel - Standard (90KG/M>Weight≥30KG/M) | [6 empty] | - Steel for W- and WT- sections, plate girders: Grade 50 conforming to ASTM A992/A992M - Steel for M, S, HP, C, MC, L shapes: Grade 36 conforming to ASTM A36/A36M - Incl. H/S Bolts&Nuts, Common Bolts&Nuts | J-01 | TON | 489.703 | 4.29 | 4.485 | 240.835 | 43.946 |  | 0.614 | 2.6 |  | 11.747 |  | 8.286 |  |  | 10.383 | 1.993 | 1.993 | 3.671 | 4.908 | 4.937 | 3.502 | 3.502 | 4.497 | 3.703 |  | 0.614 | 0.614 | 0.712 | 2.6 | [6 empty] | 3.703 | 0.614 |  |  |  | 1.444 | [5 empty] | 2.678 | 4.72 |  |  |  | 30.909 | [11 empty] | 81.203
S01AA003-00001 |  | Main Steel Structure Fabrication Work | Shelter/Building | Light Steel - Standard (30KG/M>Weight) | [6 empty] | - Steel for W- and WT- sections, plate girders: Grade 50 conforming to ASTM A992/A992M - Steel for Plates, M, S, HP, C, MC, L shapes: Grade 36 conforming to ASTM A36/A36M - Incl. H/S Bolts&Nuts, Common Bolts&Nuts | J-01 | TON | 138.916 |  | 1.534 | 20.963 | 24.801 | 10.274 | 0.098 | 0.274 | 1.125 | 0.752 | 1.927 | 0.658 | 1.927 | 1.927 | 0.658 | 0.188 | 0.188 | 0.282 | 0.376 | 0.837 | 0.462 | 0.462 | 0.758 | 0.503 | 10.274 | 0.098 | 0.098 | 0.098 | 0.274 | 1.125 | 1.125 | 1.125 | 1.125 | 1.125 | 1.125 | 0.503 | 0.098 | 0.92 | 0.197 | 1.271 | 0.098 | 0.446 | 1.061 | 0.54 | 0.197 | 0.197 | 0.769 | 0.376 | 2.191 | 1.139 | 0.526 | 14.103 | 0.446 | 0.446 | 0.197 | 0.526 | 0.526 | 0.526 | 0.197 | 0.197 | 0.197 | 2.629 | 0.098 | 19.733
S01AA007-00001 |  | Main Steel Structure Fabrication Work | Shelter/Building | Girth & Purlin | [6 empty] | - Material: ASTM A653 - Hot-Dip Galvanizing w/ APCS-26 in accordance with SAES-H-001, Section 7.1-B8 & Section 7.1-H5 - Incl. Common Bolts&Nuts | J-01 | TON | 84.24 |  | 0.875 | 49.61 |  |  |  | 2.774 | 0.589 | [10 empty] | 1.382 | 0.92 | 0.92 | 1.219 | 0.993 |  |  |  |  | 2.774 | 0.589 | 0.589 | 0.589 | 0.589 | 0.589 | 0.589 | 0.993 | [10 empty] | 2.546 |  |  |  |  | 4.074 | [11 empty] | 11.037
S01AA009-00001 |  | Main Steel Structure Fabrication Work | Shelter/Building | Plates - Gusset, Stiffener, ETC | [6 empty] | - Material: Grade 36 conforming to ASTM A36/A36M | J-01 | TON | 126.098 | 4.198 | 0.602 | 50.34 | 13.274 | 1.057 | 0.086 | 1.169 | 0.243 | 1.92 | 0.716 | 1.48 | 0.716 | 0.716 | 1.69 | 0.386 | 0.386 | 0.646 | 0.863 | [5 empty] | 1.057 | 0.086 | 0.086 | 0.096 | 1.169 | 0.243 | 0.243 | 0.243 | 0.243 | 0.243 | 0.243 |  | 0.086 | 0.098 | 0.023 | 0.476 | 0.169 | 0.624 | 0.112 | 0.06 | 0.023 | 0.023 | 1.265 | 0.844 | 0.83 | 0.463 | 0.227 | 8.745 | 0.624 | 0.624 | 0.023 | 0.227 | 0.227 | 0.227 | 0.023 | 0.023 | 0.023 | 0.962 | 0.011 | 24.596
S01AA010-00002 |  | Main Steel Structure Fabrication Work | Shelter/Building | Steel Painting/Coating | for Fireproofed Steel Surface, Surface Preparation & Primer Coat | [5 empty] | - Material: ( ) |  | M2 | 837.295 | [50 empty] | 837.295
S01AA010-00004 |  | Main Steel Structure Fabrication Work | Shelter/Building | Steel Painting/Coating | Hot-Dip Galvanizing w/ Surface Preparation and Additional Painting Coat | [5 empty] | - Hot-Dip Galv. in accordance with SAES-H-001 - APCS-26 in accordance with SAES-H-001, Section 7.1-B8 & Section 7.1-H5 |  | M2 | 35855.006 | 771.568 | 295.363 | 17109.52 | 3605.495 | 359.431 | 3.62 | 545.817 | 107.366 | 190.616 | 84.791 | 142.963 | 84.791 | 84.794 | 168.043 | 36.368 | 36.368 | 62.703 | 83.771 | 309.7 | 209.764 | 209.764 | 277.476 | 234.403 | 359.431 | 3.62 | 4.29 | 24.168 | 545.817 | 107.366 | 107.366 | 107.366 | 107.366 | 107.366 | 107.366 | 234.403 | 4.29 | 31.39 | 7.374 | 54.736 | 45.605 | 109.005 | 37.159 | 22.17 | 7.374 | 7.374 | 585.548 | 81.514 | 97.137 | 52.028 | 24.661 | 1331.775 | 109.005 | 109.005 | 7.374 | 24.661 | 24.661 | 24.661 | 7.374 | 7.374 | 7.374 | 114.884 | 3.687 | 6085.386
S02AA017-00001 |  | Miscellaneous Steel Fabrication Work | Shelter/Building | Checkered/Flooring Plate | [6 empty] | - Material: ASTM A786M Pattern 4 or 5 and ASTM A36M Material - THK=6mm, Hot-Dip Galvanized | J-05 | M2 | 229.2 |  |  |  |  | 16.2 | 26.26 | [17 empty] | 16.2 | 34.39 | 26.26 | 28.36 | [8 empty] | 38.77 | 3.86 |  |  | 23.46 |  | 7.72 | 7.72
S02AA018-00001 |  | Miscellaneous Steel Fabrication Work | Shelter/Building | Grating | [6 empty] | - Material: ASTM A1011/A1011M - THK=32mm 5x32mm Bearing Bars, 30mm Pitch and Cross Bars 100mm C/C | J-04 | M2 | 1778.24 | 12.41 | 3.12 | 126.9 | 175.99 | 233.2 | 1.62 | [12 empty] | 26.22 | 16.27 | 16.27 | 22.38 | 18.54 | 233.2 | 1.62 | 1.62 | 1.62 | [7 empty] | 18.54 | 1.62 | 38.11 | 3.1 |  | 1.67 | 3.87 | 57.11 | 43.75 | 3.1 | 3.1 | [5 empty] | 80.89 | 3.87 | 3.87 | 3.1 |  |  |  | 3.1 | 3.1 | 21.14 |  | 1.57 | 592.65
S02AA020-00001 | A | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Handrails | [6 empty] | [Handrail] - Material: ASTM A53/A53M Type E or S, Grade B. ASTM A106/A106M Grade B - Hot-Dip Galvanized & Painted - H=870mm | J-06 | M | 271.12 |  |  |  | 126 | [14 empty] | 6.4 | 3.2 | 3.2 | 6.4 | 6.4 | [11 empty] | 6.4 | [15 empty] | 113.12
S02AA020-00001 | B | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Handrails | [6 empty] | [Guardrail w/ Handrail] - Material: ASTM A53/A53M Type E or S, Grade B. ASTM A106/A106M Grade B - Hot-Dip Galvanized & Painted - H=1070mm |  | M | 761.82 | 33.2 | 6.88 | 156.8 | 156 | 19 | 4 | [17 empty] | 19 | 4 | 4 | 4 | [8 empty] | 4 | 15.08 | 23.94 |  | 4 | 10.59 | 15.07 | 15.07 | 23.94 | 23.94 | 6 |  |  |  |  | 25.76 | 10.59 | 10.59 | 16.02 |  |  |  | 16.02 | 16.02 | 28.01 |  | 4.06 | 86.24
S02AA020-00001 | C | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Handrails | [6 empty] | [Guardrail] - Material: ASTM A53/A53M Type E or S, Grade B. ASTM A106/A106M Grade B - Hot-Dip Galvanized & Painted - H=1070mm |  | M | 758.57 |  |  |  | 144 | [14 empty] | 23.8 | 16.5 | 16.5 | 20.6 | 17.4 | [11 empty] | 17.4 |  |  | 15.58 | [5 empty] | 15.58 | 15.78 | [5 empty] | 90.22 |  |  | 7.84 |  |  |  | 7.84 | 7.84 | 16.8 |  |  | 324.89
S02AA021-00001 |  | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Handrails - Removable | [6 empty] | [Removable Guardrail] - Material: ASTM A53/A53M Type E or S, Grade B. ASTM A106/A106M Grade B - Hot-Dip Galvanized & Painted - H=1070mm | J-06 | M | 25.7 | [37 empty] | 4.8 | [5 empty] | 4.8 | 4.8 | [5 empty] | 1.7 |  |  | 2.4 |  |  |  | 2.4 | 2.4 | 2.4
S02AA022-00001 | B | Miscellaneous Steel Fabrication Work | Shelter/Building | Stainless Steel Handrail | [6 empty] | [Guardrail w/ Handrail] - H=1070mm - Decorative Type and Commercial Grade |  | M | 126.6 | 126.6
S02AA022-00001 | C | Miscellaneous Steel Fabrication Work | Shelter/Building | Stainless Steel Handrail | [6 empty] | [Guardrail] - H=1070mm - Decorative Type and Commercial Grade |  | M | 16.7 | 16.7
S02AA022-00001 | D | Miscellaneous Steel Fabrication Work | Shelter/Building | Stainless Steel Handrail | [6 empty] | [Removable Guardrail] - H=1070mm - Decorative Type and Commercial Grade |  | M | 6.6 | 6.6
S02AA023-00001 | A | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Ladder | With Cage | [5 empty] | - Material: ASTM A36/A36M - H (Landing to Landing) <9m - Hot-Dip Galvanized & Painted - Side-Step Type - incl. Safety Gate | J-10 | M | 509.13 |  | 16.9 | 94.14 | 63.75 | 18.86 | 8.4 | [17 empty] | 18.86 | 8.4 | 8.4 | 9.3 | [8 empty] | 8.4 | 19.7 | 19.4 |  | 9.3 | 6.12 | 19.7 | 19.7 | 19.4 | 19.4 | [5 empty] | 9.2 | 6.12 | 6.12 | 19.4 |  |  |  | 19.4 | 19.4 | 19.9 |  | 6.5 | 14.96
S02AA023-00001 | B | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Ladder | With Cage | [5 empty] | - Material: ASTM A36/A36M - H (Landing to Landing) ≥9m - Hot-Dip Galvanized & Painted - Side-Step Type - incl. Platform, Safety Gate | J-10 | M | 90.9 | 24 |  |  | 34.8 | [36 empty] | 10.7 | [10 empty] | 10.7 | 10.7
S02AA023-00002 |  | Miscellaneous Steel Fabrication Work | Shelter/Building | Steel Ladder | Without Cage | [5 empty] | - Material: ASTM A36/A36M - Hot-Dip Galvanized & Painted - Side-Step Type | J-10 | M | 9.15 | [50 empty] | 9.15
S02AA024-00001 |  | Miscellaneous Steel Fabrication Work | Shelter/Building | Galvanized Steel Deck Plate | [6 empty] | - Plate THK=1.6mm, Rib Depth=75mm - ASTM A653M or ASTM A1008M w/ Min. Yield-Strength of 228MPa - incl. Stud Bolts and Side Molding |  | M2 | 3238.85 | 640.77 |  | 2598.08
S02AA025-00003 |  | Miscellaneous Steel Fabrication Work | Shelter/Building | Anchor Bolt (Straight Type) | M20 | [5 empty] | - L=460mm | J-02 | EA | 1052 |  | 20 | 320 | 208 |  |  | 40 | [11 empty] | 48 | 48 | 48 | 48 | 48 |  |  |  |  | 40 | [6 empty] | 48 | [5 empty] | 32 |  |  |  |  | 40 | [5 empty] | 32 | 32
S02AA025-00005 |  | Miscellaneous Steel Fabrication Work | Shelter/Building | Anchor Bolt (Straight Type) | M24 | [5 empty] | - L=530mm | J-02 | EA | 812 | [8 empty] | 64 | 48 | 56 | 48 | 48 | 56 | 16 | 16 | 24 | 32 | [13 empty] | 16 | 16 | 16 |  |  |  |  | 32 | [7 empty] | 32 | 56 | 32 | 16 | 68 |  |  |  | 16 | 16 | 16 |  |  |  | 64 |  | 8
S02AA025-00006 |  | Miscellaneous Steel Fabrication Work | Shelter/Building | Anchor Bolt (Straight Type) | M30 | [5 empty] | - L=620mm | J-02 | EA | 40 | 16 |  | 24
S02AA025-00008 |  | Miscellaneous Steel Fabrication Work | Shelter/Building | Anchor Bolt (Straight Type) | M36 | [5 empty] | - L=720mm |  | EA | 216 | [50 empty] | 72 | [11 empty] | 144
S02AA025-00017 |  | Miscellaneous Steel Fabrication Work | Shelter/Building | Anchor Bolt (Straight Type) | M27 | [5 empty] | - Material: ( ) |  | EA | 216 |  |  | 64 | 152
S03AA007-00001 |  | Main Steel Structure Erection Work | Shelter/Building | Girth & Purlin | [6 empty] | - Material: ASTM A653 - Hot-Dip Galvanizing w/ APCS-26 in accordance with SAES-H-001, Section 7.1-B8 & Section 7.1-H5 - Incl. Common Bolts&Nuts | J-01 | TON | 84.24 |  | 0.875 | 49.61 |  |  |  | 2.774 | 0.589 | [10 empty] | 1.382 | 0.92 | 0.92 | 1.219 | 0.993 |  |  |  |  | 2.774 | 0.589 | 0.589 | 0.589 | 0.589 | 0.589 | 0.589 | 0.993 | [10 empty] | 2.546 |  |  |  |  | 4.074 | [11 empty] | 11.037
S03AA027-00001 |  | Main Steel Structure Erection Work | Shelter/Building | Heavy Steel (Weight≥90KG/M) | [6 empty] | - Steel for W- and WT- sections, plate girders: Grade 50 conforming to ASTM A992/A992M - Steel for M, S, HP, C, MC, L shapes: Grade 36 conforming to ASTM A36/A36M - Incl. H/S Bolts&Nuts, Common Bolts&Nuts | J-01 | TON | 609.426 | 41.455 | 0 | 265.763 | 65.134 | 0.325 | 0 | 8.32 | 0 | 3.624 | 3.28 | 3.181 | 3.28 | 3.28 | 3.17 | 0.911 | 0.911 | 1.362 | 1.817 | 0.31 | 0.311 | 0.311 | 0.311 | 0.311 | 0.325 | 0 | 0 | 0 | 8.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0.311 | 0 | 0 | 0 | 2.187 | 0 | 4.898 | 0 | 0 | 0 | 0 | 8.736 | 1.818 | 3.83 | 2.192 | 1.097 | 28.978 | 4.898 | 4.898 | 0 | 1.097 | 1.097 | 1.097 | 0 | 0 | 0 | 4.373 | 0 | 121.907
S03AA028-00001 |  | Main Steel Structure Erection Work | Shelter/Building | Medium Steel (90KG/M>Weight≥30KG/M) | [6 empty] | - Steel for W- and WT- sections, plate girders: Grade 50 conforming to ASTM A992/A992M - Steel for M, S, HP, C, MC, L shapes: Grade 36 conforming to ASTM A36/A36M - Incl. H/S Bolts&Nuts, Common Bolts&Nuts | J-01 | TON | 539.904 | 4.719 | 4.934 | 264.918 | 48.512 | 0 | 0.688 | 2.894 | 0 | 13.181 | 0 | 9.328 | 0 | 0 | 11.648 | 2.25 | 2.25 | 4.13 | 5.522 | 4.937 | 3.502 | 3.502 | 4.497 | 3.703 | 0 | 0.688 | 0.688 | 0.796 | 2.894 | 0 | 0 | 0 | 0 | 0 | 0 | 3.703 | 0.688 | 0 | 0 | 0 | 1.602 | 0 | 0 | 0 | 0 | 0 | 2.978 | 5.314 | 0 | 0 | 0 | 34.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.711
S03AA029-00001 |  | Main Steel Structure Erection Work | Shelter/Building | Light Steel (30KG/M>Weight) | [6 empty] | - Steel for W- and WT- sections, plate girders: Grade 50 conforming to ASTM A992/A992M - Steel for M, S, HP, C, MC, L shapes: Grade 36 conforming to ASTM A36/A36M - Incl. H/S Bolts&Nuts, Common Bolts&Nuts | J-01 | TON | 155.093 | 0 | 1.687 | 23.059 | 27.378 | 11.301 | 0.11 | 0.305 | 1.368 | 0.844 | 2.216 | 0.741 | 2.216 | 2.216 | 0.738 | 0.212 | 0.212 | 0.317 | 0.423 | 0.837 | 0.462 | 0.462 | 0.758 | 0.503 | 11.301 | 0.11 | 0.11 | 0.11 | 0.305 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 0.503 | 0.11 | 1.018 | 0.22 | 1.462 | 0.109 | 0.504 | 1.173 | 0.6 | 0.22 | 0.22 | 0.855 | 0.423 | 2.52 | 1.312 | 0.607 | 15.845 | 0.504 | 0.504 | 0.22 | 0.607 | 0.607 | 0.607 | 0.22 | 0.22 | 0.22 | 3.022 | 0.109 | 22.043
S03AA030-00001 |  | Main Steel Structure Erection Work | Shelter/Building | Non-Shrink Grouting | [6 empty] | - THK=25mm - Min. 28 days Compressive Strength: 35MPa | J-03 | M3 | 11.9 | 0.42 | 2.12 | 1.26 | 1.97 | 1.25 | 0.05 | 0.08 | 0.02 | 0.07 | 0.05 | 0.06 | 0.05 | 0.05 | 0.06 | 0.02 | 0.02 | 0.03 | 0.04 | 0.08 | 0.08 | 0.08 | 0.08 | 0.1 | 0.1 | 0.05 | 0.05 | 0.58 | 0.08 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.05 |  |  | 0.04 | 0.5 | 0.06 |  |  |  |  | 0.38 | 0.04 | 0.06 | 0.04 | 0.02 | 0.67 | 0.06 | 0.06 |  | 0.02 | 0.02 | 0.02 |  |  |  | 0.07 |  | 0.67
S04AA017-00001 |  | Miscellaneous Steel Erection Work | Shelter/Building | Checkered/Flooring Plate | [6 empty] | - Material: ASTM A786M Pattern 4 or 5 and ASTM A36M Material - THK=6mm, Hot-Dip Galvanized | J-05 | M2 | 229.2 |  |  |  |  | 16.2 | 26.26 | [17 empty] | 16.2 | 34.39 | 26.26 | 28.36 | [8 empty] | 38.77 | 3.86 |  |  | 23.46 |  | 7.72 | 7.72
S04AA018-00001 |  | Miscellaneous Steel Erection Work | Shelter/Building | Grating | [6 empty] | - Material: ASTM A1011/A1011M - THK=32mm 5x32mm Bearing Bars, 30mm Pitch and Cross Bars 100mm C/C | J-04 | M2 | 1778.24 | 12.41 | 3.12 | 126.9 | 175.99 | 233.2 | 1.62 | [12 empty] | 26.22 | 16.27 | 16.27 | 22.38 | 18.54 | 233.2 | 1.62 | 1.62 | 1.62 | [7 empty] | 18.54 | 1.62 | 38.11 | 3.1 |  | 1.67 | 3.87 | 57.11 | 43.75 | 3.1 | 3.1 | [5 empty] | 80.89 | 3.87 | 3.87 | 3.1 |  |  |  | 3.1 | 3.1 | 21.14 |  | 1.57 | 592.65
S04AA020-00001 | A | Miscellaneous Steel Erection Work | Shelter/Building | Steel Handrails | [6 empty] | [Handrail] - Material: ASTM A53/A53M Type E or S, Grade B. ASTM A106/A106M Grade B - Hot-Dip Galvanized & Painted - H=870mm | J-06 | M | 271.12 |  |  |  | 126 | [14 empty] | 6.4 | 3.2 | 3.2 | 6.4 | 6.4 | [11 empty] | 6.4 | [15 empty] | 113.12
S04AA020-00001 | B | Miscellaneous Steel Erection Work | Shelter/Building | Steel Handrails | [6 empty] | [Guardrail w/ Handrail] - Material: ASTM A53/A53M Type E or S, Grade B. ASTM A106/A106M Grade B - Hot-Dip Galvanized & Painted - H=1070mm |  | M | 761.82 | 33.2 | 6.88 | 156.8 | 156 | 19 | 4 | [17 empty] | 19 | 4 | 4 | 4 | [8 empty] | 4 | 15.08 | 23.94 |  | 4 | 10.59 | 15.07 | 15.07 | 23.94 | 23.94 | 6 |  |  |  |  | 25.76 | 10.59 | 10.59 | 16.02 |  |  |  | 16.02 | 16.02 | 28.01 |  | 4.06 | 86.24
S04AA020-00001 | C | Miscellaneous Steel Erection Work | Shelter/Building | Steel Handrails | [6 empty] | [Guardrail] - Material: ASTM A53/A53M Type E or S, Grade B. ASTM A106/A106M Grade B - Hot-Dip Galvanized & Painted - H=1070mm |  | M | 758.57 |  |  |  | 144 | [14 empty] | 23.8 | 16.5 | 16.5 | 20.6 | 17.4 | [11 empty] | 17.4 |  |  | 15.58 | [5 empty] | 15.58 | 15.78 | [5 empty] | 90.22 |  |  | 7.84 |  |  |  | 7.84 | 7.84 | 16.8 |  |  | 324.89
S04AA021-00001 |  | Miscellaneous Steel Erection Work | Shelter/Building | Steel Handrails - Removable | [6 empty] | [Removable Guardrail] - Material: ASTM A53/A53M Type E or S, Grade B. ASTM A106/A106M Grade B - Hot-Dip Galvanized & Painted - H=1070mm | J-06 | M | 25.7 | [37 empty] | 4.8 | [5 empty] | 4.8 | 4.8 | [5 empty] | 1.7 |  |  | 2.4 |  |  |  | 2.4 | 2.4 | 2.4
S04AA023-00001 | A | Miscellaneous Steel Erection Work | Shelter/Building | Steel Ladder | With Cage | [5 empty] | - Material: ASTM A36/A36M - H<9m - Hot-Dip Galvanized & Painted - Side-Step Type - incl. Safety Gate | J-10 | M | 509.13 |  | 16.9 | 94.14 | 63.75 | 18.86 | 8.4 | [17 empty] | 18.86 | 8.4 | 8.4 | 9.3 | [8 empty] | 8.4 | 19.7 | 19.4 |  | 9.3 | 6.12 | 19.7 | 19.7 | 19.4 | 19.4 | [5 empty] | 9.2 | 6.12 | 6.12 | 19.4 |  |  |  | 19.4 | 19.4 | 19.9 |  | 6.5 | 14.96
S04AA023-00001 | B | Miscellaneous Steel Erection Work | Shelter/Building | Steel Ladder | With Cage | [5 empty] | - Material: ASTM A36/A36M - H≥9m - Hot-Dip Galvanized & Painted - Side-Step Type - incl. Platform, Safety Gate | J-10 | M | 90.9 | 24 |  |  | 34.8 | [36 empty] | 10.7 | [10 empty] | 10.7 | 10.7
S04AA023-00002 |  | Miscellaneous Steel Erection Work | Shelter/Building | Steel Ladder | Without Cage | [5 empty] | - Material: ASTM A36/A36M - Hot-Dip Galvanized & Painted - Side-Step Type | J-10 | M | 9.15 | [50 empty] | 9.15
S04AA024-00001 |  | Miscellaneous Steel Erection Work | Shelter/Building | Galvanized Steel Deck Plate | [6 empty] | - Plate THK=1.6mm, Rib Depth=75mm - ASTM A653M or ASTM A1008M w/ Min. Yield-Strength of 228MPa - incl. Stud Bolts and Side Molding |  | M2 | 3238.85 | 640.77 |  | 2598.08

## (AR) Building List
Unit | Project Facility Code | Building Tag | Database Code | Building Name | BD w/o BM | Building/Shelter |  |  | Green/ Brown | Size | [11 empty] | Blast Design |  |  | Fire Proofing | OHC/Hoist | Remark
[6 empty] | Type | Superstructure | Project WBS |  | Story |  | Floor |  | W (m) | L (m) | H (m) | Area (m2) | Area Deduction (m2) | Including Total Area (m2) | Total Area (m2) | Volume (m3) | Resistance/ Resilience | Pso (psi) | Duration (ms)
[10 empty] | Total | (Count) | Floor | Info.
861 | 902.10.01 | 861-B-6105 | A201 | Central Control Building |  | BD | RS | Building(Steel) | Green | 1 |  |  |  | 86.15 | 56.2 | 9.5 |  |  |  | 4029.59 | 38281.105 | Resistance | 0.81 | 471.30 |  |  | [Functional Tag Number : CCR01]
[11 empty] | O | Ground |  | 86.15 | 56.2 | 9.5 | 4841.63 |  | O
[12 empty] | Ground | ACCU Area | 21.33 | 13.17 | 0 | 280.92
861 | 905.10.17 | 861-B-6107 | A808 | Laboratory & Inspection Building |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 49 | 41 | 5.75 |  |  |  | 2146.94 | 12002.6176 | N/A |  |  |  |  | [Functional Tag Number : LAB01]
[11 empty] | O | Ground |  | 49 | 41 | 5.75 | 2009 |  | O
[12 empty] | Ground | Cylinder Shelter | 3 | 6.2 | 3.27 | 18.6 |  | O
[12 empty] | Ground | GBS Area | 4.26 | 28 | 3.27 | 119.34 |  | O
[12 empty] | Ground | ACCU Area | 9.1 | 5.3 | 0 | 48.23
[12 empty] | Ground | ACCU Area | 15.2 | 9.22 | 0 | 140.14
861 | 905.10.18 | 861-B-6120 | A815 | Central Maintenance Building |  | BD | ST | Building(Steel) | Green | 1 |  |  |  | 89.9 | 46.85 | 9.99 |  |  |  | 4211.82 | 42076.0318 | N/A |  |  |  | OHC 7건 | [Functional Tag Number : MF10] - Valve Shop (2T) - RV Testting Room (2T) - Machine Shop (15T) - Process Control Maintenance Room (15T) - Metal Shop(15T) - HVAC D Gen & Crane unit Shop (15T) - Electrical and CP Shop (15T)
[11 empty] | O | Ground |  | 89.9 | 46.85 | 9.99 | 4211.82 |  | O | [6 empty] | OHC, 2Ton, 6.65m / OHC, 2Ton, 6.65m / OHC, 15Ton, 6.65m / OHC, 15Ton, 6.65m / OHC, 15Ton, 6.65m / OHC, 15Ton, 6.65m / OHC, 15Ton, 6.65m
[12 empty] | Ground | ACCU Area | 12.85 | 6.99 | 0 | 89.82
[12 empty] | Ground | ACCU Area | 4.26 | 7.93 | 0 | 33.78
861 | 901.10.01 | 861-B-6130A | A308 | 230KV GIS Main Receiving Substation |  | BD | RC | Building(RC) | Green | 2 |  |  |  | 158.61 | 29.3 | 12.45 |  |  |  | 5519.77 | 54153.476 | N/A |  |  |  | OHC 2건 | [Functional Tag Number : GIS01] Overhead Crane for 230kV GIS (5T)
[11 empty] | O | Basement | Cable Tunnel | 158.61 | 5.5 | 3.65 | 872.36 |  | O
[11 empty] | O | Ground | GIS Room | 158.61 | 16.8 | 13 | 2664.65 |  | O | [6 empty] | OHC, 5Ton, 8m / OHC, 5Ton, 8m
[12 empty] | Ground | Mech Room-1 | 28.69 | 12.5 | 13 | 358.63 |  | O
[12 empty] | Ground | Grid 5-20 | 98.79 | 12.5 | 5.35 | 1234.88 |  | O
[12 empty] | Ground | Mech Room-2 | 31.14 | 12.5 | 13 | 389.25 |  | O
[12 empty] | Ground | ACW Area | 26.78 | 5.89 | 0 | 157.73
[12 empty] | Ground | ACW Area | 5.55 | 3.25 | 0 | 18.04
[12 empty] | Ground | GIB Fence Area | 8.95 | 146.39 | 0 | 1310.19
861 | 901.10.02 | 861-B-6130B | A308 | Main Substation 01 |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 70 | 15 | 7 |  |  |  | 3282.88 | 7350 | N/A |  |  |  |  | [Functional Tag Number : MS01]
[11 empty] | O | Ground |  | 70 | 15 | 7 | 1050 |  | O
[12 empty] | Ground | TR Area | 98.8 | 22.6 | 0 | 2232.88 |  | O
[12 empty] | Ground | ACCU Area | 7.1 | 7.8 | 0 | 55.38
861 | 901.10.04 | 861-B-6131A | A306 | EDG Building - MS01 |  | BD | PC | Building(RC) | Green | 1 |  |  |  | 10 | 13 | 5.95 |  |  |  | 130 | 773.5 | N/A |  |  |  | Hoist 1건 | [Functional Tag Number : EDG18] Geared Trolley with Chain Block (3T) for EDG
[11 empty] | O | Ground |  | 10 | 13 | 5.95 | 130 |  | O | [6 empty] | Hoist, 3Ton, 0m
[12 empty] | Ground | Dike | 4.85 | 6.45 | 0 | 31.28
861 | 905.10.36 | 861-B-6170A | A104 | Chemical Storage Shelter - Utilities |  | PS | ST | Shelter | Green | 1 |  |  |  | 10 | 10 | 5.2 |  |  |  | 100 | 520 | N/A |  |  |  |  | [Functional Tag Number : CSH02]
[11 empty] | O | Ground |  | 10 | 10 | 5.2 | 100 |  | O
861 | 905.10.19 | 861-B-6172A | A901 | Smoking Shelter - CCB |  | PS | ST | Shelter | Green | 1 |  |  |  | 4 | 4 | 2.35 |  |  |  | 16 | 37.6 | N/A |  |  |  |  | [Functional Tag Number : SSH01]
[11 empty] | O | Ground |  | 4 | 4 | 2.35 | 16 |  | O
861 | 905.10.22 | 861-B-6174E | A817 | Parking Sunshade - CCB (1) |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 67 | 4.15 |  |  |  | 402 | 1668.3 | N/A |  |  |  |  | [Functional Tag Number : PKS01]
[11 empty] | O | Ground | 20ea | 6 | 67 | 4.15 | 402 |  | O
861 | 905.10.26 | 861-B-6174F | A817 | Parking Sunshade - Laboratory |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 30 | 4.15 |  |  |  | 180 | 747 | N/A |  |  |  |  | [Functional Tag Number : PKS06]
[11 empty] | O | Ground | 10ea | 6 | 30 | 4.15 | 180 |  | O
861 | 905.10.27 | 861-B-6174G | A817 | Parking Sunshade - OME05 |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 43 | 4.15 |  |  |  | 258 | 1070.7 | N/A |  |  |  |  | [Functional Tag Number : PKS12]
[11 empty] | O | Ground | 10ea | 6 | 43 | 4.15 | 258 |  | O
861 | 905.10.28 | 861-B-6174H | A817 | Parking Sunshade - Maint BD (1) |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 30 | 4.15 |  |  |  | 180 | 747 | N/A |  |  |  |  | [Functional Tag Number : PKS07]
[11 empty] | O | Ground | 10ea | 6 | 30 | 4.15 | 180 |  | O
861 | 905.10.29 | 861-B-6174I | A817 | Parking Sunshade - Maint BD (2) |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 30 | 4.15 |  |  |  | 180 | 747 | N/A |  |  |  |  | [Functional Tag Number : PKS08]
[11 empty] | O | Ground | 10ea | 6 | 30 | 4.15 | 180 |  | O
861 | 905.10.23 | 861-B-6174V | A817 | Parking Sunshade - CCB (2) |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 60 | 4.15 |  |  |  | 360 | 1494 | N/A |  |  |  |  | [Functional Tag Number : PKS02]
[11 empty] | O | Ground | 18ea | 6 | 60 | 4.15 | 360 |  | O
861 | 905.10.24 | 861-B-6174W | A817 | Parking Sunshade - CCB (3) |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 10 | 4.15 |  |  |  | 60 | 249 | N/A |  |  |  |  | [Functional Tag Number : PKS03]
[11 empty] | O | Ground | 3ea | 6 | 10 | 4.15 | 60 |  | O
861 | 905.10.25 | 861-B-6174X | A817 | Parking Sunshade - CCB (4) |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 10 | 4.15 |  |  |  | 60 | 249 | N/A |  |  |  |  | [Functional Tag Number : PKS04]
[11 empty] | O | Ground | 3ea | 6 | 10 | 4.15 | 60 |  | O
861 | 905.10.30 | 861-B-6174Y | A817 | Parking Sunshade - GIS01 |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 20 | 4.15 |  |  |  | 120 | 498 | N/A |  |  |  |  | [Functional Tag Number : PKS05]
[11 empty] | O | Ground | 6ea | 6 | 20 | 4.15 | 120 |  | O
861 | 905.10.31 | 861-B-6174Z | A102 | Parking Sunshade - MS01 |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 25.8 | 4.15 |  |  |  | 154.8 | 642.42 | N/A |  |  |  |  | [Functional Tag Number : PKS09]
[11 empty] | O | Ground | 6ea | 6 | 25.8 | 4.15 | 154.8 |  | O
862 | 862.90.01 | 862-B-6230 | A309 | Substation 07 - Utilities |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 65.03 | 15 | 7 |  |  |  | 2061.38 | 6828.15 | N/A |  |  |  |  | [Functional Tag Number : SS07]
[11 empty] | O | Ground |  | 65.03 | 15 | 7 | 975.38 |  | O
[12 empty] | Ground | TR Area | 72.4 | 15 | 0 | 1086 |  | O
[12 empty] | Ground | ACCU Area | 8.45 | 7.3 | 0 | 61.69
862 | 862.90.03 | 862-B-6250 | A203 | PIB 07 - Utilities |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 42 | 21.6 | 7.25 |  |  |  | 907.2 | 6577.2 | N/A |  |  |  |  | [Functional Tag Number : PIB07]
[11 empty] | O | Ground |  | 42 | 21.6 | 7.25 | 907.2 |  | O
[12 empty] | Ground | ACCU Area | 8.8 | 3.02 | 0 | 26.53
[12 empty] | Ground | ACCU Area | 4.65 | 2.42 | 0 | 11.25
862 | 905.10.34 | 862-B-6274A | A817 | Parking Sunshade - Utilities Area |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 18 | 4.15 |  |  |  | 108 | 448.2 | N/A |  |  |  |  | [Functional Tag Number : PKS19]
[11 empty] | O | Ground | 6ea | 6 | 18 | 4.15 | 108 |  | O
863 | 905.10.08 | 863-B-6300B | A102 | OME Building 03 - Import |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 51 | 23 | 8.4 |  |  |  | 1173 | 9853.2 | Resistance | 1.41 | 507.50 |  | OHC 1건 | [Functional Tag Number : OME03] Overhead Gantry Crane for Main Work shop (2T)
[11 empty] | O | Ground |  | 51 | 23 | 8.4 | 1173 |  | O | [6 empty] | OHC, 2Ton, 0m
[12 empty] | Ground | ACCU Area | 3.85 | 14.25 | 0 | 54.86
863 | 863.90.01 | 863-B-6330A | A309 | Substation 06 - Export Area |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 75.03 | 15 | 7.4 |  |  |  | 2117.76 | 8328.33 | N/A |  |  |  |  | [Functional Tag Number : SS06]
[11 empty] | O | Ground |  | 75.03 | 15 | 7.4 | 1125.38 |  | O
[12 empty] | Ground | TR Area | 67.08 | 14.79 | 0 | 992.38 |  | O
[12 empty] | Ground | ACCU Area | 6.56 | 11 | 0 | 72.16
863 | 863.90.02 | 863-B-6330B | A309 | Substation 09 - Import Area |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 75.03 | 15 | 7.4 |  |  |  | 2099.16 | 8328.33 | N/A |  |  |  |  | [Functional Tag Number : SS09]
[11 empty] | O | Ground |  | 75.03 | 15 | 7.4 | 1125.38 |  | O
[12 empty] | Ground | TR Area | 71.2 | 13.95 | 0 | 993.24 |  | O
[12 empty] | Ground | ACCU Area | 6.4 | 7 | 0 | 44.8
[12 empty] | Ground | ACCU Area | 4.35 | 2.3 | 0 | 10.01
863 | 863.90.05 | 863-B-6350A | A203 | PIB 06 - Export Area |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 35.2 | 21.6 | 7.25 |  |  |  | 760.32 | 5512.32 | N/A |  |  |  |  | [Functional Tag Number : PIB06]
[11 empty] | O | Ground |  | 35.2 | 21.6 | 7.25 | 760.32 |  | O
[12 empty] | Ground | ACCU Area | 7.81 | 5.53 | 0 | 43.21
[12 empty] | Ground | ACCU Area | 2.56 | 4.47 | 0 | 11.44
863 | 863.90.06 | 863-B-6350B | A203 | PIB 09 - Import Area |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 39.2 | 21 | 7.25 |  |  |  | 823.2 | 5968.2 | N/A |  |  |  |  | [Functional Tag Number : PIB09]
[11 empty] | O | Ground |  | 39.2 | 21 | 7.25 | 823.2 |  | O
[12 empty] | Ground | ACCU Area | 9.93 | 3.05 | 0 | 30.27
[12 empty] | Ground | ACCU Area | 5.1 | 2.12 | 0 | 10.81
863 | 905.10.10 | 863-B-6370B | A104 | Chemical Storage Shelter - Import |  | PS | ST | Shelter | Green | 1 |  |  |  | 11 | 10 | 5.2 |  |  |  | 110 | 572 | N/A |  |  |  |  | [Functional Tag Number : CSH07]
[11 empty] | O | Ground |  | 11 | 10 | 5.2 | 110 |  | O
863 | 905.10.12 | 863-B-6374A | A817 | Parking Sunshade - OME04 |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 24 | 4.15 |  |  |  | 144 | 597.6 | N/A |  |  |  |  | [Functional Tag Number : PKS11]
[11 empty] | O | Ground | 7ea | 6 | 24 | 4.15 | 144 |  | O
863 | 905.10.11 | 863-B-6374B | A817 | Parking Sunshade - OME03 |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 33 | 4.15 |  |  |  | 198 | 821.7 | N/A |  |  |  |  | [Functional Tag Number : PKS10]
[11 empty] | O | Ground | 11ea | 6 | 33 | 4.15 | 198 |  | O
863 | 905.10.13 | 863-B-6374C | A817 | Parking Sunshade - PIB06 |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 15 | 4.15 |  |  |  | 90 | 373.5 | N/A |  |  |  |  | [Functional Tag Number : PKS16]
[11 empty] | O | Ground | 5ea | 6 | 15 | 4.15 | 90 |  | O
863 | 905.10.14 | 863-B-6374D | A817 | Parking Sunshade - PIB09 |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 6 | 4.15 |  |  |  | 36 | 149.4 | N/A |  |  |  |  | [Functional Tag Number : PKS17]
[11 empty] | O | Ground | 2ea | 6 | 6 | 4.15 | 36 |  | O
869 | 869.90.01 | 869-B-6950A | A203 | PIB 03 - SRU/TGTU Train 1 |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 26 | 22.6 | 7.25 |  |  |  | 587.6 | 4260.1 | N/A |  |  |  |  | [Functional Tag Number : PIB03]
[11 empty] | O | Ground |  | 26 | 22.6 | 7.25 | 587.6 |  | O
[12 empty] | Ground | ACCU Area | 7.4 | 3.05 | 0 | 22.57
[12 empty] | Ground | ACCU Area | 2.2 | 6.6 | 0 | 14.52
869 | 905.10.01 | 869-B-6974A | A817 | Parking Sunshade - PIB03 |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 6 | 4.15 |  |  |  | 36 | 149.4 | N/A |  |  |  |  | [Functional Tag Number : PKS13]
[11 empty] | O | Ground | 2ea | 6 | 6 | 4.15 | 36 |  | O
869 | 905.10.02 | 869-B-6974B | A817 | Parking Sunshade - PIB04 |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 6 | 4.15 |  |  |  | 36 | 149.4 | N/A |  |  |  |  | [Functional Tag Number : PKS14]
[11 empty] | O | Ground | 2ea | 6 | 6 | 4.15 | 36 |  | O
869 | 905.10.03 | 869-B-6974C | A817 | Parking Sunshade - PIB05 |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 6 | 4.15 |  |  |  | 36 | 149.4 | N/A |  |  |  |  | [Functional Tag Number : PKS15]
[11 empty] | O | Ground | 2ea | 6 | 6 | 4.15 | 36 |  | O
870 | 870.90.01 | 870-B-7005 | A310 | Sulfur Loading Control Building |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 53 | 23.4 | 7.5 |  |  |  | 1400.2 | 9301.5 | N/A |  |  |  |  | [Functional Tag Number : CCR02]
[11 empty] | O | Ground |  | 53 | 23.4 | 7.5 | 1240.2 |  | O
[12 empty] | Ground | TR Area | 10 | 16 | 0 | 160 |  | O
[12 empty] | Ground | ACCU Area | 15.28 | 4.26 | 0 | 65.09
870 | 905.10.05 | 870-B-7074A | A817 | Parking Sunshade - Sulfur Loading |  | OS | ST | Shelter | Green | 1 |  |  |  | 6 | 42 | 4.15 |  |  |  | 252 | 1045.8 | N/A |  |  |  |  | [Functional Tag Number : PKS18]
[11 empty] | O | Ground | 14ea | 6 | 42 | 4.15 | 252 |  | O
870 | 905.10.04 | 870-B-7088 | A802 | SL Drivers Welfare Building |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 5 | 11.5 | 4.05 |  |  |  | 57.5 | 232.875 | N/A |  |  |  |  | [Functional Tag Number : SLW01]
[11 empty] | O | Ground |  | 5 | 11.5 | 4.05 | 57.5 |  | O
[12 empty] | Ground | ACCU Area | 3.24 | 6.7 | 0 | 21.71
870 | 870.90.03 | 870-B-7073 | A507 | Sulfur Loading Arm Shelter |  | OS | ST | Shelter | Green | 1 |  |  |  | 22 | 36 | 17 |  |  |  | 792 | 13464 | N/A |  |  |  | Hoist 3건 | [Functional Tag Number : SLA01]
[11 empty] | O | Ground |  | 22 | 36 | 17 | 792 |  | O | [6 empty] | Hoist, 0.5Ton, 0m / Hoist, 0.5Ton, 0m / Hoist, 0.5Ton, 0m
863 | 863.90.07 | 863-B-6373 | A504 | Propane Storage Shelter |  | OS | ST | Shelter | Green | 1 |  |  |  | 12 | 42.5 | 13 |  |  |  | 510 | 6630 | N/A |  |  | O | Hoist 3건 | [Functional Tag Number : PSS01]
[11 empty] | O | Ground |  | 12 | 42.5 | 13 | 510 |  | O | [6 empty] | Hoist, 0.4Ton, 0m / Hoist, 0.4Ton, 0m / Hoist, 0.4Ton, 0m
861 | 861.90.01 | 861-B-6173A | A901 | Flare RIO Shelter |  | PS | ST | Shelter | Green | 1 |  |  |  | 10 | 4.8 | 3.5 |  |  |  | 48 | 168 | N/A |  |  |  |  | [Functional Tag Number : RIO01]
[11 empty] | O | Ground |  | 10 | 4.8 | 3.5 | 48 |  | O
861 | 861.90.02 | 861-B-6173B | A901 | Burn Pit RIO Shelter |  | PS | ST | Shelter | Green | 1 |  |  |  | 5.9 | 4.8 | 3.5 |  |  |  | 28.32 | 99.12 | N/A |  |  |  |  | [Functional Tag Number : RIO02]
[11 empty] | O | Ground |  | 5.9 | 4.8 | 3.5 | 28.32 |  | O
861 | 861.90.03 | 861-B-6173C | A901 | Evaporation Pond RIO Shelter |  | PS | ST | Shelter | Green | 1 |  |  |  | 5.9 | 4.8 | 3.5 |  |  |  | 28.32 | 99.12 | N/A |  |  |  |  | [Functional Tag Number : RIO03]
[11 empty] | O | Ground |  | 5.9 | 4.8 | 3.5 | 28.32 |  | O
861 | 861.90.04 | 861-B-6173D | A901 | Custody Metering RIO Shelter |  | PS | ST | Shelter | Green | 1 |  |  |  | 8.4 | 4.8 | 3.5 |  |  |  | 40.32 | 141.12 | N/A |  |  |  |  | [Functional Tag Number : RIO04]
[11 empty] | O | Ground |  | 8.4 | 4.8 | 3.5 | 40.32 |  | O
861 | 861.90.05 | 860-B-6073A | A901 | Aquifer Well A RIO Shelter |  | PS | ST | Shelter | Green | 1 |  |  |  | 6.8 | 4.8 | 3.5 |  |  |  | 32.64 | 114.24 | N/A |  |  |  |  | [Functional Tag Number : RIO05]
[11 empty] | O | Ground |  | 6.8 | 4.8 | 3.5 | 32.64 |  | O
861 | 901.10.02 | 861-B-6130C | A308 | Main Substation 02 |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 70 | 15 | 7 |  |  |  | 3282.88 | 7350 | N/A |  |  |  |  | [Functional Tag Number : MS01]
[11 empty] | O | Ground |  | 70 | 15 | 7 | 1050 |  | O
[12 empty] | Ground | TR Area | 98.8 | 22.6 | 0 | 2232.88 |  | O
[12 empty] | Ground | ACCU Area | 7.1 | 7.8 | 0 | 55.38
869 | 869.90.01 | 869-B-6950B | A203 | PIB 04 - SRU/TGTU Train 2 |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 26 | 22.6 | 7.25 |  |  |  | 587.6 | 4260.1 | N/A |  |  |  |  | [Functional Tag Number : PIB03]
[11 empty] | O | Ground |  | 26 | 22.6 | 7.25 | 587.6 |  | O
[12 empty] | Ground | ACCU Area | 7.4 | 3.05 | 0 | 22.57
[12 empty] | Ground | ACCU Area | 2.2 | 6.6 | 0 | 14.52
863 | 905.10.08 | 863-B-6300A | A102 | OME Building 04 - Export |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 51 | 23 | 8.4 |  |  |  | 1173 | 9853.2 | Resistance | 1.41 | 507.50 |  | OHC 1건 | [Functional Tag Number : OME03] Overhead Gantry Crane for Main Work shop (2T)
[11 empty] | O | Ground |  | 51 | 23 | 8.4 | 1173 |  | O | [6 empty] | OHC, 2Ton, 0m
[12 empty] | Ground | ACCU Area | 3.85 | 14.25 | 0 | 54.86
869 | 869.90.01 | 869-B-6950C | A203 | PIB 05 - SRU/TGTU Train 3 |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 26 | 22.6 | 7.25 |  |  |  | 587.6 | 4260.1 | N/A |  |  |  |  | [Functional Tag Number : PIB03]
[11 empty] | O | Ground |  | 26 | 22.6 | 7.25 | 587.6 |  | O
[12 empty] | Ground | ACCU Area | 7.4 | 3.05 | 0 | 22.57
[12 empty] | Ground | ACCU Area | 2.2 | 6.6 | 0 | 14.52
863 | 905.10.08 | 862-B-6200 | A102 | OME Building 05 - Utilities |  | BD | RC | Building(RC) | Green | 1 |  |  |  | 51 | 23 | 8.4 |  |  |  | 1173 | 9853.2 | Resistance | 1.41 | 507.50 |  | OHC 1건 | [Functional Tag Number : OME03] Overhead Gantry Crane for Main Work shop (2T)
[11 empty] | O | Ground |  | 51 | 23 | 8.4 | 1173 |  | O | [6 empty] | OHC, 2Ton, 0m
[12 empty] | Ground | ACCU Area | 3.85 | 14.25 | 0 | 54.86
861 | 901.10.04 | 863-B-6331A | A306 | EDG Building - Substation 6 |  | BD | PC | Building(RC) | Green | 1 |  |  |  | 10 | 13 | 5.95 |  |  |  | 130 | 773.5 | N/A |  |  |  | Hoist 1건 | [Functional Tag Number : EDG18] Geared Trolley with Chain Block (3T) for EDG
[11 empty] | O | Ground |  | 10 | 13 | 5.95 | 130 |  | O | [6 empty] | Hoist, 3Ton, 0m
[12 empty] | Ground | Dike | 4.85 | 6.45 | 0 | 31.28
861 | 901.10.04 | 870-B-7031A | A306 | EDG Building - Substation 8 |  | BD | PC | Building(RC) | Green | 1 |  |  |  | 10 | 13 | 5.95 |  |  |  | 130 | 773.5 | N/A |  |  |  | Hoist 1건 | [Functional Tag Number : EDG18] Geared Trolley with Chain Block (3T) for EDG
[11 empty] | O | Ground |  | 10 | 13 | 5.95 | 130 |  | O | [6 empty] | Hoist, 3Ton, 0m
[12 empty] | Ground | Dike | 4.85 | 6.45 | 0 | 31.28
861 | 901.10.04 | 861-B-6131B | A306 | EDG Building - Facility Security |  | BD | PC | Building(RC) | Green | 1 |  |  |  | 12 | 15 | 5.95 |  |  |  | 180 | 1071 | N/A |  |  |  | Hoist 1건 | [Functional Tag Number : EDG18] Geared Trolley with Chain Block (3T) for EDG
[11 empty] | O | Ground |  | 12 | 15 | 5.95 | 180 |  | O | [6 empty] | Hoist, 3Ton, 0m
[12 empty] | Ground | Dike | 4.85 | 6.45 | 0 | 31.28
861 | 905.10.36 | 863-B-6370A | A104 | Chemical Storage Shelter - Exports |  | PS | ST | Shelter | Green | 1 |  |  |  | 10 | 10 | 5.2 |  |  |  | 100 | 520 | N/A |  |  |  |  | [Functional Tag Number : CSH02]
[11 empty] | O | Ground |  | 10 | 10 | 5.2 | 100 |  | O
861 | 905.10.19 | 861-B-6172B | A901 | Smoking Shelter - LAB01 |  | PS | ST | Shelter | Green | 1 |  |  |  | 4 | 4 | 2.35 |  |  |  | 16 | 37.6 | N/A |  |  |  |  | [Functional Tag Number : SSH01]
[11 empty] | O | Ground |  | 4 | 4 | 2.35 | 16 |  | O
861 | 905.10.19 | 861-B-6172C | A901 | Smoking Shelter - Maintenance BD |  | PS | ST | Shelter | Green | 1 |  |  |  | 4 | 4 | 2.35 |  |  |  | 16 | 37.6 | N/A |  |  |  |  | [Functional Tag Number : SSH01]
[11 empty] | O | Ground |  | 4 | 4 | 2.35 | 16 |  | O
861 | 905.10.19 | 870-B-7072 | A901 | Smoking Shelter - Sulfur Loading |  | PS | ST | Shelter | Green | 1 |  |  |  | 4 | 4 | 2.35 |  |  |  | 16 | 37.6 | N/A |  |  |  |  | [Functional Tag Number : SSH01]
[11 empty] | O | Ground |  | 4 | 4 | 2.35 | 16 |  | O
861 | 905.10.19 | 863-B-6372B | A901 | Smoking Shelter - OME 03 |  | PS | ST | Shelter | Green | 1 |  |  |  | 4 | 4 | 2.35 |  |  |  | 16 | 37.6 | N/A |  |  |  |  | [Functional Tag Number : SSH01]
[11 empty] | O | Ground |  | 4 | 4 | 2.35 | 16 |  | O
861 | 905.10.19 | 863-B-6372A | A901 | Smoking Shelter - OME 04 |  | PS | ST | Shelter | Green | 1 |  |  |  | 4 | 4 | 2.35 |  |  |  | 16 | 37.6 | N/A |  |  |  |  | [Functional Tag Number : SSH01]
[11 empty] | O | Ground |  | 4 | 4 | 2.35 | 16 |  | O
861 | 905.10.19 | 861-B-6172D | A901 | Smoking Shelter - OME 05 |  | PS | ST | Shelter | Green | 1 |  |  |  | 4 | 4 | 2.35 |  |  |  | 16 | 37.6 | N/A |  |  |  |  | [Functional Tag Number : SSH01]
[11 empty] | O | Ground |  | 4 | 4 | 2.35 | 16 |  | O
861 | 861.90.05 | 860-B-6073B | A901 | Aquifer Well B RIO Shelter |  | PS | ST | Shelter | Green | 1 |  |  |  | 6.8 | 4.8 | 3.5 |  |  |  | 32.64 | 114.24 | N/A |  |  |  |  | [Functional Tag Number : RIO05]
[11 empty] | O | Ground |  | 6.8 | 4.8 | 3.5 | 32.64 |  | O
861 | 901.10.04 | 863-B-6331B | A306 | EDG Building - Substation 9 |  | BD | PC | Building(RC) | Green | 1 |  |  |  | 10 | 13 | 5.95 |  |  |  | 130 | 773.5 | N/A |  |  |  | Hoist 1건 | [Functional Tag Number : EDG18] Geared Trolley with Chain Block (3T) for EDG
[11 empty] | O | Ground |  | 10 | 13 | 5.95 | 130 |  | O | [6 empty] | Hoist, 3Ton, 0m
[12 empty] | Ground | Dike | 4.85 | 6.45 | 0 | 31.28
862 | 862.90.02 | 862-B-6231 | A306 | EDG Building - Substation-07 |  | BD | PC | Building(RC) | Green | 1 |  |  |  | 12 | 15 | 6.85 |  |  |  | 180 | 1233 | N/A |  |  |  | Hoist 1건 | [Functional Tag Number : EDG07] Geared Trolley with Chain Block (5T) for EDG
[11 empty] | O | Ground |  | 12 | 15 | 6.85 | 180 |  | O | [6 empty] | Hoist, 5Ton, 0m
[12 empty] | Ground | Dike | 4.85 | 6.45 | 0 | 31.28
| History Memo |  |  |  |  | Building Q'ty Summary |  |  |  | Building Area Summary
| 2021.12.02 Sulfur Loading Arm Shelter - Building Tag 수정 (기계 Tag -> 신규 BLDG Tag 부여) 2022.01.07 BLDG No. 53~60 - BLDG Tag Number는 발주처로부터 받아야 하므로 임의 부여했던 Tag No. 삭제했음 2022.01.11 FDN for Bottled Air System 총 6개 삭제 -> 각 건물에 편입 완료, SIZE HOLD (CCB, LAB, SLBD, OME3, OME4, OME5) 2022.01.19 BLDG Name 수정 OME 05 - PLANT No. (UNIT) 수정 862 ->861 2022.01.25 OHC 내역 수정 - CCB 내역 -> CMB로 이관 (오기) 2022.02.15 Cylinder Shelter - Laboratory -> LABORATORY 건물로 편입 Substation 09 - Import Area Size 수정 (70.03 -> 75.03) 입찰당시 70.03m로 돼있었으나 특별한 History/사유 찾지못했음. FEED 기준으로 수정 Parking Sunshade - Laboratory (16ea) / Maint BD (1)(18ea) / Maint BD (2)(18ea) 대수 Plot Plan 기준으로 변경 (모두 10ea) Sulfur Loading Welfare Building -> SL Drivers Welfare Building 건물명 수정 (FFED 기준+글자수 제한) GIS Main Receiving Substation Size 수정 - Room별 Area 분리 (Area별 Height 상이함) 2022.03.14 Functional Tag Number 사용 -> Remark란에 정리 EDG BLDG (6ea) Building Size 수정 L : 7.5m / IFR 도면 기준으로 수정 2022.03.15 아래 건물들의 Blast Resistant 적용여부 수정 Chemical storage shelter (EXPORT, IMPORT, UTILITIES) EDG Building - Substation-07 EDG Building - Facility Security Sulfur Loading Control Building 2022.04.05 Propane Storage Shelter Size 변경 (41.0x9.2x10.0 -> 13.0x42.5x12.0) (IOM-PI-0045) 2022.04.18 (BLDG List 전체 Update) BLDG Size 수정 - W : 도면상 좌우 길이로 통일 / L : 도면상 위아래 길이로 통일 H : E-Space Manual에 명시된 Ground Floor 바닥마감 level - Roof TOC or TOS(LP) 2022.04.27 (SYH) CCB/SLCB/SL Welfare/SS07 Size 에 대해 Latest DWGs 기준으로 Update 2022.04.27 (KSJ) BAS FDN Size 모두 삭제 - 추후 inform 접수시 반영 -> SF TQ통해 BAS 제외로 모두 삭제 TR Yard Height 삭제 2022.04.28 (KSY) LAB - Add Area (by HV) 삭제(건물 면적에 포함), GBS Area 면적 기입 (draft) 2022.05.16 (KSJ) EDG 08 - 잘못 입력돼있던 Blast값 삭제 2022.07.14 (KSJ) PSS01, SLA01 - BLDG TAG NO. 임의 부여 2022.08.04 (KSJ) PSS01, SLA01 - BLDG Tag No. 수정 2022.08.16 (KSJ) GIS, EDG(all) - Superstructure type 변경 (RC -> PC) Parking sunshade Height 수정 (all) PKS11, PKS16 - Size 수정 (L) SLA01 - Size 수정 (W/H) PSS01 - Size 수정 (H) 2022.08.17 (KSJ) LAB01 - ACCU Area -> ACW Area로 수정 GIS01 - Add. Area(by HV) 입찰당시 작성된 내용은 삭제했음 PACC Area -> ACW Area로 수정 2022.09.19 (SYH) GIS01 - Latest DWGs(AR Basic Rev. A/B) 기준으로 Update 2022.09.30 (KSJ) PKS10 - OME03 - Latest DWG 기준으로 Size Update 2023.02.02 (KSJ) BLDG Name 수정 (LAB01, GIS01) 2023.02.06 (KSJ) Building Area에서 ACCU Area 삭제 (walkway 확장+PED concept으로 진행중이라 별도 Area 산정은 불필요하다 판단) BRA Report Rev.00A 기준 Blast Design update (All BLDG) 2023.02.09 (KSJ) ACCU Area 다시 추가 (Total Area에는 산정안되게 반영 - including Total Area 체크해제) 2023.03.27 (GJM) CMB - Hook height 기입 2023.03.29 (GJM) EDG Building 6동 건물 size 수정 2023.06.29 (GJM) Smoking shelter 3동(OME-3,4,5) 및 RIO Shelter 6동 추가 2023.8.3 (SYH) GIS Substation 에서 GIB Fence Area 추가 (GIB Shelter 가 해당 구역에 있음) Update for Chem Storage Shelter Aquifer Well RIO Shelter 에 대한 Unit 860 -> 861 로 수정 (물리적 Unit 구분은 861, Process Unit 구분은 860 이라고 함) 2023.8.3(KSY) EDG, PKS 면적 업데이트 2023.8.3(CHJ) SLA01 Monorail 추가, PSS Fireproofing 추가 |  |  |  |  | BD (Building) : |  |  | 26 | BD (Building) : |  |  |  | 38862.4
[6 empty] | OS (Open Shelter) : |  |  | 21 | OS (Open Shelter) : |  |  |  | 4192.8
[6 empty] | PS (Partially Open Shilter) : |  |  | 16 | PS (Partially Open Shilter) : |  |  |  | 632.24
[6 empty] | FD (Foundation) : |  |  | 0 | FD (Foundation) : |  |  |  | 0
[6 empty] | Total : |  |  | 63 | Total : |  |  |  | 43687.44

## (AR) Reference Spec.
No | Description | Remark
A-01 | Excavation a) Soil Excavation up to 2.0m depth from ground by machinery equipment as per SAES-A-114 b) Soil Excavation below 2.0m depth by machinery equipment as per SAES-A-114 c) Including soil compaction of the bottom of the excavated site as per SAES-A-114 | SAES-A-114 7.1
A-02 | Backfill and Fill: a) Fill and backfill materials shall conform to the criteria in sections 6.1.1, 6.1.2, 6.1.3, and 6.1.4 as per SAES-A-114 All sources of supply shall be approved by Saudi Aramco. Stockpiles shall be placed, graded, and shaped for proper drainage. Storage or stockpiling of material shall not be permitted on a completed subgrade. Stockpiles of cohesive soil shall be protected from freezing. Soils shall be classified per ASTM D2487. | SAES-A-114 Sec 6.1, 6.3
A-03 | Selected Fill: a) Select Fill or ‘Structural Fill’ shall be composed only of inorganic material and shall have 100% passing the 5 cm (2 in) sieve and from 0 to 20% passing the No. 200 sieve. b) The portion of Select Fill material passing the No. 40 sieve shall have a maximum liquid limit of 35 and a maximum plasticity index of 12 per ASTM D4318. Liquid limit and plastic limit tests are not required for select fill material with less than 15% passing the No. 200 sieve. c) Subgrade and fill materials shall be compacted to at least 95% of the maximum Modified Proctor density as determined by ASTM D1557 or at lest 85% of relative density as determinded by ASTM D4253 and ASTM D4254 for cohesionless granular soils that do not exhibit a well-defined moisture density relationship as per SAES-A-114 section 6.3.6. | SAES-A-114 Sec.6.1.2 / 6.3.6
A-04 | Disposal: a) Excavated Soil b) All excavated materials that are unsatisfactory for use as fill or backfill or that are surplus to that needed for backfilling shall immediately be disposed of at a location designated by the Saudi Aramco Company Representative. | SAES-A-114 Sec 7.6
A-05 | Polyethylene Sheet: a) A plasticized sheet vapor barrier, Class A, minimum of 0.25 mm (10 mils) in thickness, shall be placed beneath slabs on grade. Outdoor sidewalks are exempted from this requirement. b) A plasticized sheet vapor barrier, minimum of 0.25 mm (10 mils) in thickness shall be placed below and around the sides of concrete that is placed directly into excavation without the use of formwork, where coal tar or bitumen coating cannot be applied | SAES-Q-001 Sec 8.20.1 Sec 8.20.3
A-08 | Coating and Protection Surface Coating for concrete structure below ground: a) All concrete surfaces in direct contact with earth shall be coated with two coats of coal tar or bitumen coating that conforms to APCS-3 or APCS-10 of SAES-H-001. b) Coating shall be extended by 150mm (min.) above high point of paving (H.P.P). c) Coating requirement for concrete not in direct contact with earth shall conform with the requirement of SAES-H-003. d) APCS-10 shall not be used where soil is contaminated with hydrocarbons and compatibility test shall be conducted when concrete surface is cured with acrylic based curing compound. e) APCS-3 compatibility test shall be conducted when concrete surface is cured with bitumen based curing compound. APCS-10: - Type of Coating: Bituminous Coating for Moderate Temperature, Buried or Immersion Service (Self-priming) - Typical Use : Buried and immersed steel. Resistant to water and acidic fumes. Not generally recommended for shop applications or when handling is required after coating. - Total Dry Film Thickness for Buried: 750 micormeters - Total Dry Film Thickness for Immersed: 1150 micrometers APCS-3: - Type of Coating: Coal Tar Epoxy Coating System for immersion Service and buried concrete - Typical Use : Immersion service in tanks containing hydrocarbons, seawater, fresh water and most alkalis; intermittent contact with acids and solvents. It is also for buried concrete foundations and oily water concrete sumps. - Total Dry Film Thickness: Min. 720 micrometers | TD-391201-001_D 4.17 4.18 SAES-Q-001 Sec 8.20.4 SAES-H-001
A-09 | Surface Coating for concrete structure above ground: APCS-1B - Type of Coating : Epoxy Coating System for Atmospheric Service (with Epoxy Primer). - Typical Use : Severe atmospheric exposure including exposure to many acids and alkalis; primer can be used with APCS - 12. - Primer : 55-100 micrometers, minimum-maximum (One coat) - Topcoats : 110-150 micrometers, minimum-maximum per coat (Two coats) - Total System : Three coats 275-400 micrometers, minimum-maximum (three coats) | "SAES-H-001 SAES-H-101V"
B-01 | Concrete: a) f'c=35MPa at 28 days (Cylinder Strength) b) Cement type: - General : Cement Type Ⅴ as per ASTM C150 Type - Exposure class C1 : Cement Type I as per ASTM C150 Type +Pozzolan or slag - Mass concrete : Cement Type I as per ASTM C150 + Slag + Silica fume c) Cement Content Min. 360 kg as per 09-SAMSS-097 c) Cement Content, W/C Ratio and Admixture refer to 09-SAMSS-097 and SAES-Q-001 | "TD-391201-001_D 4.2" "TD-821201_D 10.4" SAES-Q-001
B-02 | Lean Concrete: a) A 50mm sub-slab (lean concrete) shall be placed beneath concrete foundation. b) f'c=14MPa at 28 days (Cylinder Strength) c) Cement type: Portland cement as per ASTM C150 Type I d) Cement Content Min. 250 kg as per 09-SAMSS-097 | "TD-391201-001_D 4.15" "TD-391201-001_D 4.2" 09-SAMSS-097
B-03 | Form: a) Coated plywood or steel forms. b) The design and construction of the formwork shall be in accordance with ACI 347R, Saudi Aramco Construction Safery Manual. c) Including 20mm chamfers | SAES-Q-001 Sec 8.13
B-04 | Rebar: a) Reinforcing steel bars shall be in accordance with SAES-Q-001, section 7.2.1. b) Concrete structures exposed to Class C1 shall have reinforcement coating in accordance with SAES-Q-001, section7.2.3. c) Reinforcement strength grade shall be standard high yield equal to 420 Mpa. d) Coated reinforcements shall be Fusion Bonded Epoxy in accordance with 09-SAMSS-106. | TD-391201-001_D 6.1
B-05 | Welded Wire Fabric: a) Welded wire reinforcement shall be plain wire in accordance with ASTM A1064/A1064M. b) Galvanized welded wire fabric shall conform to ASTM A1060/A1060M. c) Concrete structures exposed to Class C1 shall have coated. | SAES-Q-001 7.2.5 7.2.6
B-06 | Isolation Joint: a) Joint filler strips for isolation joints shall conform to ASTM D1751 or ASTM D1752. b) The joint width = 12mm (Generally), 25mm(Equipment Ped. ONLY) c) All joints shall be filled with a suitable sealer, as specified in 09-SAMSS-075. d) Dowel Bar (if required) | TD-821201_D 5.2 TD-821201_D 5.5.9 TD-391203 SAES-Q-001 8.14.2
B-07 | Expansion Joint: a) Joint filler strips for expansion joints shall conform to ASTM D1751 or ASTM D1752. b) The compound shall be elastomeric, single or multi-component, non-sag, paintable, and have good resistance to occasional hydrocarbon and lubricating oil spills. The compound shall have zero moisture/vapor permeability, and have adequate resistance to wind driven rain and atmospheric pollutants in concentrations found in hydrocarbon processing facilities. Oil resistant polysulphide joint sealer U.N.O. c) Entire space of expansion joint shall be filled with Joint Filler. d) All joints shall be filled with a suitable sealer, as specified in 09-SAMSS-075. | TD-821201_D 5.2 09-SAMSS-075 Sec. 4 TD-821201_D 5.5.9
B-08 | Water Stop: a). Waterstop shall be central or external (surface) type made from extruded PVC (Polyvinyl chloride) or approved TPER (Thermoplastic Elastomeric Rubber) material. b) Waterstops are available in various sizes, shapes, and materials. Environmental concrete structures commonly use waterstops of preformed rubber or polyvinyl chloride with a minimum thickness of 9.5 mm. They should normally be at least 230 mm wide for expansion joints and 150 mm wide for other types of joints to provide adequate embedment in the concrete. c) Waterstops shall be polyvinyl chloride or other suitable materials. Material proposed for use on the job site shall be certified by the manufacturer based on laboratory tests, or other tests shall be made that will assure compliance with the specification. d) Hydrocarbon resistant or equivalent in accordance with ACI 350.5 | SAES-Q-001 Sec 8.14.7 ACI 350.5
C-01 | Concrete Masonry Unit: a) Hollow and Solid load-bearing concrete masonry units shall be manufactured according to ASTM C90, and tested in accordance with ASTM C140. b) Minimum reinforcement : The minimum vertical reinforcement shall be 12 mm diameter bars at 1.2 meters spacing (#4 bars at 4 ft spacing). The minimum horizontal joint reinforcement shall be 2 longitudinal truss bars of 5 mm diameter placed at 400 mm (16-inch) centers c) The minimum compressive strength of concrete masonry units shall be 13.1 Mpa (1900 psi) d) The specified compressive strength of mortar shall not be less than 12.4 Mpa (1800 psi) e) Non-load bearing concrete masonry units shall be manufactured according to ASTM C129, and tested in accordance with ASTM C140.f) The mortar shall be type V Portland Cement as specified in ASTM C150. g) Masonry work includes below works: - Install metal lath as required with stainless steel fasteners and lapped joints tied with galvanized wire. - Install corner (angle) beads at all openings and fasten with stainless steel fasteners. - Install plaster grounds (stops) to finish the plaster as required and fasten with stainless steel fasteners. - Precasted lintel is included in masonry work. h) Applied for building exteior/interior wall and chemical shelter. i) Decorative rustication grooves in render is included for every horizontal 1.5m. | SAES-M-100 Chapter 21 AA-036602 SAES-Q-001 Sec 7.3 SABP-Q-008 Sec 3 SAES-Q-001 Sec 3.2
D-01 | Paint (General): 1. The manufacturer shall be approved by COMPANY during the construction stage. 2. All proposed coating materials shall be supplied by a single manufacturer and from one manufacturing batch. Different makers and brands shall be compatible, only used after COMPANY approval and in accordance with noted specifications for painting and coatings work. 3. The paint system and dry film thickness shall be selected considering the local climate condition, the building characteristic and the severe industrial environment and they shall be in line with the approved manufacturer's standard. 4. This work includes the fair-face treatment. | General
D-02 | Acrylic Emulsion Paint: 1) Surface Preparation Requirements : Near white blast cleaning 2) Dry Film Thickness Requirement: - Primer: Alkali Resistant Primer, Emulsion Primer (30 Micrometers DFT). - Intermediate: Fenomastic 04 Flat Emulsion (30 Micrometers DFT) (Acrylic emulsion paint, conforming to SASO SSA 470 for Exterior Emulsion) - Finish Coat: Fenomastic 20 Semi Gloss Emulsion (25 Micrometers DFT) (Acrylic emulsion paint, conforming to SASO SSA 470 for Exterior Emulsion) | General
D-03 | Textured Paint TEXTURE - Within a specific color palette the Designer /Architect can introduce standard textures in Concrete Masonry Units. Fairface treatment shall be done prior to painting work. | SAES-R-004A1
E-01 | Ceramic Tile: a) Floor Tile - Floor tile shall be impervious unglazed, non slip ceramic tile with all-purpose edges. - BASE trim pieces shall match Floor tile in size and pattern. Provide tile on factory-mounted sheets b) Wall Tile - Wall tile shall be glazed ceramic. - trim pieces shall match Wall tile and be provided in shape required to Provide a smooth, continuous surface. - Provide tile with cushion edges, except where square edges are required. c) Tiles shall be glued on mortar coating, using an appropriate adhesive in strict accordance with the manufacturer's instructions. d) Straight joints filled with fine white waterproof cement. Wall joints must be lined up with floor joints. e) Ceramic and acid-resisting ceramic wall tiles and accessories shall comply with relevant ANSI and SAMSS Standards and requirements and shall be square edged, plain and flat. f) The size of unglazed ceramic tile shall be as follows. - Wet Area : 300x300 - Office Area : 600x600 | "Standard Dwgs AA-036065"
E-02 | Acid Resistance Quarry Tile: a) Tiles shall be glued on mortar coating, using an appropriate adhesive in strict accordance with the manufacturer's instructions. b) Straight joints filled with fine white waterproof cement. Wall joints must be lined up with floor joints. | "Standard Dwgs AA-036065"
E-03 | Vinyl Tile: 1.Resilient flooring tile shall be 300 mm by 300 mm by 3 mm, and shall conform to ASTM F1066. composition 1, Class 2 vinyl tile. | "Standard Dwgs AA-036065"
E-04 | Vinyl Coved Base: 1.Vinyl coved base shall be 100 mm by 300 mm by 3 mm, and shall conform to ASTM F1066. composition 1, Class 2 vinyl tile.
F-01 | Liquid Waterproofing 1. Sika 1 waterproofing with a ratio of 1:10, shall be provided for waterproofing in toilet, kitchen, etc.. | General
G-01 | Water Proofing Membrane: a) 1.52 mm (0.060") thick EPDM (Ethylene Propylene Diene Monomer) b) All completed flat roofs shall be subjected to a leak detection test using Electric Field Vector Mapping (EFVM) or approved equal by an approved testing lab/company. Where applicable, a water flood test (20 mm minimum ponding) for a period of no less than 24 hours may be used in lieu of the above, if the roof has sufficient load-resisting capacity and at the approval of the project engineer. | "SAES-M-100 Chapter 15"
G-02 | Rigid Insulation: a) The overall heat transmission coefficient (U-factor) shall not exceed 0.193 W/(m² °K) or 0.034 btu/(h ft² °F). b) The insulation material shall be rot and rodent resistant and must not be affected by temperatures of 65°C (150°F) or by short period exposure to direct sunlight, causing thermal decomposition not related to combustion. c) All insulation materials other than foam plastic shall have a flame-spread rating not to exceed 25 and a smoke density not to exceed 450 in accordance with the International Building Code, 2006 Edition, Section 719. d) The recommanded inuslation material is Polyisocyanurate Insulation Board (mechanically fastened). | "SAES-N-004 10.1.2.1 7.2 7.6 Standard Dwgs AA-036091"
G-03 | Lightweight Concrete Screed 1. Min. 50MM for roof finish. Upon waterproof membrane and insulation. 2. Unit Weight: 1,200kg/m3 3. Aggregate conforming to ASTM C332 GroupⅠ And ASTM C28 And Portland Cement Conforming To ASTM C150 TypeⅠ. 4. One Cement To Six Aggregate To Produce A Concrete Of 8.8N/㎟ Min. Compressive Strength. 5. Crack control shall be ensured. 6. Fair face treatment included. | SAES-M-100
H-01 | Steel Door: a) Doors shall comply with PIP Specification ARS08111. Door leaves shall be 45 mm thick, full flush, fabricated from Class G90 (Z275) zinc coated sheets or better. Jamb extensions shall be furnished where required to provide secure attachment to the wall framing. b) Door hardware shall comply with PIP Specification ARS08710. c) Each door leaf shall be installed with three 114 mm x 114 mm galvanized steel, interlocking, template butt hinges. d) Door leaves and frames shall be shop-painted with one coat of primer and finished to match the walls in accordance with coating system of APCS-6 e) The threshold shall be an extruded aluminum shape to provide positive weather seal. f) All doors shall be as per ther requirements of SSD 7 & 8 g) Fire-rated Hardware - All hardware for doors in firewalls shall be fire-rated and be provided with a UL label. - Only qualified companies listed in the UL Building Materials Directory, UL-Qualified Companies for Door Hardware, shall provide fire-rated hardware. h) Thresholds - Thresholds shall be in accordance with ANSI/BHMA A156.21. - Thresholds for out-swinging doors shall be provided with an interlocking lip and with a hook on the bottom edge of the door to act as a weather bar. - Thresholds shall be either extruded or cast aluminum. i) Exit Devices - Exit Devices shall meet the requirements of ANSI/BHMA A156.3, Grade 2, unless otherwise specified. - Nonlabeled doors shall be provided with a lock-down feature. - Doors wider than 36 inches (900 mm) shall be provided with crossbars in stainless steel material with reinforcement (Grade 1 in mortise, rim, or surface-mounted designs). j) Gas tight - Where doors are gas tight required, privide with gas tight structure and sealing finished. k) Vision panel - Vision panels, where required, shall be provided with clear glass panels. - Where fire rating is required, glazing shall be Pyran / Georgian wired glass or equal approved, to the necessary fire rating. l) All toilet cubicle doors shall be fitted with one anodised aluminium hat / coathook, rubber buffer, doorstop, and loop handle sliding indicator bolt. | 12-SAMSS-014 8.3 " ARS08710 Sec 4.5.1.10" ARS08710 Sec 4.5.1.8" ARS08710 Sec 4.5.1.5 TD- 821261 8.24
H-01A | Panic Hardware 1. Substations, motor control centers, and other rooms that contain electrical connect and disconnect equipment shall have doors that open outwards. Panic hardware shall be installed on the doors. 2. Power operated egress doors shall meet requirements of ANSI/BHMA A156.10, be manually opened under power with either a push switch or panic bar, and be openable manually in a power failure with a maximum force of 220 N (50 lbs.). 3. All external doors shall be fitted with door closers and door-stops and all external emergency exit doors and the active leaves of double doors shall be fitted with door closers, panic latches and door-stops. 4. Active leaf in equipment door for use as emergency personnel exit shall be provided with panic hardware. | SAES-B-014 5.13 TD- 821261 8.7.3, 8.7.5
H-02 | Blast Resistant Door a) The performance category for the blast resistant doors shall be in accordance with Table 1. b) The response limits and other requirements shall be as given in Table 11. c) In buildings large enough to require more than one egress door in accordance with SAES-M-100 and the IBC, at least two doors shall be designated as egress doors for the purpose of limiting the damage to these doors if subjected to blast loads. d) Doors, door frames, and door hardware shall be designed for the performance criteria and applied blast loads in accordance with the BDR Data Sheet and shall comply with 12-SAMSS-010. e) Doors shall be outward opening and shall seat against the frame in response to positive phase blast wave. f) Door hardware shall be capable of restraining the door under rebound forces and negative phase blast loads for Door Performance Categories I, II, and III. g) Blast door manufacturer’s calculations or test data shall be provided to verify adequate blast resistance and door performance for the design load conditions. Refer to company specification 12-SAMSS-010 for full requirements. h) Manually operated egress doors shall meet the requirements of SAES-M-100 and be set in motion with a maximum force of 133 N (30 lbs.).Power operated egress doors shall meet requirements of ANSI/BHMA A156.10, be manually opened under power with either a push switch or panic bar, and be openable manually in a power failure with a maximum force of 220 N (50 lbs.). i) Reinforced conventional fire rated metal doors may be used if substantiated with a design calculation or with test data to verify adequate blast resistance and door performance for the design load condition. Refer to company specification 12-SAMSS-010 for full requirements. j) The door system shall be designed to withstand the applied blast loading one time only. k) After an explosion, exit doors and other doors specified in the contract documents shall be manually operable from the inside and outside to permit egress from the building. The response limit for doors other than exit doors shall be specified in the contract documents. l) The door system shall be designed to resist rebound. Maximum rebound forces shall be identified and factored into the system design. m) Exit doors shall meet the requirements of the local building code for swing, maximum opening force, and clear width. n) Exit doors shall meet the requirements of the local building code for swing, maximum opening force, and clear width. o) Subframes designs and details shall be provided in sufficient time for field fabrication and installation in the building. p) The connection of the subframes to the door frames shall be designed to maintain structural integrity throughout all the responses to the applied loads. q) The installation and maintenance of the structural integrity of the subframe installation during construction shall be the responsibility of others. r) Frames shall have adjustable gaskets around the perimeter at heads and jambs for perimeter seling of doors. And bottoms of doors shall have gaskets for sealing at sills. s) Hinges shall be heavy-duty, low-friction, full-mortise ball bearing, with highquality corrosion resistant finish. t) Door leaves and frames shall be shop-painted with one coat of primer and finished to match the walls. | SAES-M-009 Sec 8.1" PIP ARS08390 Sec 4.5/ 4.6/ 4.7"
H-03A | 1. Blast resistant door shall be designed as follows and calculations shall be provided by Vendor. (1) Category: Ⅰ - Hardware: Operable - Panels: Elastic - Ductilty Limit: 1.0 - Edge Rotation: 1.2 deg (2) Category: Ⅱ - Hardware: Operable - Panels: Significant damage - Ductilty Limit: 3 - Edge Rotation: 2 deg (3) Category: Ⅲ - Hardware: Inoperable - Panels: Substantial damage - Ductilty Limit: 10 - Edge Rotation: 8 deg | "SAES-M-009 8.1, Table 11"
H-03B | 2. Blast loads for buildings are as follows, - Central Control Building: 0.81psi / 471.3psi.ms - Central Maintenance Building: 0.49psi / 435psi.ms - EDG Building - Facility Security: 0.53psi / 37psi.ms - EDG Building - MS01: 0.53psi / 37psi.ms - EDG Building - Substation-06: 0.53psi / 30.2psi.ms - EDG Building - Substation-07: 0.36psi / 25.2psi.ms - EDG Building - Substation-08: 0.07psi / 6.5psi.ms - EDG Building - Substation-09: 0.57psi / 45.7psi.ms - 230KV GIS Main Receiving Substation: 0.45psi / 31.8psi.ms - Laboratory & Inspection Building: 0.66psi / 580psi.ms - Main Substation 01: 0.56psi / 36.7psi.ms - Main Substation 02: 0.53psi / 33.5psi.ms - OME Building 03 - Import: 1.41psi / 507.5psi.ms - OME Building 04 - Export: 1.9psi / 1033.1psi.ms - OME Building 05 - Utilities: 0.98psi / 543.8psi.ms - PIB 03 - SRU TGTU Train 1: 0.43psi / 29.3psi.ms - PIB 04 - SRU TGTU Train 2: 0.42psi / 30.7psi.ms - PIB 05 - SRU TGTU Train 3: 0.39psi / 32psi.ms - PIB 06 - Export Area: 0.54psi / 30.3psi.ms - PIB 07 - Utilities: 0.4psi / 29.4psi.ms - PIB 09 - Import Area: 0.71psi / 48.8psi.ms - Substation 06 - Export Area: 0.59psi / 32.5psi.ms - Substation 07 - Utilities: 0.43psi / 31.8psi.ms - Substation 09 - Import Area: 0.69psi / 47psi.ms - Sulfur Loading Control Building: 0.11psi / 101.5psi.ms - Sulfur Loading Welfare Building: 0.1psi / 101.5psi.ms | TE-788210-001_Rev.00A Building Risk Assessment Report
H-04A | Fencing: a) 2.4m high w/ top strand of barbed wire and accessories shall comply to SAES-M-006. b) Saudi aramco security fencing Type-IV shall be used. c) Fencing shall be built according to the reference Saudi Aramco Engineering Standards and Standard Drawings (AB-036677, AA-036678, AB-036679, AC-036680, AE-036881, AE-036882, AE-036883, AE-036884, and AE-036904.) d) Fencing footings shall be provided as per AC-036680 | "Standard Dwgs AB-036677"
H-04B | Fence (General Type): 1. All steel work to be hot-dip galvanized. 2. PVC coated chain link fence: Dia.3.55mm x 40mm x 40mm, PVC coated to 1000 microns (Exact mesh size will be defined during the detailed engineering.) 3. All necessary accessories including access gates w/ padlock set, expansion bolts, bolts, tie wire, tension wire, brace, and similar items shall be provided together. | General
H-07 | Aluminum windows: a) Aluminum windows shall be designed and constructed for integral installation with the system. Unless required otherwise in the contract documents, provide building manufacturer's standard insulated double-pane window (AAMA HS-C20 horizontal sliding, commercial grade) with medium natural anodized finish (NAAMM AA-C22A31). (Alternative if selected by buyer: fixed sash AAMA, Grade C20.) b) Aluminum Extruded Frame: Material shall comply with ASTM B221 or ASTM B221M. c) Provide “thermal-break” construction. Separate frame and sash members exposed on the exterior from metal parts exposed on the interior by a continuous gasket or filler of rubber or plastic, locked into construction. d) Mullions: Provide mullions between adjacent windows, fabricated of extruded aluminum matching the finish of window units. e) Fasteners: Provide aluminum, stainless steel, or other material warranted by the manufacturer to be non-corrosive and compatible with aluminum window members, trim, hardware, anchors, and other components of window units. f) Anchors, Clips, and Window Accessories: Depending on strength and corrosion-inhibiting requirements, fabricate from aluminum, stainless steel, or hot-dip zinc- coated steel (complying with ASTM A123/A123M) according to material compatibility. g) Compression Glazing Strips and Weather-Stripping: Provide molded EPDM, neoprene gaskets complying with ASTM D2000 designation 2BC415 to 3BC620, molded PVC gaskets complying with ASTM D2287, Grade 4, or molded expanded neoprene gaskets complying with ASTM C509. h) Sliding Weather-Stripping: Provide woven pile weather-stripping of wool, polypropylene, or nylon pile and resin-impregnated backing fabric, with aluminum backing strip. Comply with AAMA 701. i) Sealants: Provide manufacturer's standard for the joint size or anticipated movement. The sealant shall remain permanently elastic and be non-shrinking and non-migrating. j) Insect Screens: Provide removable insect screen on each operable exterior sash, with finish matching window. k) Pre-glazed Construction: To the greatest extent possible, glaze units at the shop before installation. l) Glass: Unless required otherwise in the contract documents, comply with ASTM C1036 for glass type, class, quality, style, kind, and form and with recommendations of the FGMA Glazing Manual. | 12-SAMSS-014 Sec 8.2 TD- 821261 8.27
I-01 | Screed: a) Screeds for floor shall be of cement and sand (1:3); the thickness and surface texture are to suit the paving or tiling they are to receive. b) Screeding shall be carried out in bays not exceeding 10 sq.m c) The maximum size of coarse aggregate shall be 10 mm.
I-02 | Access Floor: a) Pedestal floors shall provide a minimum 610 mm clearance between the finished floor surface and subfloor. b) Floor panels shall be gravity held, electrically conductive per UL 779 and shall be made of noncombustible material. c) The floor shall be designed for the static and dynamic loads encountered during normal operation and during the installation of the distributed control system. Static loads and load factors associated with the installation of a particular PCS shall be based on vendor design data. d) Pedestals and stringers shall be designed to accommodate the required clearance and shall provide a rigid stable platform. The pedestal system shall be selected to minimize leveling problems. The floor surface shall be leveled to within +0.25 mm per panel and +1.65 mm in 3.0 m. e) Floor panels shall be surfaced with high pressure laminated fiber resin. f) The 600 x 600 mm square fully removable floor panels shall be formed from heavy duty composite materials with acoustic properties to prevent impact noise, noise transference and tile rocking. They shall be finished with factory applied, hardwearing, anti-static vinyl surface and with aluminum base. g) Floor panels shall be supported by removable stringers and braced, adjustable and lockable steel pedestals, mechanically fixed to the concrete floor base. | SAES-J-801 Sec 8.2
I-03 | Carpet Tile: a) Commercial quality carpet/carpet tiles shall be installed complete with all necessary accessories, underlay, grippers, edgings and trims. b) Installation shall be carried out only when the base surface has a relative humidity above 75%, unless otherwise complying with the recommendations of the carpet manufacturer. c) Any adhesives used in the installation shall be as specified by the carpet manufacturer. d) Color and Textures As selected by COMPANY e) Pattern As selected by COMPANY f) Antron nylon, 100 % loop, Nova II Primex PLB series, manufactured by Mohawk, or approved equal. g) Pile Tufted Multilevel Loop h) Tile Size : 600mm x 600mm i) Warranty period 15 years "j) Yarn Weight 737 grams (26 oz.) per yard. k) Backing Woven synthetic, or with 6 mm thick bonded polyurethane foam cushion" | MIP 6
I-05 | Plastering: a) Materials - Provide Number 1 white silica with 100 percent passing a Number 20 sieve, conforming to ASTM C35 (BS 1199, table 1) for finish coat. - Sand shall be clean, free from organic material, with no more than 5 percent clay, silt, or other impurities and shall contain no salt or alkali. - Use standard brand of Portland Cement conforming to ASTM C-150, Type 1, (BS EN 197-1) white for finish coat. - Normal finishing hydrated lime shall conform to BS EN 459-1. - Metal lath, stops and beads shall be galvanized and shall conform to ASTM C 847 (BS1369-1), as manufactured by Expanded Metals Co. LTD or Catric Compartments Ltd., or equal approved by the CONTRACTOR. b) Mixing - Slurry Coat shall be 400 kgs of cement to one cubic meter of sand. - Second and third coats shall be 300 kgs of cement and 50 kgs of lime to one cubic meter of sand. | BONE
I-06 | Gypsum Board on Metal Stud: a) External walls of all concrete/masonry buildings shall be insulated internally and lined with a gypsum board drywall system utilising steel framing members (Metal Stud). Gypsum board shall be 16 mm thick board of types indicated in maximum lengths useable to minimise end joints. b) Steel Profiles - Steel profiles for studs, runners, furring channels, main carriers (intermediate channels) etc. shall be made of Steel complying with corresponding ASTM standards. c) All edges shall be tapered and the system shall include all edge trim, cornerbeads and control joints. d) Including Polyethylene Sheet (Vapor Barrier), 0.25 mm Fire/Moisture Resistant Gypsum Board w/ Stud: a) Standard Gypsum board - Gypsum board used for building construction shall meet the requirements of ASTM C1396M and SASO 887 standard. It shall consist of a core of gypsum, encased in and firmly bonded to paper liners. It shall be available in thickness of 16mm. b) Fire Resistant Gypsum board - Fire resistant gypsum wallboard used for building construction shall meet the requirements of ASTM C1396M and SASO 887 standard. It shall consist of a core of gypsum, enriched with fibers, encased in and firmly bonded to impregnated paper liners. It sha c) Water-Resistant Gypsum Board - Comply with ASTM C1396M where water-resistant type is indicated to extend beyond the application of wall tile and receive a painted finish provide standard taper long-edge profile. d) Including Polyethylene Sheet (Vapor Barrier), 0.25 mm, Insulation: a) The overall heat transmission coefficient (U-factor) shall not exceed 0.301 W/(m² °K) or 0.053 btu/(h ft² °F). b) The insulation material shall be rot and rodent resistant and must not be affected by temperatures of 65°C (150°F) or by short period exposure to direct sunlight, causing thermal decomposition not related to combustion. c) All insulation materials other than foam plastic shall have a flame-spread rating not to exceed 25 and a smoke density not to exceed 450 in accordance with the International Building Code, 2006 Edition, Section 719. d) The recommanded inuslation material is Polyisocyanurate Insulation Board (mechanically fastened). | MIP 6
I-07 | Suspended Ceiling System (Acoustic Tile): a) Suspended ceiling system shall be lay-in type with exposed grids. b) Material shall comply with all requirements for non-combustibility and sound absorption performance. c) noise reduction coefficient min. 0.55. d) Main and cross runners roll formed from cold-rolled steel sheet, pre-painted, electrolytically zinc coated, or hot-dip galvanized according to ASTM A 653M, not less than Z90 coating designation, with prefinished 15mm wide metal caps on flanges. | MIP 6
I-08 | Suspended Ceiling System (Moisture Resistant Tile): a) Suspended ceiling system shall be lay-in type with exposed grids. b) Main and cross runners roll formed from cold-rolled steel sheet, pre-painted, electrolytically zinc coated, or hot-dip galvanized according to ASTM A 653M, not less than Z90 coating designation, with prefinished 15mm wide metal caps on flanges. | MIP 6
I-10A | Single Metal Wall Sheet : 1. The panel shall be made of a minimum 0.5 mm (26 gage) thick galvanized or aluminum-zinc alloy-coated steel sheet, or aluminum as applicable, formed architecturally consistent with the ribbing of the roof. 2. Wall panels shall have nominal covering width not less than 900 mm (3 ft nominal) unless approved otherwise by Saudi Aramco. 3. Wall panels shall be supported at their base by a raised curb or grade beam that is a minimum of 150 mm above the building floor level. Wall panels shall extend not less than 38 mm below the concrete support, and sit in a recess in the concrete grade beam or curb to close off the lower end of the panels. The panels shall be self-draining to the exterior. 4. Galvanized sill angles shall be provided to secure wall panels to the grade beam or curb. 5. Galvanized steel for flashing shall be minimum 0.5 mm (26 gage). | "12-SAMSS-014 6.5.1 12-SAMSS-014 6.5.3 12-SAMSS-014 6.7.2"
I-10B | Single Metal Roof Sheet: a) Roof panels shall be made of a minimum 0.5 mm (26 gage) thick galvanized steel sheet. b) Panels shall provide a net coverage width of 900 mm (3 ft nominal) minimum. Roof panels shall be laid full length from ridge to eaves where possible to minimize the possibility of water leaks at the end laps. When required, end lap shall be a minimum of 100 mm (4 inches nominal). c) Material for prepainted galvanized steel panels shall have a minimum yield of 230 MPa (33 ksi) and conform to ASTM A653/A653M SS Grade 33 (Grade 230) or better and galvanized in accordance with coating designation of G90 (Z275). d) A chemical and pollution resistant paint finished profiled metal sheet on a galvanised steel support framework. The system shall be specified complete with matching flashings, closures, trims, rainwater goods and fixings and shall be compatible with all door and louvre systems proposed for the PROJECT. e) Galvanized steel for flashing shall be minimum 0.5 mm (26 gage). | 12-SAMSS-014 Sec 6.5.3, 6.5.1
I-10C | Insulated Sandwich Wall Panel : 1. Wall panels shall be self-contained, factory assembled foam plastic insulated units, having a nominal covering width not less than 900 mm (3 ft nominal) unless approved otherwise by Saudi Aramco. 2. The prepainted exterior face sheet shall be made of a minimum 0.5 mm (26 gage) galvanized steel sheet and shall be formed architecturally to provide adequate rigidity. 3. The prepainted interior face sheet shall be made of a minimum 0.5 mm (26 gage) galvanized steel sheet shall be formed into a plane surface. 4. Metal to metal contact between the interior and exterior faces on vertical edges shall be prevented. 5. The vertical joints shall overlap having a thermal break and providing for mechanical, as well as thermal, horizontal movement. The panel design shall provide for expansion and/or contraction as caused by an ambient temperature range without causing harmful buckling, opening of joints, or other detrimental effects. 6. Contractor shall submit three material samples to match what is shown in the document TD-841501 "Material and Finishes Schedule" during EPC for COMPANY's final selection and approval. 7. Galvanized steel for flashing shall be minimum 0.5 mm (26 gage). 8. The overall heat transmission coefficient (U-factor) shall not exceed 0.528 W/(m² °K) or 0.093 btu/(h ft² °F). | 12-SAMSS-014 6.5.2, 6.5.4 12-SAMSS-014 6.7.2 TD-841501
I-10D | Insulated Sandwich Roof Panel : 1. Roof panels shall be self-contained, factory assembled foam plastic insulated units having a nominal covering width of not less than 900 mm (3 ft nominal) unless approved otherwise by Saudi Aramco. 2. The exterior face sheet shall be made of minimum 0.5 mm (26 gage) thick galvanized steel sheet and shall be formed architecturally to provide adequate rigidity. 3. The interior face sheet shall be minimum 0.5 mm (26 gage) thick galvanized steel sheet and shall be formed into a plane surface. 4. Galvanized steel for flashing shall be minimum 0.5 mm (26 gage). 5. The overall heat transmission coefficient (U-factor) shall not exceed 0.369 W/(m² °K) or 0.065 btu/(h ft² °F). | 12-SAMSS-014 6.5.2 12-SAMSS-014 6.7.2
I-11 | Gypsumboard Partition Wall: 1. Gypsumboard partitions shall be based on a steel frame(galvanized metal bars) fixed to the floor underlying layer and roof slab when fire rating is required. But, ther partition shall be installed between the floor finish and the soffit of the ceiling as the removable type when it doesn't needs to be the fire resistant type. 2. Partitions shall be minimum of 100 mm thick, including sound insulation (glass wool, minimum density 50 kg/m³), to meet the specified sound transmission loss. 3. Steel framing members and all fixings to gypsum board construction shall comply with the manufacturers recommendation for relevant application. 4. The type of gypsum board, general/moisture resistant/fire resistant, shall be selected considering the proposed installation area.
I-13 | Downspouts: Downspouts shall be round or rectangular shaped 0.5 mm (26 gage) galvanized steel. Downspouts shall have a 45 degree elbow at the bottom and shall be supported by attachment to the wall covering at every sidewall girt location. | 12-SAMSS-014 Sec 8.7
I-17 | Eave Gutters: Eave Gutters shall be box shaped 0.7 mm (24 gage) galvanized steel. The outside face of the gutter shall be supported with 2.0 mm galvanized steel straps to the eave member at a maximum spacing of 1000 mm. | "12-SAMSS-014 8.7"
I-18 | Safety Bollard a) C.S pipe post 100 to 150mm dia. x 1700mm height(Exposed: 1200mm, Embedded: 800mm) steel pipe filled with concrete b) Painted with 2 coats of yellow reflective standard traffic paint | SASD AE-036412-001
I-19 | Signage: Each building shall have identification signs posted on the sides of the main entrances of the building and other sides as deemed necessary by the building owner. All signs required by this Code shall be designed in accordance with the signing guidelines of Saudi Aramco Corporate Identity, Public Relations Department. Signs should not pose any hazards to occupants in buildings subject to blast loads. | SAES-M-100 Appendix H
I-20 | Concrete Wheel Stop : Width 1000, drilled hold down pin (300 long) w/ 10mm horizontal bar : Hold down pin length 300mm, 16mm bar 5ΦO.D. X 3THK. Steel Washer | DD-950107
I-22 | Matwell: Matwell frames shall be cast into screed or floor slabs and manufactured from aluminium angles, mitred at corners and welded with suitable mat inlays. | TD-821261 rC 8.9.7
J-01 | Structural Steel a) Structural Steel - Steel for W- and WT- sections, and for plate girders shall be high strength, Grade 50 steel conforming to ASTM A992/A992M. - Secondary steel shall be considered to include all other off grid steel, including minor equipment supports, access platforms, floor and stair stringers, trimming steel, lifting/runway beams, baseplates and ‘special’ pipe supports generally. - Steel for M, S, HP, C, MC and L shapes shall be Grade 36 steel conforming to ASTM A36/A36M or equivalent, alternative materials shall only be applicable with approval of COMPANY. - All other structural shapes, plates and bars shall be ASTM A36/A36M in accordance with 12-SAMSS-007, section 4.2. - Fabrication shall be in accordance with 12-SAMSS-007. Erection shall be in accordance with 12-SAMSS-008. b) Protection Coatings - All steel, steel shapes and plates shall be hot-dip galvanized and painted in accordance with coating systems specified in SAES-H-004. c) Connections - All bolted structural connections shall consist of bearing-type high strength bolts in accordance with 12-SAMSS-007, section 4.6, minimum bolt diameter shall be 20mm. - All other bolted connection (e.g. for purlins, girts, door frames, ladders, handrails and stairs) shall consist of ASTM A307 grade A bolts per 12-SAMSS-007. Minimum bolt diameter shall be 16mm. - All bolted connections shall have a minimum of two bolts U.O.N. d) For more detail, refer to 12-SAMSS-007 Structural bolts a) All structural bolts shall be galvanised to 12-SAMSS-007 high strength bolts and conform to the following sizes and standard: - Primary members : M20 or larger ASTM F3125M; Bolt: ASTM A25M Type-1 Heavy Hex Nut: ASTM A563M Grade 10S Washer: ASTM F436M Type -1 Coating: Galvanized as per ASTM B695, or ASM A153/153M - Secondary members : M16 or smaller ASTM F3125M. | TD-821201 rC 10.1, 10.2
J-02 | Anchor Bolt: a) Threaded holding-down bolts shall comply with ASTM F1554 Grade 36 or equivalent and nuts to be ASM A563 Grade A per ASTM A153 class C or ASTM B695 Class 50. b) High strength holding-down bolts shall comply with ASTM F1544 Grade 105, brittle fracture should be accounted for as per ACI 318. c) All items shall be hot-dipped galvanized as per the requirements of 12-SAMSS-007 and in compliance with SAUDI ARAMCO standard drawing AA-036322 sheet 001. d) Post-installed anchors shall comply with manufacturer’s recommendations and shall be subject to approval of COMPANY. e) head bolt, washer, plate washer and nuts shall be as follows; Headed Bolts - ASTM A307 Grade A (Hex ½" - 1½" diameter, Heavy Hex over 1½" diameter) Washers - ASTM F436 or ASTM F436M Plate Washers - ASTM A36/ASTM A36M Nuts - ASTM A563 Grade A, Heavy Hex or ASTM A563M | TD-821201 Rc 10.7 12-SAMSS-007 4.6
J-03 | Non-Shrink Grout a) Cement based non-shrink grout in accordance with SAES-Q-010 and shall have a minum 28-days compressive strength of 35MPa. | SAES-Q-010 Sec 4.2.1 / 5.1.6
J-04 | Grating: a) ASTM A1011/A1011M, galvanized per ASTM A123/A123M b) Steel grating shall be rectangular type, with plain 3/16-inch x 1-1/4-inch (5-mm x 32-mm bearing bars on 1-3/16-inch (30-mm) spacing with cross bars on 4-inch (100-mm) spacing. c) Grating stair treads shall have abrasive or checkered plate nosing. d) Heavy duty metal bar grating shall comply with NAAMM MBG 532. | 12-SAMSS-007_ Sec. 4.14
J-05 | Checkered Floor Plates: a) Raised-pattern (checkered) floor plate shall meet requirements of 12-SAMSS-007 and be minimum 6mm thick when not specified on the drawings. b) Checkered plates shall be ASTM A786/A786M pattern 4 or 5 material to ASTM A36/A36M and 12mm drain hole for eaxh 2 m2 of area.
J-06 | Handrails: a) Pipe for columns or handrail shall be per ASTM A53/A53M Type E or S, Grade B or ASTM A106/A106M Grade B. b) OD 48mm Galv. Pipe Post & painted c) Hot dip galvanized in accordance with ASTM A123 d) APCS-26 as per SAES-H-004 e) Color coding: 'safety yellow (RAL 1023)' in SAES-B-067 Sec.4.2 f) For more details, see PIP STF05520 | 12-SAMSS-007 Sec 4.3
J-10 | Ladder: a) Refer to PIP STF05501 and 12-SAMSS-007 b) Max. Distance between landings : 9000mm c) Material: ASTM A36 d) Hop dip galvanized in accordance with ASTM A123 e) APCS-26 as per SAES-H-004 f) Unless noted otherwise on the contract documents, a self-closing double bar safety gate, in conformance with OSHA, shall be provided for all ladders. g) Ladder rung design is based on a 200-pound (890-N) concentrated live load. | SAES-B-054 PIP STF05501