## AUX 2
AUX 2
No. | Punch No | System | Subsystem | Location / Area | Tag/Drawing/Line/Cable No. | Punch Description | Punch Category | Discipline | Action by | Originator | Issued Date | Closed Date | Punch Type | Note | Remarks | Submit to Owner | Punch Comment | File | RFI No | Report No.(Old) | Target Date | Scope of Punch
. | 26877 | 800.00 | 1304-12-28 | Operator Building (1000-OB-45F) | EGAT-HEC-1000-HVA-DWG-38401 | Lack of flushing and desinfection PW water installation | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26878 | 800.00 | 1304-12-28 | Operator Building (1000-OB-45F) | EGAT-HEC-1000-HVA-DWG-38401 | Lack of final inspection | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26879 | 800.00 | 1304-12-28 | Operator Building (1000-OB-45F) | EGAT-HEC-1000-HVA-DWG-38401 | Lack of sanitary accesories | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-24 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26880 | 800.00 | 1304-12-28 | Operator Building (1000-OB-45F) | EGAT-HEC-1000-HVA-DWG-38401 | Isulation of PW installation need to be replaced | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-22 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26881 | 800.00 | 1304-12-28 | Operator Building (1000-OB-45F) | EGAT-HEC-1000-HVA-DWG-38401 | Earthing cabel is not connected | C | EL | HEC EL Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-03-21 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26882 | 800.00 | 1304-12-28 | Operator Building (1000-OB-45F) | EGAT-HEC-1000-HVA-DWG-38401 | lack of dewatering installation from safety valve | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-24 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26942 | 800.00 | 1304-12-28 | Operator Building(1000-OB-45F) | EGAT-HEC-900-ELE-DLP-01004,EGAT-HEC-900-ELE-DLP-05022,EGAT-HEC-1000-ELE-DLP-04008 | Normal and Emergency Lighting fixtures, Cable tray Installation to be complete and official inspection to be carried out. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-18 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26943 | 800.00 | 1304-12-28 | Operator Building(1000-OB-45F) | EGAT-HEC-900-ELE-DLP-01004,EGAT-HEC-900-ELE-DLP-05022,EGAT-HEC-1000-ELE-DLP-04008 | Cable pulling and Cable termination to be done and official inspection to be carried out. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-19 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26944 | 800.00 | 1304-12-28 | Operator Building(1000-OB-45F) | EGAT-HEC-900-ELE-DLP-01004,EGAT-HEC-900-ELE-DLP-05022,EGAT-HEC-1000-ELE-DLP-04008 | Socket Outlet, Escape Lighting, Exit Lighting, Canopy lighting to be installed and oficially inspection to be carried out. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-19 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26945 | 800.00 | 1304-12-28 | Operator Building(1000-OB-45F) | EGAT-HEC-900-ELE-DLP-01004,EGAT-HEC-900-ELE-DLP-05022,EGAT-HEC-1000-ELE-DLP-04008 | Tag no- 45F-PDP-001&002 Panel to be installed and official inspection to be carried out. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-19 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26946 | 800.00 | 1304-12-28 | Operator Building(1000-OB-45F) | EGAT-HEC-900-ELE-DLP-01004,EGAT-HEC-900-ELE-DLP-05022,EGAT-HEC-1000-ELE-DLP-04008 | Lighting (45A-ELP-001/10) on the roof to be installed and oficial inspection to be done. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-19 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26947 | 800.00 | 1304-12-28 | Operator Building(1000-OB-45F) | EGAT-HEC-900-ELE-DLP-01004,EGAT-HEC-900-ELE-DLP-05022,EGAT-HEC-1000-ELE-DLP-04008 | Earthing for the Door frame, Monkey ladder, HVAC Fans to be provided | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-19 | 2023-04-18 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26948 | 800.00 | 1304-12-28 | Operator Building(1000-OB-45F) | EGAT-HEC-900-ELE-DLP-01004,EGAT-HEC-900-ELE-DLP-05022,EGAT-HEC-1000-ELE-DLP-04008 | Lightning protection bare copper tape and lightning air terminal to be installed. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-19 | 2023-04-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26949 | 800.00 | 1304-12-28 | Operator Building(1000-OB-45F) | EGAT-HEC-900-ELE-DLP-01004,EGAT-HEC-900-ELE-DLP-05022,EGAT-HEC-1000-ELE-DLP-04008 | Earth rod with Test well for lightning protection to be installed . | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-19 | 2023-03-24 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26950 | 800.00 | 1304-12-28 | Operator Building(1000-OB-45F) | EGAT-HEC-900-ELE-DLP-01004,EGAT-HEC-900-ELE-DLP-05022,EGAT-HEC-1000-ELE-DLP-04008 | Earthing resistance test to be done protocol to be submitted. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-19 | 2023-04-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26951 | 800.00 | 1304-12-28 | Operator Building(1000-OB-45F) | EGAT-HEC-900-ELE-DLP-01004,EGAT-HEC-900-ELE-DLP-05022,EGAT-HEC-1000-ELE-DLP-04008 | Illumination test to be done and protocol to be submitted. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-19 | 2023-04-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26952 | 800.00 | 1304-12-28 | Operator Building(1000-OB-45F) | EGAT-HEC-1000-ELE-DLP-04008 | Smoke detectors, Fire Beacon, Remote Indicator,Power suppl unit, Manual call point, Alarm Pushbutton and Transponder I/O module box to be installed and oficially Inspection to be carried out. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-19 | 2023-06-01 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26953 | 800.00 | 1304-12-28 | Operator Building(1000-OB-45F) | EGAT-HEC-1000-ELE-DLP-04008 | Fire alarm Cable pulling and termination to be done and oficial inspection to be carried out. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-19 | 2023-06-01 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26954 | 800.00 | 1304-12-28 | Operator Building(1000-OB-45F) | EGAT-HEC-1000-ELE-DLP-04008 | Fire Alarm Sat to be done | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | EGAT-RFI-AR-GS-06360.01 | 800.00 | 1304-12-28 | 1000-OB-45F | Axis D-C/3-4 | Chamfering to be redone | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-23 | 2022-08-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06360 |  |  | Construction
. | EGAT-RFI-AR-GS-06360.02 | 800.00 | 1304-12-28 | 1000-OB-45F | Axis D-C/3-4 | Walkway to be repaired / finished after dismantle of the scaffolding | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-23 | 2022-08-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06360 |  |  | Construction
. | EGAT-RFI-AR-GS-06895.01 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Silicon around doors to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-04 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-06895.02 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Top of the tiles to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-04 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-06993.01 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Tiles not in flat surface | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06993 |  |  | Construction
. | EGAT-RFI-AR-GS-06993.02 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Tiles around drain to be improved | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06993 |  |  | Construction
. | EGAT-RFI-AR-GS-06993.03 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Joints and sealant to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06993 |  |  | Construction
. | EGAT-RFI-AR-GS-07002.01 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Cleaning ceiling tile | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-21 | 2022-11-28 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07002 |  |  | Construction
. | EGAT-RFI-AR-GS-07412.01 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Embeded plate for canopy rod - to be checked if not too deep | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-16 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07412 |  |  | Construction
. | EGAT-RFI-AR-GS-07455.01 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Plaster under cable trays to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-25 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07455 |  |  | Construction
. | EGAT-RFI-AR-GS-07566.01 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Splash block missing | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-08 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07566 |  |  | Construction
. | EGAT-RFI-AR-GS-07915.01 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Dilatation between stoop and building to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-04 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07915.02 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Dilatation between stoop and walkway to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-04 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07915.03 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Damaged to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-04 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07919.01 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Walkway to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-11 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07919.02 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Lack of Vertical chamfering on ladder foundation | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-11 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07121.01 | 800.00 | 1304-12-28 | 1000-OB-45F | EGAT-HEC-900-ELE-DLP-06003_Z0 | Logic tag should be provide for divise. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-14 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07121.02 | 800.00 | 1304-12-28 | 1000-OB-45F | EGAT-HEC-900-ELE-DLP-06003_Z0 | Name tag should be provide for Devises. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-14 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07121.03 | 800.00 | 1304-12-28 | 1000-OB-45F | EGAT-HEC-900-ELE-DLP-06003_Z0 | Cable tag should be provide. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-14 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07121.04 | 800.00 | 1304-12-28 | 1000-OB-45F | EGAT-HEC-900-ELE-DLP-06003_Z0 | Power cable for ZSP should be fixed. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-14 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07201.01 | 800.00 | 1304-12-28 | 1000-OB-45F | EGAT-HEC-900-ELE-DLP-06003(4 OF 4) | All FACPs shall work as Fiber Optic Ring. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-24 |  | SAT |  | 1000-FACP-RIB12-0001 |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07201.02 | 800.00 | 1304-12-28 | 1000-OB-45F | EGAT-HEC-900-ELE-DLP-06003(4 OF 4) | All faults to be cleared from 1000-FACP-RIB12-0001. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-24 |  | SAT |  | 1000-FACP-RIB12-0001 |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07201.03 | 800.00 | 1304-12-28 | 1000-OB-45F | EGAT-HEC-900-ELE-DLP-06003(4 OF 4) | 1000-MAC-8641-CNBOP glow in the dark plate missing. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-24 |  | SAT |  | 1000-FACP-RIB12-0001 |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07201.04 | 800.00 | 1304-12-28 | 1000-OB-45F | EGAT-HEC-900-ELE-DLP-06003(4 OF 4) | Tags for all SD's missing. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-24 |  | SAT |  | 1000-FACP-RIB12-0001 |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-00914.01 | 800.00 | 1304-12-28 | 1000-OB-45F | PW Pipe Installation | Prepare as built documentation | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-25 | 2022-09-01 | Construction |  | Sign Punch to be delivered by 9/2 from JW |  |  | V | EGAT-RFI-HV-JW-00914 |  |  | Construction
. | EGAT-RFI-HV-JW-00914.02 | 800.00 | 1304-12-28 | 1000-OB-45F | PW Pipe Installation | Fastening the pipe | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-25 | 2023-02-22 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00914 |  |  | Construction
. | EGAT-RFI-HV-JW-00940.01 | 800.00 | 1304-12-28 | 1000-OB-45F | PW Pipe Installation | To be assembled elbows in a walls, all connection | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-31 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00940 |  |  | Construction
. | EGAT-RFI-HV-JW-01046.01 | 800.00 | 1304-12-28 | 1000-OB-45F | UG PW Pipe Installation | To be provided bolting report of PW connection | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01046 |  |  | Construction
. | EGAT-RFI-HV-JW-01046.02 | 800.00 | 1304-12-28 | 1000-OB-45F | UG PW Pipe Installation | To be provided wrapping report of PW connection | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2022-10-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01046 |  |  | Construction
. | EGAT-RFI-HV-JW-01104.01 | 800.00 | 1304-12-28 | 1000-OB-45F | PW Pipe Isulation | To be cut orange PVC pipe entering to bld | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-08 | 2023-02-22 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01104 |  |  | Construction
. | EGAT-RFI-HV-JW-01412.01 | 800.00 | 1304-12-28 | 1000-OB-45F | Hvac Equipment | Fan flow efficiency need to be verified with documentation | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-03-15 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-HV-JW-01415.01 | 800.00 | 1304-12-28 | 1000-OB-45F | Hvac Duct work | Dumper is on collission with doors | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-03-15 | 2023-03-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01462.01 | 800.00 | 1304-12-28 | 1000-OB-45F | - | Lack of tags on wall fan and electric radiators | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-04-18 | 2023-04-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | UG-0003 | 800.00 | 1504-14-10 | 1000-OB-45F | 1000-OB-45F | Underneath of paving exposed | A | CV | HEC CV Construction | J.T.Choi | 2022-09-13 | 2022-10-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | 18034 | 800.00 | 1304-12-10 | Raw Water Treatment Building | 810-SHT-CC-100 | The doors should be repaired. All doors should be finished. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-14 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18035 | 800.00 | 1304-12-10 | Raw Water Treatment Building | 810-SHT-CC-100 | The corner should be covered by steel angle. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-14 | 2023-06-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18036 | 800.00 | 1304-12-10 | Raw Water Treatment Building | 810-SHT-CC-100 | All technological passage should be finished. | B | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-14 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18037 | 800.00 | 1304-12-10 | Raw Water Treatment Building | 810-SHT-CC-100 | All doors should be finished. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-14 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18038 | 800.00 | 1304-12-10 | Raw Water Treatment Building | 810-SHT-CC-100 | The entrance gate isn't installed. | A | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-14 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18039 | 800.00 | 1304-12-10 | Raw Water Treatment Building | 810-SHT-CC-100 | Remove the foam excess. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-14 | 2023-03-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18040 | 800.00 | 1304-12-10 | Raw Water Treatment Building | 810-SHT-CC-100 | Corrosion and damages on the crane beam | C | SS | HEC SS Construction | Mr. Andrzej Wójcikiewicz | 2022-12-14 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18041 | 800.00 | 1304-12-10 | Raw Water Treatment Building | 810-SHT-CC-100 | No canopy above the entrance. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-14 | 2023-05-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18042 | 800.00 | 1304-12-10 | Raw Water Treatment Building | 810-SHT-CC-100 | Thermal insulation of foundation should be finished. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-14 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18043 | 800.00 | 1304-12-10 | Raw Water Treatment Building | 810-SHT-CC-100 | The U-ditch should be finished. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-14 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18044 | 800.00 | 1304-12-10 | Raw Water Treatment Building | 810-SHT-CC-100 | UDT inspection to be done | C | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-12-14 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 18045 | 800.00 | 1304-12-10 | Raw Water Treatment Building | 810-SHT-CC-100 | Limit switch to be installed | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-12-14 | 2023-01-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18046 | 800.00 | 1304-12-10 | Raw Water Treatment Building | 810-SHT-CC-100 | Limit switch for Hoist not installed | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-12-14 | 2023-01-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 21098 | 800.00 | 1304-12-10 | Raw Water Treatment Building | EGAT-HEC-900-ELE-DLP-01005, 04018 & 05026 | Canopy lighting fixture is missing to be provided | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-03-27 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21099 | 800.00 | 1304-12-10 | Raw Water Treatment Building | EGAT-HEC-900-ELE-DLP-01005, 04018 & 05026 | Lighting fixture cable tags is missing | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-03-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21100 | 800.00 | 1304-12-10 | Raw Water Treatment Building | EGAT-HEC-900-ELE-DLP-01005, 04018 & 05026 | Lighting JB blind plug is missing to be provided | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-03-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21101 | 800.00 | 1304-12-10 | Raw Water Treatment Building | EGAT-HEC-900-ELE-DLP-01005, 04018 & 05026 | Instrument beacon cable entry on wall to be provide fire sealing | B | CI | HEC CI Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-01-19 | Walkdown |  |  | 2023-01-07 |  | V |  |  |  | RFC/RFSU
. | 29580 | 800.00 | 1304-12-10 | Raw Water Treatment Building (810-SHT-CC-100) | General | Lack of SAT inspection | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-12 | 2023-03-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29581 | 800.00 | 1304-12-10 | Raw Water Treatment Building (810-SHT-CC-100) | General | Lack of Final Inspection- HVAC/Plumbng | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-12 |  | Walkdown | [8 empty] | RFC/RFSU
. | 29582 | 800.00 | 1304-12-10 | Raw Water Treatment Building (810-SHT-CC-100) | General | Lack of Final Inspection- Fire Protection | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-12 |  | Walkdown | [8 empty] | RFC/RFSU
. | 29583 | 800.00 | 1304-12-10 | Raw Water Treatment Building (810-SHT-CC-100) | Eyewash | Lack of Polish describtion | C | ME | HEC ME Construction | Ms. Daria Pliszka | 2022-12-12 | 2023-04-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29584 | 800.00 | 1304-12-10 | Raw Water Treatment Building (810-SHT-CC-100) | Eyewash | Lack of drainage pipe | C | EM | HEC SE Design | Ms. Daria Pliszka | 2022-12-12 |  | Walkdown | [8 empty] | RFC/RFSU
. | 29585 | 800.00 | 1304-12-10 | Raw Water Treatment Building (810-SHT-CC-100) | Eyewash | Touch up and cleaning should to be provided | C | ME | HEC ME Construction | Ms. Daria Pliszka | 2022-12-12 | 2023-03-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29586 | 800.00 | 1304-12-10 | Raw Water Treatment Building (810-SHT-CC-100) | Eyewash | The Eyewash is not mounted stably | C | ME | HEC ME Construction | Ms. Daria Pliszka | 2022-12-12 | 2023-04-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29587 | 800.00 | 1304-12-10 | Raw Water Treatment Building (810-SHT-CC-100) | PW installation | Lack of part of insulation and jacketing on PW outside | C | IN | HEC IN Construction | Ms. Daria Pliszka | 2022-12-12 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29588 | 800.00 | 1304-12-10 | Raw Water Treatment Building (810-SHT-CC-100) | Heating installation | Touch up for UH should to be corrected | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-12 | 2023-03-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 32456 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Coating (paint) damages due to construction work activities. All structure including miscellaneus structure. | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2023-06-21 |  | PAC | [8 empty] | RFC/RFSU
. | EGAT-RFI-AR-GS-01426.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | EF2 | To be attach bearing capacity confirmation | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-03-26 | 2021-12-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-01426 | C-AR-GS-00011 |  | Construction
. | EGAT-RFI-AR-GS-01428.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | FDN F4 | To be attach bearing capacity confirmation | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-03-26 | 2022-01-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-01428 | C-AR-GS-00012 |  | Construction
. | EGAT-RFI-AR-GS-01452.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | FDN F2 Axis A~B/3 | To be attached bearing capacity confirmation | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-04-18 | 2022-08-01 | Construction |  | 'Punch Category' changed C -> A (2022-08-01) evidence attached |  |  | V | EGAT-RFI-AR-GS-01452 | C-AR-GS-00021 |  | Construction
. | EGAT-RFI-AR-GS-04079.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Ground Slab Axis 2-3/D-H | The last 2.10m of Slab is not ready (Axis D) | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-09-28 | 2021-11-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-04121.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Trench Axis D/2-3 | Finishing Works for correction | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-10-06 | 2023-02-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-04334.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Tie Girder & Pedestal Axis A-C/1 ,1-2/C | The same level of the girder and the slab | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-10-27 | 2022-09-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-04334 |  |  | Construction
. | EGAT-RFI-AR-GS-05121.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | EP 1-4; Stair foundation | Chantering to correct | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-17 | 2023-02-06 | Construction | 2022-02-21 |  |  |  | V | EGAT-RFI-AR-GS-05121 |  |  | Construction
. | EGAT-RFI-AR-GS-05121.02 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | EP 1-4; Stair foundation | Close the holes after nails | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-17 | 2023-02-06 | Construction | 2022-02-21 |  |  |  | V | EGAT-RFI-AR-GS-05121 |  |  | Construction
. | EGAT-RFI-AR-GS-05121.03 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | EP 1-4; Stair foundation | Grinding the surface | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-17 | 2023-02-06 | Construction | 2022-02-21 |  |  |  | V | EGAT-RFI-AR-GS-05121 |  |  | Construction
. | EGAT-RFI-AR-GS-05809.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Axis 2-3/A-H | Doors on the north side and west side are scratched | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05809 |  |  | Construction
. | EGAT-RFI-AR-GS-06026.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | F1-F4, PD1-PD3 | Chamfering to be done | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-22 | 2023-06-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06026 |  |  | Construction
. | EGAT-RFI-AR-GS-06042.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Axis 1-3/A-H | Sump pit is flooded | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-16 | 2023-06-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06042 |  |  | Construction
. | EGAT-RFI-AR-GS-06042.02 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Axis 1-3/A-H | Surface of the ground slab to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-16 | 2023-06-19 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06042 |  |  | Construction
. | EGAT-RFI-AR-GS-06042.03 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Axis 1-3/A-H | Lack of sealant | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-16 | 2023-06-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06042 |  |  | Construction
. | EGAT-RFI-AR-GS-06042.04 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Axis 1-3/A-H | Damages of the surface of the ground slab to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-16 | 2023-06-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06042 |  |  | Construction
. | EGAT-RFI-AR-GS-06063.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | EF1, EC1, EP5, EP6, EP7, EP7A, EP8 | Surface to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-05 | 2023-06-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06063 |  |  | Construction
. | EGAT-RFI-AR-GS-06063.02 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | EF1, EC1, EP5, EP6, EP7, EP7A, EP8 | Damages to be required | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-05 | 2023-06-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06063 |  |  | Construction
. | EGAT-RFI-AR-GS-06063.03 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | EF1, EC1, EP5, EP6, EP7, EP7A, EP8 | Lack of epoxy coating | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-05 | 2023-06-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-06063 |  |  | Construction
. | EGAT-RFI-AR-GS-06063.04 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | EF1, EC1, EP5, EP6, EP7, EP7A, EP8 | Surface to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-05 | 2023-06-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06063 |  |  | Construction
. | EGAT-RFI-AR-GS-06171.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Axis 1-3/A-H | Lack of base angle | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-08 | 2023-06-19 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06171 |  |  | Construction
. | EGAT-RFI-AR-GS-06171.02 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Axis 1-3/A-H | Panel dents under the fasteners | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2021-07-08 | 2023-06-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06171 |  |  | Construction
. | EGAT-RFI-AR-GS-06171.03 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Axis 1-3/A-H | Panel damages | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-08 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-06171 |  |  | Construction
. | EGAT-RFI-AR-GS-06171.04 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Axis 1-3/A-H | Three screws should be used to fix the last panels | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-08 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06171 |  |  | Construction
. | EGAT-RFI-AR-GS-06935.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Axis 3/H-F | Lean concrete elevation too low (10 cm). Rebar should be raised | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-02 | 2022-11-08 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06935 |  |  | Construction
. | EGAT-RFI-AR-GS-06975.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Flashing | No flashing around doors | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 | 2023-06-19 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06975 |  |  | Construction
. | EGAT-RFI-AR-GS-06975.02 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Flashing | Bottom flashing - bended and dirty | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-06975 |  |  | Construction
. | EGAT-RFI-AR-GS-06975.03 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Flashing | No flashing around wall penetration (piping, cables, structure) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 | 2023-06-19 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06975 |  |  | Construction
. | EGAT-RFI-AR-GS-07137.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Folding Door | Missing flashing around folding door | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-01-14 | 2023-02-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07137 |  |  | Construction
. | EGAT-RFI-AR-GS-07137.02 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Folding Door | Protect door againts scratches | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-01-14 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07137 |  |  | Construction
. | EGAT-RFI-AR-GS-07191.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Panel Installation | Missing flashing from inside bottom on windows | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-28 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07191 |  |  | Construction
. | EGAT-RFI-AR-GS-08150.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | Top surface to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-20 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08150.02 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | Corossion on steel angle | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-20 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08151.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | Sandwich panels dirty | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08151.02 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | Folding doors to be checked when possible to open, folding doors dirty, scratched hinces rusted, coating damaged, sealant around to be done | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08151.03 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | Sealant to be done around canopy construction | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08151.04 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | Lack of plinth | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08151.05 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | Flashing bended dirty | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08151.06 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | Different level of steel angles on sxtension trench, grating to be cleaned and anti-corrossion protected | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08151.07 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | Connection with civil trench to be secured | C | CV | HEC CV Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08151.08 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | Part of grating missing | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 | 2023-06-26 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08151.09 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | Downspout mounting damaged | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08151.10 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | No isolation over a trench south west side | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08151.11 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | Lack of grating-inside trench | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 | 2023-06-26 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08151.12 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | - | Panels to be cleaned inside | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-CI-CW-01161.01 | 800.00 | 1304-12-10 | 810-AUX | 810-XV-1032 | Provide flow direction confirmation | C | CI | CW Construction | Mr. Tomasz Jozel | 2022-04-27 | 2023-03-31 | Construction |  |  | 2023-03-24 | Closed on 31/03 | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01161.02 | 800.00 | 1304-12-10 | 810 AUX | 810-XV-1032 | Provide atex certificate | C | EM | HEC CI Design | Mr. Tomasz Jozel | 2022-04-27 | 2022-07-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01257.01 | 800.00 | 1304-12-10 | Raw water treatment and fire water | Cable tray | Grouting to be done for cable tray support | B | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-05-12 | 2022-12-09 | Construction |  |  | 2022-12-05 |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01196.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Duct Installation | To be cleaned the louvers and VD | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-08 | 2022-12-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01197.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | 810-SHT-CC-100 | To be installed a local panels | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-08 | 2022-12-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01197.02 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | 810-SHT-CC-100 | To be re-painted the supports of UH | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-08 | 2022-12-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01198.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | Roof | To be removed dust and paint | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-08 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01372.01 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | HVAC start up inspection | Sound level shall be measurement - fans | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-11 | 2023-05-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01372 |  |  | Construction
. | EGAT-RFI-HV-JW-01372.02 | 800.00 | 1304-12-10 | 810-SHT-CC-100 | HVAC start up inspection | Difficult access to main switch of the heaters | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-11 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01372 |  |  | Construction
. | EGAT-RFI-SS-MK-01260.01 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Curved toe plates of the handrailings | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-28 | 2022-06-02 | Construction | 2022-03-29 |  |  |  | V | EGAT-RFI-SS-MK-01260 |  |  | Construction
. | EGAT-RFI-SS-MK-01260.02 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | The gap between grating and toe board | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-28 | 2023-06-12 | Construction | 2022-03-29 |  |  |  | V | EGAT-RFI-SS-MK-01260 |  |  | Construction
. | EGAT-RFI-SS-MK-01260.03 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Curved handrailings | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-28 | 2022-06-02 | Construction | 2022-03-29 |  |  |  | V | EGAT-RFI-SS-MK-01260 |  |  | Construction
. | EGAT-RFI-SS-MK-01260.04 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | No support for the ladder flight at the ground level | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-03-28 | 2022-11-25 | Construction | 2022-03-29 | 'Discipline' changed SS -> AR (2022-06-10) evidence attached |  |  | V | EGAT-RFI-SS-MK-01260 |  |  | Construction
. | EGAT-RFI-SS-MK-01260.05 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Bended rungs | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-28 | 2022-06-02 | Construction | 2022-03-29 |  |  |  | V | EGAT-RFI-SS-MK-01260 |  |  | Construction
. | EGAT-RFI-SS-MK-01260.06 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Transport damages | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-28 | 2023-06-21 | Construction | 2022-03-29 |  |  |  | V | EGAT-RFI-SS-MK-01260 |  |  | Construction
. | EGAT-RFI-SS-MK-01260.07 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Lack of U-ditch drawings EGAT-810-SHT-CC-100-E0029 for gratings | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-03-28 | 2022-11-30 | Construction | 2022-03-29 | 'Discipline' changed SS -> AR (2022-06-10) evidence attached |  |  | V | EGAT-RFI-SS-MK-01260 |  |  | Construction
. | EGAT-RFI-SS-MK-01260.08 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Not assembled gratings due to collision with pipe | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-28 | 2023-01-25 | Construction | 2022-03-29 |  |  |  | V | EGAT-RFI-SS-MK-01260 |  |  | Construction
. | EGAT-RFI-SS-MK-01286.01 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Curved toe plate of the handrail (EGAT-RFI-SS-MK-01260.01) | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-04-19 | 2022-06-02 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-SS-MK-01286 |  |  | Construction
. | EGAT-RFI-SS-MK-01286.02 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | The gap between grating and toe board (EGAT-RFI-SS-MK-01260.02) | B | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-04-19 | 2022-12-29 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-SS-MK-01286 |  |  | Construction
. | EGAT-RFI-SS-MK-01286.03 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Curved handrailing (EGAT-RFI-SS-MK-01260.03) | B | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-04-19 | 2022-06-02 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-SS-MK-01286 |  |  | Construction
. | EGAT-RFI-SS-MK-01286.04 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Bended rungs (EGAT-RFI-SS-MK-01260.05) | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-04-19 | 2022-06-02 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-SS-MK-01286 |  |  | Construction
. | EGAT-RFI-SS-MK-01286.05 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Transport damages - coating (EGAT-RFI-SS-MK-01260.06) | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-04-19 | 2022-12-29 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-SS-MK-01286 |  |  | Construction
. | EGAT-RFI-SS-MK-01286.06 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | No support for the ladder (EGAT-RFI-SS-MK-01260.04) | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-19 | 2022-11-25 | Construction | 2022-04-20 | 'Discipline' changed SS -> AR (2022-06-10) evidence attached |  |  | V | EGAT-RFI-SS-MK-01286 |  |  | Construction
. | EGAT-RFI-SS-MK-01286.07 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Lack of u-ditch at drawings (EGAT-RFI-SS-MK-01260.07) | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-19 | 2022-11-30 | Construction | 2022-04-20 | 'Discipline' changed SS -> AR (2022-06-10) evidence attached |  |  | V | EGAT-RFI-SS-MK-01286 |  |  | Construction
. | EGAT-RFI-SS-MK-01286.08 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Not assembled gratings due to collision with pipe (EGAT-RFI-SS-MK-01260.08) | A | PI | HEC PI Construction | Mr. Slawomir Nasilowski | 2022-04-19 | 2022-06-14 | Construction | 2022-04-20 | 'Discipline' changed SS -> PI (2022-06-10) evidence attached |  |  | V | EGAT-RFI-SS-MK-01286 |  |  | Construction
. | EGAT-RFI-SS-MK-01286.09 | 800.00 | 1304-12-10 | AUX | 810-SHT-CC-100 | Coating damages due to other branches works | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-04-19 | 2023-06-21 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-SS-MK-01286 |  |  | Construction
. | 12404 | 810.10 | 810-10-42 | AUX Area / 810-SHT-CC-300 | EGAT-HEC-200-HSE-PID-00202 | Pit to be cleaned and dewatered | A | AR | HEC CV Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12406 | 810.10 | 810-10-42 | AUX Area / 810-SHT-CC-300 | EGAT-HEC-200-HSE-PID-00202 | Cover for pit to be provided | A | AR | HEC CV Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12420 | 810.10 | 810-10-42 | AUX Area / 810-SHT-CC-300 | Common | Grating to be provided for trench | A | CV | HEC CV Construction | Ms. Alicja Sulżyc | 2022-11-04 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20917 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Refer to Photo in Correspondence 04-PDHP-HEC-E-1318 | The door assembly should be finished. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-30 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20918 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Refer to Photo in Correspondence 04-PDHP-HEC-E-1318 | The walls damages from bolts should be repaired. | C | EL | HEC EL Construction | Mr. Andrzej Wójcikiewicz | 2022-12-30 | 2023-04-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20919 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Refer to Photo in Correspondence 04-PDHP-HEC-E-1318 | All useless holes in the wall should be repaired. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-30 | 2023-06-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20920 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Refer to Photo in Correspondence 04-PDHP-HEC-E-1318 | No sealant on connection floor/foundation and floor/U-ditch. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-30 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20921 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Wall Openings / Refer to Photo in Correspondence 04-PDHP-HEC-E-1318 | All technological passages should be finished. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-30 | 2023-05-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20922 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Refer to Photo in Correspondence 04-PDHP-HEC-E-1318 | No cover plates on manholes. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-30 | 2023-03-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20923 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Refer to Photo in Correspondence 04-PDHP-HEC-E-1318 | The doors should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-30 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20924 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Refer to Photo in Correspondence 04-PDHP-HEC-E-1318 | The downsput should be finished. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-30 | 2023-03-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20925 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Refer to Photo in Correspondence 04-PDHP-HEC-E-1318 | The canopy above doors should be finished. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-30 | 2023-06-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20926 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Refer to Photo in Correspondence 04-PDHP-HEC-E-1318 | The plinth should be finished. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-30 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20927 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Refer to Photo in Correspondence 04-PDHP-HEC-E-1318 | The facade near to ladder should be finished. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-30 | 2023-06-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20928 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Inspection | Lack of SAT inspection | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-30 | 2023-03-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20929 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Inspection | Lack of Final Inspection- HVAC/Plumbng | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-30 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20930 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Inspection | Lack of Final Inspection- Fire Protection | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-30 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20931 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | Ventilation system | Lack of power and earthing connection - Fans | C | EL | HEC EL Construction | Ms. Daria Pliszka | 2022-12-30 | 2023-03-22 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20932 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | Canopy lighting fixture are missing | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-03-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20933 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | Fire sealing for the cable tray entry on the wall to be provided and sticker to be attached | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-04-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20934 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | 810-PDP-001, 860-PDP-001 for spare hole blind plug to be provided | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-03-27 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20935 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | PDP, NLP and ELP panel earthing is loose to be tightned | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20936 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | For Busbar earthing bolts is missing to be provided and tightned. | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20937 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | Stub-up conduit duct sealing to be provided | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-02-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20938 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | Vertical CNBOP cable tray PVC ties to be change with SS cable ties. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-03-24 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20939 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | For Tag no-810-MP0005B/LCP/JB and Skid earthing and fire controller panel earthing is loose to be tightned | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 20940 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | Over head crane Isolator box tag is missing and cable tag is missing to be provided | C | ME | HEC ME Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20941 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | For Lighting fixtures PVC reducers to be change to Metal reducers | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-04-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20942 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | Cable tray support grouting to be provided | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-02-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20943 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | PDP,NLP,ELP panels outgoing feeders tag stickers to be provided. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-04-19 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20944 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | Unused conduit pipe sealing to be provided | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-02-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20945 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | Cable termination for Exhaust fans to be complete | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-02-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20946 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | Cable tray main earthing to be provided | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-02-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20947 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-05028,EGAT-HEC-900-ELE-DLP-04019,EGAT-HEC-900-ELE-DLP-01003 | Illumination test to be done. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-30 | 2023-03-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20948 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-06008 | Fire alarm SAT to be complete. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 | 2023-04-06 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20949 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-06008 | Manual call point dark glow CNBOP certified stickers to be provided | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 | 2023-02-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20950 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-ELE-DLP-06008 | Fire alarm Devices to be installed and official inspection to be carried out inFire pump sheleter. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 | 2023-03-24 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20951 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-INC-DLP-00112 | PAGA and Intercom System installation to be complete and official inspection to be carried out in Compressor shelter. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 | 2023-03-27 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20952 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-INC-DLP-00112 | PAGA and intercom SAT to be complete | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 20953 | 800.00 | 1304-12-11 | Fire Water Pump Building (810-SHT-CC-300) | EGAT-HEC-900-INC-DLP-00112 | PAGA and intercom SAT to be complete | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 30240 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | General | Ladder Flashing area Rubber mat platform prefered | C | AR | HEC CI Construction | Mr. Andrzej Misiek | 2023-02-24 |  | Construction | [8 empty] | RFC/RFSU
. | EGAT-RFI-AR-GS-01305.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Ground Slab Axis 1-2/A-F | To be attach Survey report | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-03-01 | 2021-11-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-01305 | C-AR-GS-00002 |  | Construction
. | EGAT-RFI-AR-GS-01525.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Ground Slab Axis A-F/1-2 | Scaling surface of concrete slab need corrective action | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-05-24 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-01525 | C-AR-GS-00040 |  | Construction
. | EGAT-RFI-AR-GS-04087.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | "EF4" 810-V0001 | DOP for anchor bolts | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-09-30 | 2021-10-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-04150.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Masonry Asis 1/C-F, 2/C-F (EL.106.250) | Works are completed. Brick wall should have equal surface with reinforcement concrete. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-10-08 | 2022-08-17 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-04215.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 2/A-C (E.L 106.250) | The same surface masonry wall and the columns and girders | D | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-10-20 | 2022-08-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-04215 |  |  | Construction
. | EGAT-RFI-AR-GS-04321.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | EF4 & Pedestal Axis 1-2/ F-H | Finishing for improve | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-10-27 | 2022-06-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-04321 |  |  | Construction
. | EGAT-RFI-AR-GS-04352.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Wall W2 Axis 1-2/A-C | Repair the top of the internal corner | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-10-22 | 2022-08-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-04352 |  |  | Construction
. | EGAT-RFI-AR-GS-04356.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | EF3 | Vertical chamfering is needed | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-10-22 | 2022-06-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-04356 |  |  | Construction
. | EGAT-RFI-AR-GS-04920.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis A/1-2 | The plaster connection is visible | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-12 | 2023-05-30 | Construction | 2022-01-13 |  |  |  | V | EGAT-RFI-AR-GS-04920 |  |  | Construction
. | EGAT-RFI-AR-GS-04923.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis F | Fill the joints with a mortar | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-12 | 2022-08-17 | Construction | 2022-01-13 |  |  |  | V | EGAT-RFI-AR-GS-04923 |  |  | Construction
. | EGAT-RFI-AR-GS-04923.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis F | Lay the wool over the blocks | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-12 | 2022-08-17 | Construction | 2022-01-13 |  |  |  | V | EGAT-RFI-AR-GS-04923 |  |  | Construction
. | EGAT-RFI-AR-GS-05057.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Parapet H/1-2 and 2/H-F | Adjust the damage holes to the real level of damages | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-07 | 2022-08-17 | Construction | 2022-02-07 |  |  |  | V | EGAT-RFI-AR-GS-05057 |  |  | Construction
. | EGAT-RFI-AR-GS-05059.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1/H-G; 1-2/H, 2/H-F | Lack of wool at the top of wall | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-04 | 2022-08-17 | Construction | 2022-02-08 |  |  |  | V | EGAT-RF-AR-GS-05059 |  |  | Construction
. | EGAT-RFI-AR-GS-05059.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1/H-G; 1-2/H, 2/H-F | Lack of a sealant at the top to cover the wool | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-04 | 2022-08-17 | Construction | 2022-02-08 |  |  |  | V | EGAT-RF-AR-GS-05059 |  |  | Construction
. | EGAT-RFI-AR-GS-05061.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis A-F/1-2 | Adjust the damage holes to the realistic level of damage | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-07 | 2022-08-17 | Construction | 2022-02-07 |  |  |  | V | EGAT-RFI-AR-GS-05061 |  |  | Construction
. | EGAT-RFI-AR-GS-05061.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis A-F/1-2 | Clean parapet from the concrete | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-07 | 2022-08-17 | Construction | 2022-02-07 |  |  |  | V | EGAT-RFI-AR-GS-05061 |  |  | Construction
. | EGAT-RFI-AR-GS-05103.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis A-F/1, F/1-2 | Upper joint to be filed with wool and sealant | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-14 | 2022-08-17 | Construction | 2022-02-15 |  |  |  | V | EGAT-RFI-AR-GS-05103 |  |  | Construction
. | EGAT-RFI-AR-GS-05104.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis A-H/1 | Upper joint to be filed with wool and sealant | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-11 | 2022-08-17 | Construction | 2022-02-15 |  |  |  | V | EGAT-RFI-AR-GS-05104 |  |  | Construction
. | EGAT-RFI-AR-GS-05106.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis F/1-2, F-A/2, A/1-2 | Adjust the drainage holes for the appropriate roof levels | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-24 | 2022-08-17 | Construction | 2022-02-15 |  |  |  | V | EGAT-RFI-AR-GS-05106 |  |  | Construction
. | EGAT-RFI-AR-GS-05172.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 2/A-F | Change the pipe at the hole for a downspout | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-03-03 | 2022-12-27 | Construction | 2022-03-04 |  |  |  | V | EGAT-RFI-AR-GS-05172 |  |  | Construction
. | EGAT-RFI-AR-GS-05172.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 2/A-F | A steal sill has to be order appopriate to the situation at site | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-03-03 | 2023-05-23 | Construction | 2022-03-04 |  |  |  | V | EGAT-RFI-AR-GS-05172 |  |  | Construction
. | EGAT-RFI-AR-GS-05205.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis A-F (west side) | Repair the columns near the ceiling (west fasade) | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-03-01 | 2022-08-17 | Construction | 2022-03-03 |  |  |  | V | EGAT-RFI-AR-GS-05205 |  |  | Construction
. | EGAT-RFI-AR-GS-05266.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | - | Detail for connection wall and roof | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-03-15 | 2023-05-23 | Construction | 2022-03-16 |  |  |  | V | EGAT-RFI-AR-GS-05266 |  |  | Construction
. | EGAT-RFI-AR-GS-05439.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Roof slab | Places for improve | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-05 | 2023-05-23 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-AR-GS-05439 |  |  | Construction
. | EGAT-RFI-AR-GS-05442.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/A-F | Some cracks and imperfections | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-06 | 2023-05-30 | Construction | 2022-04-07 |  |  |  | V | EGAT-RFI-AR-GS-05442 |  |  | Construction
. | EGAT-RFI-AR-GS-05502.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Facade Axis 2/A-H | Remove stains on the facade | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-12 |  | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-AR-GS-05502 |  |  | Construction
. | EGAT-RFI-AR-GS-05502.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Facade Axis 2/A-H | Lack of flashing on the parapet | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-12 | 2022-08-17 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-AR-GS-05502 |  |  | Construction
. | EGAT-RFI-AR-GS-05661.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1/A-F | Damaged area to be painted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-06 | 2023-05-30 | Construction | 2022-05-09 |  |  |  | V | EGAT-RFI-AR-GS-05661 |  |  | Construction
. | EGAT-RFI-AR-GS-05661.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1/A-F | Top surface of beam and bracket to be inspected when access is avaliable | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-06 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05661 |  |  | Construction
. | EGAT-RFI-AR-GS-05664.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 2/A-F | Wall near floor to be finished | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-09 | 2022-08-17 | Construction | 2022-05-11 |  |  |  | V | EGAT-RFI-AR-GS-05664 |  |  | Construction
. | EGAT-RFI-AR-GS-05664.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 2/A-F | Top surface of beam and bracket to be inspected when access is avaliable | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-09 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05664 |  |  | Construction
. | EGAT-RFI-AR-GS-05717.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1/A-F | Dirty places to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-24 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05717 |  |  | Construction
. | EGAT-RFI-AR-GS-05717.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1/A-F | Damages to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-24 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05717 |  |  | Construction
. | EGAT-RFI-AR-GS-05849.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/A-F | Flashing is dent | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05849 |  |  | Construction
. | EGAT-RFI-AR-GS-05849.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/A-F | Flashing touch the membrane | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-06 | 2022-09-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05849 |  |  | Construction
. | EGAT-RFI-AR-GS-05849.03 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/A-F | Flashing touvh the fasade | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-06 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05849 |  |  | Construction
. | EGAT-RFI-AR-GS-05849.04 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/A-F | Lack of step near the ladder | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-06 | 2023-02-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05849 |  |  | Construction
. | EGAT-RFI-AR-GS-05895.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/A | Wall to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-09 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05895 |  |  | Construction
. | EGAT-RFI-AR-GS-05895.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/A | There were no possibility to provide the inspection upper site of beam | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-09 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05895 |  |  | Construction
. | EGAT-RFI-AR-GS-05896.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/F-H | Flashing is dent | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05896 |  |  | Construction
. | EGAT-RFI-AR-GS-05896.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/F-H | Flashing touch membrane | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-06 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05896 |  |  | Construction
. | EGAT-RFI-AR-GS-05896.03 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/F-H | Flashing touch fasade | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-06 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05896 |  |  | Construction
. | EGAT-RFI-AR-GS-05896.04 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/F-H | Lack of step near the ladder | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-06 | 2023-02-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05896 |  |  | Construction
. | EGAT-RFI-AR-GS-05954.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Ramp 1-2/A | Edges to be repaired | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-09 | 2022-09-08 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05954 |  |  | Construction
. | EGAT-RFI-AR-GS-05954.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Ramp 1-2/A | Survey confirmation of slope | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-09 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-05954 |  |  | Construction
. | EGAT-RFI-AR-GS-06016.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/F-H | Pencil marks | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-21 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06016 |  |  | Construction
. | EGAT-RFI-AR-GS-06016.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/F-H | Places around the window to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-21 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06016 |  |  | Construction
. | EGAT-RFI-AR-GS-06017.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/F-H | Pencil marks | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-21 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06017 |  |  | Construction
. | EGAT-RFI-AR-GS-06095.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis A-C/1-2 | Sump PIT is too high | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-27 | 2022-08-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06095 |  |  | Construction
. | EGAT-RFI-AR-GS-06095.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis A-C/1-2 | Sump PIT inside to be painted | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-27 | 2022-09-08 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06095 |  |  | Construction
. | EGAT-RFI-AR-GS-06298.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis A/1-2 | Door to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-14 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06298 |  |  | Construction
. | EGAT-RFI-AR-GS-06298.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis A/1-2 | Damages of painting, rusty places | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-14 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06298 |  |  | Construction
. | EGAT-RFI-AR-GS-06298.03 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis A/1-2 | Hardware to be monted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-14 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06298 |  |  | Construction
. | EGAT-RFI-AR-GS-06327.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis F-G/1 | Scratch at the left side over the panic bar, inside | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-20 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-06327 |  |  | Construction
. | EGAT-RFI-AR-GS-06432.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis B-F/1-2 | Hot deep galvanizing is demaged. Method statement of repairing to be consulted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-08-09 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06432 |  |  | Construction
. | EGAT-RFI-AR-GS-06514.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/F | Top surface of beam and bracket to be inspected when access is avaliable | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-08-19 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06514 |  |  | Construction
. | EGAT-RFI-AR-GS-06514.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Axis 1-2/F | Dirty wall to be painted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-08-19 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06514 |  |  | Construction
. | EGAT-RFI-AR-GS-06779.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Walkway | Elevation of earthing manhole need to be verify | C | EL | HEC EL Construction | Mr. Andrzej Misiek | 2022-10-13 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-06779 |  |  | Construction
. | EGAT-RFI-AR-GS-06882.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Walkway | To be finish around pit | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-01 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06882 |  |  | Construction
. | EGAT-RFI-AR-GS-06882.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Walkway | Edge to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-01 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06882 |  |  | Construction
. | EGAT-RFI-AR-GS-06882.03 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Walkway | To be finished around pipe support | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-01 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06882 |  |  | Construction
. | EGAT-RFI-AR-GS-06947.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | - | Membrane to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-14 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06947 |  |  | Construction
. | EGAT-RFI-AR-GS-06947.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | - | Membrane to be rectify under roof ventilation fans | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-14 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06947 |  |  | Construction
. | EGAT-RFI-AR-GS-06947.03 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | - | Lamp pole bolts and base to be sealed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-14 | 2023-05-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06947 |  |  | Construction
. | EGAT-RFI-AR-GS-07804.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | - | Horizon rebar not long enough | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-14 | 2023-05-31 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-07804.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | - | Too much distance from wall to anchorage plate | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-14 | 2023-05-31 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-07804.03 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | - | West side- not possible to check | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-14 | 2023-05-31 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-07804.04 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | - | Official drawing to be attached | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-14 | 2023-05-31 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-07964.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | - | Scratches on windowsill, west-south side & east-south sside | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-08 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08157.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | - | Different paint color, struture to be rectify | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-27 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-CI-CW-00686.01 | 800.00 | 1202-10-16 | 810-SHT-CC-300 AUX | 820-JA-010 (is) | Surface preparation of concrete foundation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-01-20 | 2022-03-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-00687.01 | 800.00 | 1202-10-16 | 810-SHT-CC-300 AUX | 810-JA-105 | Grouting to be done | B | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-01-20 | 2022-03-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01388.01 | 810.10 | 810-10-28 | 810-SHT-CC-300 | LT/PT | Torquing to be done | B | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-03 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01390.01 | 810.10 | 810-10-28 | 810-SHT-CC-300 | LG/PG | Torquing to be done | B | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-03 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01205.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Duct Installation | To be cleaned louvers and VD | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-08 | 2023-01-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01206.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Unit heater | To be installed local panel | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-08 | 2022-12-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01206.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Unit heater | To be re-painted supports of UH | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-08 | 2023-01-23 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01207.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Roof | To be removed dust and paint of fan | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-08 | 2023-02-08 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01207.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Roof | To be connected electrical and earthing cables | C | EL | HEC EL Construction | Ms. Daria Pliszka | 2022-11-08 | 2023-03-28 | Construction |  | 'Discipline' changed HV -> EL (2022-11-25) evidence attached |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01208.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | Hvac equipment | To be provide certificate of validity of fire extiguishers | A | EM | HEC SE Design | Mr. Jerzy Wegner | 2022-11-07 | 2023-01-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01371.01 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | HVAC start up inspection | Sound level should be measurement - fan | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-11 | 2023-05-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01371 |  |  | Construction
. | EGAT-RFI-HV-JW-01371.02 | 800.00 | 1304-12-11 | 810-SHT-CC-300 | HVAC start up inspection | Difficult access to main switch of the heaters | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-11 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01371 |  |  | Construction
. | 18264 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-200) | Curb | The sealant should be replaced | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-15 | 2023-03-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18265 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-201) | Beam top side | Pin holes on SS. | C | EL | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-15 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18266 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-202) | Beam top side | The SS should be cleaned. | C | SS | HEC SS Construction | Mr. Andrzej Wójcikiewicz | 2022-12-15 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18267 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-203) | Ground slab | The epoxy coating should be replaced. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-15 | 2023-03-30 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 18268 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-204) | Cladding (internal) | The sandwichpanels should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-15 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18269 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-205) | Cladding openings | All technological passage should be finished. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-15 | 2023-02-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18270 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-205) | Cladding openings | All technological passage should be finished. | C | EL | HEC EL Construction | Mr. Andrzej Wójcikiewicz | 2022-12-15 | 2023-02-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18271 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-206) | Cladding openings | Useless hole in sandwichpanels should be closed. | B | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-15 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18272 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-207) | Canopy | No canopy above the door. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-15 | 2023-05-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18273 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-208) | Door Accessory | The door stop should be replaced. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-15 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18274 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-209) | External Cladding | The sandwichpanels should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-15 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18275 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-210) | Thermal Insulation (gab between cladding and slab) | No thermal insulation of foundation. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-15 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18276 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-211) | Ladder | The ladder should repaired. | C | SS | HEC SS Construction | Mr. Andrzej Wójcikiewicz | 2022-12-15 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18277 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-212) | General | Lack of SAT inspection | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-15 | 2023-03-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 18278 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-213) | General | Lack of Final Inspection- HVAC/Plumbng | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-15 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 18279 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-214) | General | Lack of Final Inspection- Fire Protection | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-15 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 18280 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-215) | Eyewash | Lack of Polish describtion | C | ME | HEC ME Construction | Ms. Daria Pliszka | 2022-12-15 | 2023-04-13 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 18281 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-216) | Eyewash | Lack of drainage pipe | C | EM | HEC SE Design | Ms. Daria Pliszka | 2022-12-15 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18282 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-217) | Eyewash | The Eyewash is not mounted stably | C | ME | HEC ME Construction | Ms. Daria Pliszka | 2022-12-15 | 2023-05-19 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 18283 | 800.00 | 1304-12-12 | Phosphate Injection & BFW Treatment Package (820-SHT-CC-218) | Ventilation system | Lack of inspection for Fan (status: Rejected) | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-15 | 2023-06-12 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 31787 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Eye washer medicaments | 1 bottle of eye washer missing | C | AR | HEC AR Construction | Mr. Jarosław Pykosz | 2023-05-07 |  | PAC | [8 empty] | RFC/RFSU
. | EGAT-RFI-AR-GS-01381.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | FDN F2-2ea & EF2 | To be attach Survey report | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-03-15 | 2021-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-01381 | C-AR-GS-00010 |  | Construction
. | EGAT-RFI-AR-GS-01508.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Pedestal Axis C/1-2 | To be attach Qulity Document for Anchor Bolt | A | AR | HEC QAQC CAS | Mr. Slawomir Nasilowski | 2021-05-24 | 2022-09-16 | Construction |  | 'Punch Category' changed C -> A (2022-08-01) evidence attached |  |  | V | EGAT-RFI-AR-GS-01508 | C-AR-GS-00046 |  | Construction
. | EGAT-RFI-AR-GS-05815.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Axis B-C/2 | The door scratches, dent | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-01 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-05815 |  |  | Construction
. | EGAT-RFI-AR-GS-05815.02 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Axis B-C/2 | Door to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-01 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-05815 |  |  | Construction
. | EGAT-RFI-AR-GS-05985.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Axis 2/B-C | Lack of chamfering | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-14 | 2022-08-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05985 |  |  | Construction
. | EGAT-RFI-AR-GS-06173.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Axis 1-2/A-C | Lack of base angle | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-08 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06173 |  |  | Construction
. | EGAT-RFI-AR-GS-06173.02 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Axis 1-2/A-C | Panel damages | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-08 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-06173 |  |  | Construction
. | EGAT-RFI-AR-GS-06173.03 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Axis 1-2/A-C | Panel dents under the fasteners | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-08 | 2023-06-06 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-06173 |  |  | Construction
. | EGAT-RFI-AR-GS-06173.04 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Axis 1-2/A-C | Three fasteners schould be used to fix the last panels | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-08 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06173 |  |  | Construction
. | EGAT-RFI-AR-GS-06200.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Axis 1-2/A-C | Surface to be grinded and finished | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-07 | 2022-08-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06200 |  |  | Construction
. | EGAT-RFI-AR-GS-06200.02 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Axis 1-2/A-C | Sealant to be done | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-07 | 2022-08-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06200 |  |  | Construction
. | EGAT-RFI-AR-GS-06200.03 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Axis 1-2/A-C | Chamfering of the sump pit to be done | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-07 | 2022-08-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06200 |  |  | Construction
. | EGAT-RFI-AR-GS-06200.04 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Axis 1-2/A-C | The dike wall to be repaired | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-07 | 2022-08-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06200 |  |  | Construction
. | EGAT-RFI-AR-GS-06200.05 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Axis 1-2/A-C | Surface to be cleaned | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-07 | 2022-08-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06200 |  |  | Construction
. | EGAT-RFI-AR-GS-06302.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | FND, PD, Sump PIT, Trench, Ramp, Dike wall, Ladder FND, GS | Ground slab to be repaired, grinded | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-22 | 2022-09-13 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06302 |  |  | Construction
. | EGAT-RFI-AR-GS-06431.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Ground floor | After removal of scaffolding touch ups to be done | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-08-10 | 2022-09-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06431 |  |  | Construction
. | EGAT-RFI-AR-GS-06980.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Flashing | Wall penetration to be closed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 | 2023-02-16 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06980 |  |  | Construction
. | EGAT-RFI-AR-GS-06980.02 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Flashing | Flashing to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-06980 |  |  | Construction
. | EGAT-RFI-AR-GS-06980.03 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Flashing | Top flashing color not correct | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-06980 |  |  | Construction
. | EGAT-RFI-AR-GS-07186.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Panel Installation | Bottom flashing to be installed inside windows | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-28 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07186 |  |  | Construction
. | EGAT-RFI-AR-GS-07617.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | - | Bottom flashing - rusted, damaged, wrong slope | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07617 |  |  | Construction
. | EGAT-RFI-AR-GS-07617.02 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | - | Bottom flashing to be done above ramp | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07617 |  |  | Construction
. | EGAT-RFI-AR-GS-07617.03 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | - | Flashing damaged | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07617 |  |  | Construction
. | EGAT-RFI-AR-GS-07617.04 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | - | No nuts on external ladder FND | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 | 2023-06-01 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07617 |  |  | Construction
. | EGAT-RFI-AR-GS-07617.05 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | - | Tape and tape leftovers to be removed from sandwich panels | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07617 |  |  | Construction
. | EGAT-RFI-AR-GS-07617.06 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | - | South side - steam from pipes making wall dirty | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07617 |  |  | Construction
. | EGAT-RFI-AR-GS-07617.07 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | - | Gutter slope around downspout to be corrected | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07617 |  |  | Construction
. | EGAT-RFI-AR-GS-07617.08 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | - | Trenches and sump pit to be clean | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07617 |  |  | Construction
. | EGAT-RFI-AR-GS-07617.09 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | - | Dike wall damaged; to be repaired around bolts | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07617 |  |  | Construction
. | EGAT-RFI-AR-GS-07617.10 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | - | EI to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07617 |  |  | Construction
. | EGAT-RFI-AR-GS-07648.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | - | Lack of flashing | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07648.02 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | - | Corrosion on bolts | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07648.03 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | - | The rods to be adjusted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-HV-JW-01199.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | Duct Installation | To be cleaned louvers and VD | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-08 | 2022-12-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01200.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | 820-SHT-CC-200 | To be installed a local panels | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-04 | 2022-12-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01200.02 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | 820-SHT-CC-200 | To be connected instruments cables | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-04 | 2022-12-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01370.01 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | HVAC start up inspection | Sound level should be measurement - fans | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-11 | 2023-05-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01370 |  |  | Construction
. | EGAT-RFI-HV-JW-01370.02 | 800.00 | 1304-12-12 | 820-SHT-CC-200 | HVAC start up inspection | Difficult access to main switch of the heaters | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-11 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01370 |  |  | Construction
. | 15493 | 800.00 | 1304-12-18 | General |  | Lack of Final Inspection - HVAC/Plumbing | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15494 | 800.00 | 1304-12-18 | General |  | Lack of Final Inspection - Fire protection | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15495 | 800.00 | 1304-12-18 | General |  | Lack of SAT Inspections | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-05-04 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15496 | 800.00 | 1304-12-18 | General |  | Lack of access to the Capacitor Room | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-05-09 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15497 | 800.00 | 1304-12-18 | Genaral | ED, PW installation | Insulation ED/water installation to be cleaned | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15498 | 800.00 | 1304-12-18 | General | Air condition installation | Instrument cable for Operation panel - all length of cable should be in the conduit | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15499 | 800.00 | 1304-12-18 | General | All installations | Lack of identification and flow direction marking in line with the procedure - installation and equipment | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-05-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15500 | 800.00 | 1304-12-18 | General | All installations | Lack of signature on the Fire passes stickers | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-06-06 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15501 | 800.00 | 1304-12-18 | UPS | Air condition installation | Operational panel to be tighten | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15502 | 800.00 | 1304-12-18 | MV Room/HVAC Room | Duct | Lack of fire passes between floors for the Motor Fire Damper | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-06-06 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15503 | 800.00 | 1304-12-18 | General | Air condition/Ventilation installation | Start filters - replace | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-05-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15504 | 800.00 | 1304-12-18 | Rack Room/HVAC Room | Ventilation installation | SAC scratched/knocked | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-05-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15505 | 800.00 | 1304-12-18 | Rack Room | ED installation | Supports should to be in line with the installation | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15506 | 800.00 | 1304-12-18 | Rack Room | Ventilation installation | SAC - tighten the screw | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15507 | 800.00 | 1304-12-18 | HVAC Room | Air condition installation | Control panel to be cleaned and Polish language descriptions | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-02-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15508 | 800.00 | 1304-12-18 | HVAC Room | RL/RG | Cover for cable tray damaged | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15509 | 800.00 | 1304-12-18 | HVAC Room | Ventilation installation | Elastic connection between SAC and ducts unstick | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15510 | 800.00 | 1304-12-18 | HVAC Room | Ventilation installation | Leaking from SAC - Leakage test should to be provided. SAC to be cleaned | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-02-14 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15511 | 800.00 | 1304-12-18 | HVAC Room | Ventilation installation | Screw inside the ducts should to be cut | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15512 | 800.00 | 1304-12-18 | General | Ventilation installation | Duct should to be clean inside | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15513 | 800.00 | 1304-12-18 | HVAC Room | PW installation | Damaged,dirty insulation, contamination valve - incomplete | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15514 | 800.00 | 1304-12-18 | HVAC Room/ Battery Room | Instrument Cable | Lack of fire passes | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-06-06 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15515 | 800.00 | 1304-12-18 | HVAC Room | Ventilation installation | Missing cover SAC - whole for cables | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15516 | 800.00 | 1304-12-18 | Roof | Ventilation installation | ACCU-0002A and B should be cleaning and remove the corrosion | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-02-14 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15517 | 800.00 | 1304-12-18 | Roof | Ventilation installation | ACCU-0002A and B - lack of earthing | A | EL | HEC EL Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15518 | 800.00 | 1304-12-18 | General | ED - outside part | ED should be finished above the U-ditch, clean up and coplete it | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15519 | 800.00 | 1304-12-18 | General | Ventilation installation | Louver (outside) - dirty and paint came off | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15520 | 800.00 | 1304-12-18 | Roof | PW installation | Heating cable - not finished | C | EL | HEC EL Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-05-08 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15521 | 800.00 | 1304-12-18 | Cable Room | ED installation | Insulation should to be finished and clean | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15522 | 800.00 | 1304-12-18 | Battery Room | Ventilation installation | Fixing the Fans - not in line with the requirements | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15523 | 800.00 | 1304-12-18 | General | Instrument Cable | Refill the tags on the instrument cables | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-04-19 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15524 | 800.00 | 1304-12-18 | Roof | RL/RG | Cover for cable tray not fixed | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-03-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15525 | 800.00 | 1304-12-18 | Roof | PW installation | Jacketing damaged | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-04-19 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15526 | 800.00 | 1304-12-18 | Roof | Ventilation installation | All AHU mounting brackets are rusted | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15527 | 800.00 | 1304-12-18 | Roof | Ventilation installation | AHUs and ACCUs are rusted inside and outside | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15528 | 800.00 | 1304-12-18 | Roof | Ventilation installation | AHU control panel - rusted | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15529 | 800.00 | 1304-12-18 | Roof | Ventilation installation | Rusted fan - AHU, ACCU | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15530 | 800.00 | 1304-12-18 | Roof | Ventilation installation | Water inside AHUs | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-06-16 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15531 | 800.00 | 1304-12-18 | Roof | Ventilation installation | Water does not flow from the jacketing | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-05-09 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15532 | 800.00 | 1304-12-18 | Roof | Ventilation installation | Silicone should to be done on jacketing | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-03-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15533 | 800.00 | 1304-12-18 | Roof | Ventilation installation | Corrosion on the exhaust duct, handles od AD and screw | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-03-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15534 | 800.00 | 1304-12-18 | Roof | Ventilation installation | Lack of stickers on volume dmper | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15535 | 800.00 | 1304-12-18 | Roof | Ventilation installation | Lack of access to the AHUs | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15536 | 800.00 | 1304-12-18 | Ground and 1st floor | All installations | Wall between axis 4 and C-E is the fire wall at a length of 4m - Fire passes should be performed | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-28 | 2023-05-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15537 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 07 | Walls should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15538 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 07 | Remove dowels from fire extinguisher tag. | B | HV | HEC HV Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15539 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 07 | On the eastern wall, a floor strip should be fixed | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15540 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 07 | The mineral wool on 4th beam is damaged. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15541 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 07 | Damages on the floor | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15542 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 9a | The floor should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15543 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 9a | Damages on the wall. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15544 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 8 | The floor and the walls should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15545 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 8 | The external door is damaged. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15546 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 9 | The floor and walls should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15547 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 9 | Rubber fillings on the steps should be improved | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15548 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 9 | Carpet on the steps should be improved | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15549 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 9 | A moldy wall at the entrance on the left. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15550 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 9 | The door should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15551 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 11 | No panels on the suspended ceiling | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 | 2023-03-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15552 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 11 | Replaced suspended ceiling. Many damaged aluminum profiles | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15553 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 11 | Walls should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15554 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 11 | The holes after air conditioners should be filled. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15555 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 11 | The door should be cleaned.(west side) | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15556 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 11 | Floor strip should be fixed near to 7/C axis | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15557 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 11 | The floor panel is damaged ( axis B/10) | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15558 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 13 | The floor should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15559 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 13 | The walls should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15560 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 13 | Remove dowels from fire extinguisher tag. | B | HV | HEC HV Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15561 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 13 | The floor should be filled. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15562 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 12 | The walls should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15563 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 12 | Floor earthing is not connected. | C | EL | HEC EL Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 | 2023-03-30 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15564 | 800.00 | 1304-12-18 | 1000-SS-02 | Room 12 | The door is damaged. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15565 | 800.00 | 1304-12-18 | 1000-SS-02 | Cable room | The floor should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 | 2023-03-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15566 | 800.00 | 1304-12-18 | 1000-SS-02 | Cable room | Pit 3 filled with water. | C | EL | HEC EL Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 15567 | 800.00 | 1304-12-18 | 1000-SS-02 | Cable room | No wool on ceiling at axis 10/11 | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15568 | 800.00 | 1304-12-18 | 1000-SS-02 | Cable room | The door is damaged ( north side) | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-11-28 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 21003 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Emergency LTG J/B Unused spare holes Blind Plug to be installed | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-27 | Walkdown | LV Room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21004 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Lighting J/B and Fixtures Cable tag to be installed in all LV, MV, Cable Cellar,UPS , Capacitor room, Rack room, HVAC room and Roof top. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-06 | Walkdown | General |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21005 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Cable tray Main Earthing to be done for LV, MV, Cable Cellar,UPS , Capacitor room, Rack room, HVAC room and Roof top. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-23 | Walkdown | General |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21006 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Floor Static earthing to be connect with main earthing cable in all rooms. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-01-09 | Walkdown | General |  |  |  | V |  |  |  | RFC/RFSU
. | 21007 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Lighting Fixture connect to CBS circuit and Exit light cable tag to be provided with another colour. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-11 | Walkdown | General |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21008 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Lighting panels and PDP panel cables to be covered with metal cover. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-07 | Walkdown | LV,UPSroom |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21009 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Cable end with PVC tape and placed in cable tray below 02-PDP-003 to be verified (Tag no:-1000-SS02-ACCU-0004C) | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-28 | Walkdown | LV room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21010 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Fire Sealing for the verical cable tray & conduit to be provided from Cable cellar to LV room and MV room to Battery room | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-27 | Walkdown | MV/LV room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21011 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Fire alarm cable on vertical cable ladder need to use metal clamp instead of PVC tie. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-06-07 | Walkdown | General |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21012 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | 02-JB-001 spare hole blind plug to be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-27 | Walkdown | LV room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21013 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | In LV room Conduit clamp to be properly fixing for the socket outlet box. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-05 | Walkdown | LV room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21014 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | For all Emergency Lighting panel descritpion to be change to Emergency Stand-By Lighting panel. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-13 | Walkdown | UPS room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21015 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | In UPS room Aircon pipe to be removed and fire sealing to be repair. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-27 | Walkdown | UPS room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21016 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | 02-BMS-1-3,1-2 under panel Checkered plate to be install properly. | C | AR | HEC AR Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-05-12 | Walkdown | UPS room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21017 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | SS-IRP-551 front & Rear door, SS-IRP-552- Rear door lock mechanisum is problem to be repaired | C | CI | HEC CI Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-05-04 | Walkdown | LV room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21018 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | General cleaning for socket outlet , J/B, Lighting fixtures. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-27 | Walkdown | General |  |  |  | V |  |  |  | RFC/RFSU
. | 21019 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | For all MAC CNBOP certificed signages to be installed | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-24 | Walkdown | General |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21020 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | All MAC point illumination test to be done with Escape light and Excit light. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 |  | Walkdown | General |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21021 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | On wall Frame overall Single line drawing to be changed with Latest revision. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-30 | Walkdown | MV & LV room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21022 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | UPS Screw covers (White) to be install | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-19 | Walkdown | UPS room |  |  |  | V |  |  |  | RFC/RFSU
. | 21023 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | 1000-MAC-6801 top side hole opening to be close in UPS room | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-27 | Walkdown | UPS room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21024 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Inside UPS room & Battery room of F&G Beacon earthing cable not connected | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-01-09 | Walkdown | UPS / Battery room |  |  |  | V |  |  |  | RFC/RFSU
. | 21025 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | In Battery room unwanted earthing cable to be removed. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-27 | Walkdown | Battery room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21026 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | In battery room all earthing cables to be connect to Earthing Bus-bar, 12-BCB-001 stantion earthing to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-22 | Walkdown | Battery room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21027 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | In battery room beside vertical cable tray checkered plate to be provided. | C | AR | HEC AR Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-05-12 | Walkdown | Battery room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21028 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | In battery room cable ladder & tray, perforated tray main earthing to be connected | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-22 | Walkdown | Battery room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21029 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | HVAC duct earthing bonding and main earth connection to be done. | C | HV | HEC HV Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-06-14 | Walkdown | General |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21030 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Lightning tape 4-Way copper clamp for lightning tape beside battery room missing bolts to be provided. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-03 | Walkdown | Beside Battery room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21031 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | In RIB-12 battery room 2 batteries some corroded to be check by vendor and verified | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21032 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Inside capacitor panel TH2-1 terminal block earthing cable is missing to be clarify. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-05-18 | Walkdown | Inside Capacitor panel |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21033 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Capacitor panel to be cleaning | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-28 | Walkdown | Cpacitor room |  |  |  | V |  |  |  | RFC/RFSU
. | 21034 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | In cable cellar room copper tape on wall is missing from cable pit to entrance door at north side. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-22 | Walkdown | Cable cellar room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21035 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | In cable cellar room some cables coiled and kept on the floor to be dressed in cable tray and to be terminated. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-19 | Walkdown | Cable cellar room |  |  |  | V |  |  |  | RFC/RFSU
. | 21036 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | LTG switch & Socket outlet conduits earthing to be provide (If continuity available) no need earthing. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-23 | Walkdown | Cable cellar room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21037 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | General cleaning of cables in Cable trays and ladders. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-06 | Walkdown | Cable cellar room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21038 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | In cable ladder and tray the cable should be properly dressed with cable ties | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-07 | Walkdown | Cable cellar room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21039 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Cable cellar room door earthing to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-21 | Walkdown | Cable cellar room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21040 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | In rack room for CNBOP vertical tray cable clamp to be provided. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-11 | Walkdown | Rack room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21041 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | 1000-SS02-AHU-0001A/1B earthing cable rusted washers to be change. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-07 | Walkdown | Roof top |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21042 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Cable tray support to be fix properly near 02-NLP-0001/24/01/JB03. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-06 | Walkdown | Roof top |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21043 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | On the roof Ltg JB & Socket outlet glands to be tightned. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-20 | Walkdown | Roof top |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21044 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | 02-EHPK-001 heat tracting cable connections to be complete and inspected. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-04-17 | Walkdown | Roof top |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21045 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Baside Battery room Ladder earhing to be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-27 | Walkdown | Battery room out side |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21046 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-05002, 04002 & 00002 | Roof top on top of the Lightning pole arrester to be tightned. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-12-30 | 2023-03-20 | Walkdown | Roof top |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21047 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-06002 | Fire alarm SAT punches to be closed | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 | 2023-04-06 | Walkdown | General |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21048 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-900-INC-DLP-00211 | Telecommunication Sat to be performed | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 |  | Walkdown | General |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21049 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-900-INC-DLP-00211 | LAN Data outlet box to be replace with new one due to wrong screw used for outlet box thread damaged | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 | 2023-06-13 | Walkdown | General |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21050 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-06002 | Firealarm cable going to raise floor to be protected with some conduit / cable tray. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 | 2023-04-06 | Walkdown | UPS room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21051 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-900-INC-DLP-00311 | In battery room for speaker support grommet to be places for protection of cable from sharp edge. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 | 2023-03-30 | Walkdown | Battery room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21052 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-1000-ELE-DLP-06002 | Fire alarm cable tags to be provided in the cable tray rack beside 1000-SS02-SAC-0001C | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 | 2023-06-13 | Walkdown | Rack room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21053 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-900-INC-DLP-00311 | 12-SP-009 Paga speaker cover to be close properly | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 | 2023-04-05 | Walkdown | Rack room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21054 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-900-INC-DLP-00211 | LAN data outlet box and wall in between small crack to be plastered. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 | 2023-05-12 | Walkdown | Rack room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21055 | 800.00 | 1304-12-18 | Utility Station & RIB (1000-SS-02) | EGAT-HEC-900-INC-DLP-00211 | Dog house Smoke detector in HVAC room is missing | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-30 | 2023-05-09 | Walkdown | HVAC room |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 30239 | 800.00 | 1304-12-18 | 1000-SS-02 | General | Ladder Flashing area Rubber mat, platform prefered | C | AR | HEC CI Construction | Mr. Andrzej Misiek | 2023-02-24 |  | Construction | [8 empty] | RFC/RFSU
. | 31578 | 800.00 | 1304-12-18 | General | General | Lack of taggings. Refer to attachment. | C | EL | HEC EL Construction | GAP | 2023-05-04 | 2023-06-13 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | EGAT-PMC-000-QAC-NCR-EL102.01 | 800.00 | 1304-12-18 | 1000-SS-02 |  | Water should be removed and PIT will sohould be cleaned | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-05-19 | [10 empty] | Construction
. | EGAT-PMC-000-QAC-NCR-EL102.02 | 800.00 | 1304-12-18 | 1000-SS-02 |  | Proper solution for prevention from water flowing cable wells | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-05-19 | [10 empty] | Construction
. | EGAT-RFI-AR-GS-01502.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Ground Floor Axis 1-18/G,17-18/D-J | Upper joint to be filled with fire resistant sealant | C | AR | HEC AR Construction | Mr. Piotr Karkowski | 2021-05-21 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-01502 | C-AR-GS-00036 |  | Construction
. | EGAT-RFI-AR-GS-01927.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 12 | Top joint to be filled with five top sealant | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-06-08 | 2021-12-03 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-01927 | C-AR-GS-00041 |  | Construction
. | EGAT-RFI-AR-GS-02119.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 12, 13 | Upper joint to be filled with fire resistant sealant | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-07-12 | 2021-12-03 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-02119 | C-AR-GS-00050 |  | Construction
. | EGAT-RFI-AR-GS-02121.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 1 | Upper joint to be filled with fire resistant sealant | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-07-12 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-02121 | C-AR-GS-00048 |  | Construction
. | EGAT-RFI-AR-GS-02446.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 9 | Upper joint to be filled with fire resistant sealant. | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-07-12 | 2021-12-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-02446 | C-AR-GS-00047 |  | Construction
. | EGAT-RFI-AR-GS-02455.01 | 800.00 | 1304-12-18 | 1000-SS-02 | 2nd Floor Axis 5-11/A-C | Inspection for epoxy painting for the 2nd floor slab was not approved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-06-21 | 2022-05-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-02455 |  |  | Construction
. | EGAT-RFI-AR-GS-02557.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No, 2, 3, 4, 5 | Upper joint to be filled with fire resistant sealant. | B | AR | HEC AR Construction | Mr. Piotr Karkowski | 2021-07-20 | 2022-06-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-02557 | C-AR-GS-00063 |  | Construction
. | EGAT-RFI-AR-GS-03741.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Ground Slab & EP Axis 6-8A/C-E | Joint to be finished | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-09-03 | 2022-06-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-03741 | C-AR-GS-00082 |  | Construction
. | EGAT-RFI-AR-GS-03742.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Ground Slab & EP1 Axis 8A-11/C-E | Joint to be finished | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-09-03 | 2022-06-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-03742 | C-AR-GS-00083 |  | Construction
. | EGAT-RFI-AR-GS-03819.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Roof Axis 1-11/A-C | Wrong water drainage. Wrong slope near the drain hole. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-10-21 | 2022-07-13 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-03819 |  |  | Construction
. | EGAT-RFI-AR-GS-03819.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Roof Axis 1-11/A-C | Wrong slope near the drain hole. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-10-21 | 2022-07-13 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-03819 |  |  | Construction
. | EGAT-RFI-AR-GS-04061.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 1 | Plaster around the openings | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-09-27 | 2022-07-22 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-04061 | C-AR-GS-00116 |  | Construction
. | EGAT-RFI-AR-GS-04066.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 8, 9 | In some points fix surface of mineral wool board where connection with balcony | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-10-06 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-04073.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 2, 3, 4, 5 | Plaster around the openings | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-09-27 | 2022-06-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-04073 | C-AR-GS-00117 |  | Construction
. | EGAT-RFI-AR-GS-04178.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 11 | Correction of the Surface | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-10-08 | 2022-06-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-04363.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 13 | The openings for instalation should be closed by fireproof materials | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-10-22 | 2022-08-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-004363 |  |  | Construction
. | EGAT-RFI-AR-GS-04452.01 | 800.00 | 1304-12-18 | 1000-SS-02 | 2nd floor slab Axis 1-4/A-C | Contractor should do leveling of the surface | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-08 | 2022-08-05 | Construction | 2021-11-09 |  |  |  | V | EGAT-RFI-AR-GS-04452 | C-AR-GS-00119 |  | Construction
. | EGAT-RFI-AR-GS-04480.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 7 | The net around the opening | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-26 | 2022-07-13 | Construction | 2021-11-26 |  |  |  | V | EGAT-RFI-AR-GS-04480 |  |  | Construction
. | EGAT-RFI-AR-GS-04480.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 7 | Remove the 10 cm of electrical wire cover | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-26 |  | Construction | 2021-11-26 |  |  |  | V | EGAT-RFI-AR-GS-04480 |  |  | Construction
. | EGAT-RFI-AR-GS-04490.01 | 800.00 | 1304-12-18 | 1000-SS-02 | ELEC Cable trench axis 2-4/D-E | Make flat the vertical surface of the trench | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-10 | 2022-08-05 | Construction | 2021-11-10 |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-04491.01 | 800.00 | 1304-12-18 | 1000-SS-02 | TIE GIRDER Axis 1/A-E , 4-6/C | Top level of girder to be adjust with concrete slab. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-04 | 2022-07-13 | Construction | 2021-11-25 |  |  |  | V | EGAT-RFI-AR-GS-04491 |  |  | Construction
. | EGAT-RFI-AR-GS-04612.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 7, 8 | Damaged plaster to be repaired and repaint | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-25 | 2022-08-12 | Construction | 2021-11-25 |  |  |  | V | EGAT-RFI-AR-GS-04612 |  |  | Construction
. | EGAT-RFI-AR-GS-04612.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Plastering | Material used for repairs has different surface than plaster | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-25 | 2022-06-24 | Construction | 2021-11-25 |  |  |  | V | EGAT-RFI-AR-GS-04612 |  |  | Construction
. | EGAT-RFI-AR-GS-04613.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Plastering | Surface of plaster at the axis 4 to be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-25 | 2022-06-24 | Construction | 2021-11-25 |  |  |  | V | EGAT-RFI-AR-GS-04613 |  |  | Construction
. | EGAT-RFI-AR-GS-04613.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Plastering | Surface of all concrete columns to be improve | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-25 | 2022-06-24 | Construction | 2021-11-25 |  |  |  | V | EGAT-RFI-AR-GS-04613 |  |  | Construction
. | EGAT-RFI-AR-GS-04615.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 11, 13 | Damages plaster to be repaired and repaint. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-25 | 2022-07-22 | Construction | 2021-11-25 |  |  |  | V | EGAT-RFI-AR-GS-04615 |  |  | Construction
. | EGAT-RFI-AR-GS-04615.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 11, 13 | Material used for repairs has different surface than plaster. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-25 | 2022-06-24 | Construction | 2021-11-25 |  |  |  | V | EGAT-RFI-AR-GS-04615 |  |  | Construction
. | EGAT-RFI-AR-GS-04615.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 11, 13 | Surface of concrete columns to be improve. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-25 | 2022-06-24 | Construction | 2021-11-25 |  |  |  | V | EGAT-RFI-AR-GS-04615 |  |  | Construction
. | EGAT-RFI-AR-GS-04615.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 11, 13 | Traces of rainwater on the wall | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-25 | 2022-06-24 | Construction | 2021-11-25 |  |  |  | V | EGAT-RFI-AR-GS-04615 |  |  | Construction
. | EGAT-RFI-AR-GS-04617.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 7, 9A | The surface of plastered walls weren't check before painting | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-24 | 2022-08-05 | Construction | 2021-11-26 |  |  |  | V | EGAT-RFI-AR-GS-04617 |  |  | Construction
. | EGAT-RFI-AR-GS-04617.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 7, 9A | Damaged plaster to be repaired and repaint of full surface of wall | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-24 | 2022-08-05 | Construction | 2021-11-26 |  |  |  | V | EGAT-RFI-AR-GS-04617 |  |  | Construction
. | EGAT-RFI-AR-GS-04617.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 7, 9A | Steel corner around the door opening to be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-24 | 2022-06-24 | Construction | 2021-11-26 |  |  |  | V | EGAT-RFI-AR-GS-04617 |  |  | Construction
. | EGAT-RFI-AR-GS-04617.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 7, 9A | Surface of the vertical joint should be improve | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-24 | 2022-06-24 | Construction | 2021-11-26 |  |  |  | V | EGAT-RFI-AR-GS-04617 |  |  | Construction
. | EGAT-RFI-AR-GS-04729.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Ground floor wall | It is necessary to provide the winter condition for finishing works. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-12-06 | 2022-07-13 | Construction | 2021-12-07 |  |  |  | V | EGAT-RFI-AR-GS-04729 |  |  | Construction
. | EGAT-RFI-AR-GS-04729.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Ground floor wall | Prepare nurface for painting | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-12-06 | 2022-07-22 | Construction | 2021-12-07 |  |  |  | V | EGAT-RFI-AR-GS-04729 |  |  | Construction
. | EGAT-RFI-AR-GS-04731.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Ground floor wall | Prepare surface for painting | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-12-06 | 2022-07-22 | Construction | 2021-12-07 |  |  |  | V | EGAT-RFI-AR-GS-04731 |  |  | Construction
. | EGAT-RFI-AR-GS-04731.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Ground floor wall | It is necessary to provide the winter condition for finishing works. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-12-06 | 2022-07-13 | Construction | 2021-12-07 |  |  |  | V | EGAT-RFI-AR-GS-04731 |  |  | Construction
. | EGAT-RFI-AR-GS-04735.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 8 | Moisture | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-12-06 | 2022-08-05 | Construction | 2021-12-07 |  |  |  | V | EGAT-RFI-AR-GS-04735 |  |  | Construction
. | EGAT-RFI-AR-GS-04791.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Roof | Improve the slope for a damage | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-12-10 | 2022-02-11 | Construction | 2021-12-14 |  |  |  | V | EGAT-RFI-AR-GS-04791 |  |  | Construction
. | EGAT-RFI-AR-GS-04791.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Roof | Cover the bolts by bitumen witch are fasted to the light concrete. | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-12-10 | 2022-03-28 | Construction | 2021-12-14 |  |  |  | V | EGAT-RFI-AR-GS-04791 |  |  | Construction
. | EGAT-RFI-AR-GS-04971.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Wall W3 Axis A-B/4-7 | The wall is dirty should be painted again - both side | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-25 | 2022-08-05 | Construction | 2022-01-27 | category changed A-> C (2022-03-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-04971 |  |  | Construction
. | EGAT-RFI-AR-GS-04971.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Wall W3 Axis A-B/4-7 | Door frame for cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-25 | 2022-08-05 | Construction | 2022-01-27 | category changed A-> C (2022-03-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-04971 |  |  | Construction
. | EGAT-RFI-AR-GS-04971.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Wall W3 Axis A-B/4-7 | The openings in the wall should be closed | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-25 | 2022-04-29 | Construction | 2022-01-27 |  |  |  | V | EGAT-RFI-AR-GS-04971 |  |  | Construction
. | EGAT-RFI-AR-GS-04971.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Wall W3 Axis A-B/4-7 | The holes in the wall are for close | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-25 | 2022-04-29 | Construction | 2022-01-27 |  |  |  | V | EGAT-RFI-AR-GS-04971 |  |  | Construction
. | EGAT-RFI-AR-GS-04971.05 | 800.00 | 1304-12-18 | 1000-SS-02 | Wall W3 Axis A-B/4-7 | Visible joints on the wall | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-25 | 2022-08-05 | Construction | 2022-01-27 | category changed A-> B (2022-03-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-04971 |  |  | Construction
. | EGAT-RFI-AR-GS-04971.06 | 800.00 | 1304-12-18 | 1000-SS-02 | Wall W3 Axis A-B/4-7 | Skirting board dirty with paint | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-25 | 2022-06-24 | Construction | 2022-01-27 | category changed A-> C (2022-03-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-04971 |  |  | Construction
. | EGAT-RFI-AR-GS-04972.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Painting 2nd floor - Axis A-C/1, A/1-4, C/1-4 | The surface should be prepaired for painting | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-19 | 2022-04-29 | Construction | 2022-01-20 |  |  |  | V | EGAT-RFI-AR-GS-04972 |  |  | Construction
. | EGAT-RFI-AR-GS-04972.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Painting 2nd floor - Axis A-C/1, A/1-4, C/1-4 | Visible strips around the room should be grinded | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-19 | 2022-04-28 | Construction | 2022-01-20 | category changed A-> B (2022-03-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-04972 |  |  | Construction
. | EGAT-RFI-AR-GS-04972.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Painting 2nd floor - Axis A-C/1, A/1-4, C/1-4 | Plaster surface should be flat and smooth | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-19 | 2022-04-28 | Construction | 2022-01-20 |  |  |  | V | EGAT-RFI-AR-GS-04972 |  |  | Construction
. | EGAT-RFI-AR-GS-04972.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Painting 2nd floor - Axis A-C/1, A/1-4, C/1-4 | The south plastered wall should be repaired in a few places | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-19 | 2022-04-28 | Construction | 2022-01-20 |  |  |  | V | EGAT-RFI-AR-GS-04972 |  |  | Construction
. | EGAT-RFI-AR-GS-04972.05 | 800.00 | 1304-12-18 | 1000-SS-02 | Painting 2nd floor - Axis A-C/1, A/1-4, C/1-4 | Surface around the door should be prepaired again | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-19 | 2022-04-28 | Construction | 2022-01-20 |  |  |  | V | EGAT-RFI-AR-GS-04972 |  |  | Construction
. | EGAT-RFI-AR-GS-04973.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Painting 2nd floor - Wall 4 | Sealant to be apply in the courners of walls and between walls and suspended ceiling | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-19 | 2022-03-24 | Construction | 2022-01-20 |  |  |  | V | EGAT-RFI-AR-GS-04973 |  |  | Construction
. | EGAT-RFI-AR-GS-04973.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Painting 2nd floor - Wall 4 | Dirty walls | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-19 | 2022-03-24 | Construction | 2022-01-20 |  |  |  | V | EGAT-RFI-AR-GS-04973 |  |  | Construction
. | EGAT-RFI-AR-GS-05086.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis A-C/1, A/1-4, C/1-4 | An even repairs of plater | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-15 | 2022-04-28 | Construction | 2022-02-16 | category changed A-> B (2022-03-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-05086 |  |  | Construction
. | EGAT-RFI-AR-GS-05086.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis A-C/1, A/1-4, C/1-4 | Some inperfection around the cable holes | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-15 | 2022-04-28 | Construction | 2022-02-16 | category changed A-> B (2022-03-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-05086 |  |  | Construction
. | EGAT-RFI-AR-GS-05087.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Battery Room No. 12 | Some holes on the ceiling | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-15 | 2022-04-26 | Construction | 2022-02-16 | category changed A-> B (2022-03-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-05087 |  |  | Construction
. | EGAT-RFI-AR-GS-05087.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Battery Room No. 12 | Some dirty places | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-15 | 2022-06-24 | Construction | 2022-02-16 | category changed A-> C (2022-03-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-05087 |  |  | Construction
. | EGAT-RFI-AR-GS-05087.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Battery Room No. 12 | Repair and paint around the hangars | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-15 | 2022-04-26 | Construction | 2022-02-16 |  |  |  | V | EGAT-RFI-AR-GS-05087 |  |  | Construction
. | EGAT-RFI-AR-GS-05088.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis C/1-4 | The cable passage have to be close by fire proof material | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-11 | 2022-04-29 | Construction | 2022-02-15 |  |  |  | V | EGAT-RFI-AR-GS-05088 |  |  | Construction
. | EGAT-RFI-AR-GS-05088.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis C/1-4 | Dirty wall will be repaint | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-11 |  | Construction | 2022-02-15 | category changed A-> C (2022-03-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-05088 |  |  | Construction
. | EGAT-RFI-AR-GS-05088.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis C/1-4 | Holes will be repaired | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-11 | 2022-04-29 | Construction | 2022-02-15 | category changed A-> B (2022-03-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-05088 |  |  | Construction
. | EGAT-RFI-AR-GS-05088.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis C/1-4 | Crack on the wall | A | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-29 | 2022-06-24 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05088 |  |  | Construction
. | EGAT-RFI-AR-GS-05151.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 9A | A lot of holes after installator works have to be repaired | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-02-25 |  | Construction | 2022-02-28 |  |  |  | V | EGAT-RFI-AR-GS-05151 |  |  | Construction
. | EGAT-RFI-AR-GS-05182.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 4-5/A-C | Lack of skirting | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-28 | 2022-07-22 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05182 |  |  | Construction
. | EGAT-RFI-AR-GS-05182.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 4-5/A-C | Wet stain on the floor | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-28 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-05182 |  |  | Construction
. | EGAT-RFI-AR-GS-05183.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis A/4-5, C/4-5 | Clean the door and frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-28 |  | Construction | 2022-03-01 |  |  |  |  | EGAT-RFI-AR-GS-05183 |  |  | Construction
. | EGAT-RFI-AR-GS-05183.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis A/4-5, C/4-5 | Make one surface around the door | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-28 | 2022-07-13 | Construction | 2022-03-01 |  |  |  | V | EGAT-RFI-AR-GS-05183 |  |  | Construction
. | EGAT-RFI-AR-GS-05183.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis A/4-5, C/4-5 | Make sealant along gypsum wall both side | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-28 | 2022-06-24 | Construction | 2022-03-01 |  |  |  | V | EGAT-RFI-AR-GS-05183 |  |  | Construction
. | EGAT-RFI-AR-GS-05183.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis A/4-5, C/4-5 | Clarity the openings near the floor | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-28 |  | Construction | 2022-03-01 |  |  |  |  | EGAT-RFI-AR-GS-05183 |  |  | Construction
. | EGAT-RFI-AR-GS-05183.05 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis A/4-5, C/4-5 | Clean the cables | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-28 | 2022-08-05 | Construction | 2022-03-01 |  |  |  | V | EGAT-RFI-AR-GS-05183 |  |  | Construction
. | EGAT-RFI-AR-GS-05184.01 | 800.00 | 1304-12-18 | 1000-SS-02 | HVAC Room No. 13 | Make some touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-28 | 2022-06-24 | Construction | 2022-03-01 |  |  |  | V | EGAT-RFI-AR-GS-05184 |  |  | Construction
. | EGAT-RFI-AR-GS-05184.02 | 800.00 | 1304-12-18 | 1000-SS-02 | HVAC Room No. 13 | Close some holes | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-28 | 2022-06-24 | Construction | 2022-03-01 |  |  |  | V | EGAT-RFI-AR-GS-05184 |  |  | Construction
. | EGAT-RFI-AR-GS-05184.03 | 800.00 | 1304-12-18 | 1000-SS-02 | HVAC Room No. 13 | Wet stain on the cealing (near the front door) | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-28 | 2022-06-24 | Construction | 2022-03-01 |  |  |  | V | EGAT-RFI-AR-GS-05184 |  |  | Construction
. | EGAT-RFI-AR-GS-05214.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 12 | Lack of skirting | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-03-07 | 2022-04-08 | Construction | 2022-03-11 |  |  |  | V | EGAT-RFI-AR-GS-05214 |  |  | Construction
. | EGAT-RFI-AR-GS-05214.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Room No. 12 | Conductivity test to be provided | A | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-03-07 | 2022-04-08 | Construction | 2022-03-11 |  |  |  | V | EGAT-RFI-AR-GS-05214 |  |  | Construction
. | EGAT-RFI-AR-GS-05375.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis A/5-11, C/5-11, A-C/11 | Plaster is not category IV | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-03-25 | 2022-11-29 | Construction | 2022-03-29 |  |  |  | V | EGAT-RFI-AR-GS-05375 |  |  | Construction
. | EGAT-RFI-AR-GS-05378.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A | Plaster is not category IV | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-03-29 | 2022-04-22 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-AR-GS-05378 |  |  | Construction
. | EGAT-RFI-AR-GS-05405.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis D-E/6, D-E/7A, D-E/8A | Plaster is not category IV | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-04 | 2022-04-22 | Construction | 2022-04-05 |  |  |  | V | EGAT-RFI-AR-GS-05405 |  |  | Construction
. | EGAT-RFI-AR-GS-05406.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis D-E/9A, D-E/11 | Plaster is not category IV | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-04 | 2022-04-22 | Construction | 2022-04-05 |  |  |  | V | EGAT-RFI-AR-GS-05406 |  |  | Construction
. | EGAT-RFI-AR-GS-05407.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis C/6-8A | Plaster is not category IV | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-04 | 2022-04-22 | Construction | 2022-04-05 |  |  |  | V | EGAT-RFI-AR-GS-05407 |  |  | Construction
. | EGAT-RFI-AR-GS-05408.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis C/8A-11 | Plaster is not category IV | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-04 | 2022-04-22 | Construction | 2022-04-05 |  |  |  | V | EGAT-RFI-AR-GS-05408 |  |  | Construction
. | EGAT-RFI-AR-GS-05460.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 6-8A/C-E | Painted cables on the walls | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-06 | 2022-04-25 | Construction | 2022-04-07 |  |  |  | V | EGAT-RFI-AR-GS-05460 |  |  | Construction
. | EGAT-RFI-AR-GS-05461.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 8A-11/C-E | Painted cables on the walls | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-06 | 2022-04-25 | Construction | 2022-04-07 |  |  |  | V | EGAT-RFI-AR-GS-05461 |  |  | Construction
. | EGAT-RFI-AR-GS-05516.01 | 800.00 | 1304-12-18 | 1000-SS-02 | 2nd Floor Axis 5-11/A-C | Adjustment of floor panels - horizontal and vertical | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-13 |  | Construction | 2022-04-14 | category changed A-> B (2022-04-28) evidence attached |  |  | V | EGAT-RFI-AR-GS-05516 |  |  | Construction
. | EGAT-RFI-AR-GS-05516.02 | 800.00 | 1304-12-18 | 1000-SS-02 | 2nd Floor Axis 5-11/A-C | Cleaning the construction from the dust and sand | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-13 | 2022-04-26 | Construction | 2022-04-14 |  |  |  | V | EGAT-RFI-AR-GS-05516 |  |  | Construction
. | EGAT-RFI-AR-GS-05516.03 | 800.00 | 1304-12-18 | 1000-SS-02 | 2nd Floor Axis 5-11/A-C | Cleaning surface under the raised floor from the trush | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-13 | 2022-04-26 | Construction | 2022-04-14 |  |  |  | V | EGAT-RFI-AR-GS-05516 |  |  | Construction
. | EGAT-RFI-AR-GS-05516.04 | 800.00 | 1304-12-18 | 1000-SS-02 | 2nd Floor Axis 5-11/A-C | Close the space around the cable tray | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-13 | 2022-04-26 | Construction | 2022-04-14 |  |  |  | V | EGAT-RFI-AR-GS-05516 |  |  | Construction
. | EGAT-RFI-AR-GS-05519.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 5-11/ A-C | Frame to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-26 |  | Construction | 2022-04-27 |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-05519 |  |  | Construction
. | EGAT-RFI-AR-GS-05519.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 5-11/ A-C | Panels to be clean or replace | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-26 |  | Construction | 2022-04-27 |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-05519 |  |  | Construction
. | EGAT-RFI-AR-GS-05519.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 5-11/ A-C | Adjust panels to frames. Surface need to be flat | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-26 |  | Construction | 2022-04-27 |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-05519 |  |  | Construction
. | EGAT-RFI-AR-GS-05558.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 11-11A/ A-C | Columns to be clean | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-26 |  | Construction | 2022-04-27 |  |  |  | V | EGAT-RFI-AR-GS-05558 |  |  | Construction
. | EGAT-RFI-AR-GS-05558.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 11-11A/ A-C | Concrete surface of landing to be prepare for painting | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-26 |  | Construction | 2022-04-27 |  |  |  | V | EGAT-RFI-AR-GS-05558 |  |  | Construction
. | EGAT-RFI-AR-GS-05558.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 11-11A/ A-C | After remaining works surface of painted elements should be inspeced one more time | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-26 |  | Construction | 2022-04-27 |  |  |  | V | EGAT-RFI-AR-GS-05558 |  |  | Construction
. | EGAT-RFI-AR-GS-05560.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis C-E/1-4 | Corner of pedestral of HVAC to be repaired | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2022-08-05 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05560 |  |  | Construction
. | EGAT-RFI-AR-GS-05560.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis C-E/1-4 | Connection of membrane and fasade to be sealed | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2022-08-11 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05560 |  |  | Construction
. | EGAT-RFI-AR-GS-05561.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | All penetration though membrane should be sealed with liquid membrane | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05561 |  |  | Construction
. | EGAT-RFI-AR-GS-05561.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Metal support of the the equipment and the cables trays should not lay directly on the membrane. | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05561 |  |  | Construction
. | EGAT-RFI-AR-GS-05561.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | The liquid membrane between the equipment to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05561 |  |  | Construction
. | EGAT-RFI-AR-GS-05567.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 6-11/D-E | Corrugated metal sheet to be corrected (edge) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-26 |  | Construction | 2022-04-26 | category changed A-> B (2022-04-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-05567 |  |  | Construction
. | EGAT-RFI-AR-GS-05567.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 6-11/D-E | Connection between flashing and fasade to be sealed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-26 |  | Construction | 2022-04-26 | category changed A-> B (2022-04-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-05567 |  |  | Construction
. | EGAT-RFI-AR-GS-05567.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 6-11/D-E | Corrugated metal sheet to be clean | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-26 |  | Construction | 2022-04-26 | category changed A-> B (2022-04-30) evidence attached |  |  | V | EGAT-RFI-AR-GS-05567 |  |  | Construction
. | EGAT-RFI-AR-GS-05568.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 6-11/E | The scratches and scaling of paint to be clean and repainted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05568 |  |  | Construction
. | EGAT-RFI-AR-GS-05568.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 6-11/E | Damages of the grouting to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 | 2023-03-07 | Construction | 2022-04-29 |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-05568 |  |  | Construction
. | EGAT-RFI-AR-GS-05568.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 6-11/E | Rust to be removed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05568 |  |  | Construction
. | EGAT-RFI-AR-GS-05587.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Flashing in bent and slope is in wrong direction | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-01-11 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05587 |  |  | Construction
. | EGAT-RFI-AR-GS-05587.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Damage flashing (and dents) should be replaced | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-01-11 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05587 |  |  | Construction
. | EGAT-RFI-AR-GS-05587.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Gap between flashing and fasade is required | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-01-11 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05587 |  |  | Construction
. | EGAT-RFI-AR-GS-05587.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Platform for ladder above flashing required (do not step on the flashing) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-02-24 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05587 |  |  | Construction
. | EGAT-RFI-AR-GS-05587.05 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | All screws fastening the lightning system should be sealed | C | EL | HEC EL Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-02-28 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05587 |  |  | Construction
. | EGAT-RFI-AR-GS-05588.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Flashing is bent on the dog house | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-29 | 2022-08-11 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05588 |  |  | Construction
. | EGAT-RFI-AR-GS-05588.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Triangular shape oh the flashing on the top of the flashing to be sealed | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-29 | 2022-08-11 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05588 |  |  | Construction
. | EGAT-RFI-AR-GS-05588.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | The bottom part of the dog house roofs are not finished | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-29 | 2022-08-11 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05588 |  |  | Construction
. | EGAT-RFI-AR-GS-05589.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/C-E | Flashing is bent and slope is in wrong direction | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-01-11 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05589 |  |  | Construction
. | EGAT-RFI-AR-GS-05589.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/C-E | Connection of fasade and flashing to be sealed. The flashing to be fastened | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2022-08-11 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05589 |  |  | Construction
. | EGAT-RFI-AR-GS-05589.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/C-E | Damage flashing (and dents) should be replaced | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-01-11 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05589 |  |  | Construction
. | EGAT-RFI-AR-GS-05589.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/C-E | Gap between flashing and fasade is required | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-01-11 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05589 |  |  | Construction
. | EGAT-RFI-AR-GS-05589.05 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/C-E | Platform for ladder above flashing required (do not step on the flashing) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-02-24 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05589 |  |  | Construction
. | EGAT-RFI-AR-GS-05589.06 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/C-E | All screws fastening the lightinig system sould be sealed | C | EL | HEC EL Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-04-07 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05589 |  |  | Construction
. | EGAT-RFI-AR-GS-05590.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A | Finish to fasade around the canopy | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-28 |  |  |  | V | EGAT-RFI-AR-GS-05590 |  |  | Construction
. | EGAT-RFI-AR-GS-05590.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A | Bottom part of the fasade to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-28 |  |  |  | V | EGAT-RFI-AR-GS-05590 |  |  | Construction
. | EGAT-RFI-AR-GS-05590.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A | All damages of the fasade to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-28 |  |  |  | V | EGAT-RFI-AR-GS-05590 |  |  | Construction
. | EGAT-RFI-AR-GS-05590.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A | The horizontal strips visible on the fasade to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-28 |  |  |  | V | EGAT-RFI-AR-GS-05590 |  |  | Construction
. | EGAT-RFI-AR-GS-05591.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/E, 4/C-E, 6-11/C | Crack on the wall close to landing | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05591 |  |  | Construction
. | EGAT-RFI-AR-GS-05591.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/E, 4/C-E, 6-11/C | Opening for cable close to canopy | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05591 |  |  | Construction
. | EGAT-RFI-AR-GS-05591.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/E, 4/C-E, 6-11/C | Finishing of fasade around the canopy | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05591 |  |  | Construction
. | EGAT-RFI-AR-GS-05591.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/E, 4/C-E, 6-11/C | The fasade not finished below flashing OSB and styrofoarm visible | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05591 |  |  | Construction
. | EGAT-RFI-AR-GS-05591.05 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/E, 4/C-E, 6-11/C | The fasade to be repair behind the temporary HVAC equipment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05591 |  |  | Construction
. | EGAT-RFI-AR-GS-05591.06 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/E, 4/C-E, 6-11/C | The fasade to be clean | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05591 |  |  | Construction
. | EGAT-RFI-AR-GS-05591.07 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/E, 4/C-E, 6-11/C | The fasade to be finished over the landing | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05591 |  |  | Construction
. | EGAT-RFI-AR-GS-05591.08 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/E, 4/C-E, 6-11/C | Bottom part of fasade to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05591 |  |  | Construction
. | EGAT-RFI-AR-GS-05591.09 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/E, 4/C-E, 6-11/C | Approved MS will be submitted (NCR 44) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05591 |  |  | Construction
. | EGAT-RFI-AR-GS-05591.10 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/E, 4/C-E, 6-11/C | Poor quality paint spot will be once again touch up paint (NCR 44) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05591 |  |  | Construction
. | EGAT-RFI-AR-GS-05592.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1/A-E | The fasade around the canopy to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-28 |  |  |  | V | EGAT-RFI-AR-GS-05592 |  |  | Construction
. | EGAT-RFI-AR-GS-05592.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1/A-E | The fasade around the handrails to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-28 |  |  |  | V | EGAT-RFI-AR-GS-05592 |  |  | Construction
. | EGAT-RFI-AR-GS-05592.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1/A-E | All damages of the fasade to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-28 |  |  |  | V | EGAT-RFI-AR-GS-05592 |  |  | Construction
. | EGAT-RFI-AR-GS-05592.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1/A-E | The fasade to be cleaned or painted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-28 |  |  |  | V | EGAT-RFI-AR-GS-05592 |  |  | Construction
. | EGAT-RFI-AR-GS-05593.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 11/A-C | The fasade to be finished around the canopy | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05593 |  |  | Construction
. | EGAT-RFI-AR-GS-05593.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 11/A-C | Remove tapes from brackets of the lightning protection | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05593 |  |  | Construction
. | EGAT-RFI-AR-GS-05593.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 11/A-C | Bottom part of the fasade to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05593 |  |  | Construction
. | EGAT-RFI-AR-GS-05593.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 11/A-C | All damages of fasade to be repair | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05593 |  |  | Construction
. | EGAT-RFI-AR-GS-05593.05 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 11/A-C | The fasade to be cleaned from dirt and wrong paint (different) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05593 |  |  | Construction
. | EGAT-RFI-AR-GS-05593.06 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 11/A-C | The openings around cabels to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05593 |  |  | Construction
. | EGAT-RFI-AR-GS-05594.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | All damages to be repaired | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 | 2022-08-12 | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05594 |  |  | Construction
. | EGAT-RFI-AR-GS-05594.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Walls to be cleaned or repainted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05594 |  |  | Construction
. | EGAT-RFI-AR-GS-05594.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Missing labels for fire stop silant | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05594 |  |  | Construction
. | EGAT-RFI-AR-GS-05594.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Cables to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-27 |  | Construction | 2022-04-29 |  |  |  | V | EGAT-RFI-AR-GS-05594 |  |  | Construction
. | EGAT-RFI-AR-GS-05597.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-E | Fasteners to the fasade to be sealed and painted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 |  | Construction | 2022-04-28 |  |  |  | V | EGAT-RFI-AR-GS-05597 |  |  | Construction
. | EGAT-RFI-AR-GS-05598.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Ground Slab & EP Axis 6-8A/C-E | Joint to be finished | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-09-03 | 2022-08-09 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-03741.01 |  |  | V | EGAT-RFI-AR-GS-05598. |  |  | Construction
. | EGAT-RFI-AR-GS-05598.02 | 800.00 | 1304-12-18 | 1000-SS-02 | 2nd floor slab Axis 1-4/A-C | Contractor should do leveling of the surface | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-08 | 2022-08-09 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-04452.01 |  |  | V | EGAT-RFI-AR-GS-05598. |  |  | Construction
. | EGAT-RFI-AR-GS-05598.03 | 800.00 | 1304-12-18 | 1000-SS-02 | ELEC Cable trench axis 2-4/D-E | Make flat the vertical surface of the trench | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-10 | 2022-08-09 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-04490.01 |  |  | V | EGAT-RFI-AR-GS-05598. |  |  | Construction
. | EGAT-RFI-AR-GS-05598.04 | 800.00 | 1304-12-18 | 1000-SS-02 | TIE GIRDER Axis 1/A-E , 4-6/C | Top level of girder to be adjust with concrete slab. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-11-04 | 2022-08-09 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-04491.01 |  |  | V | EGAT-RFI-AR-GS-05598. |  |  | Construction
. | EGAT-RFI-AR-GS-05606.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-E | Scratches and damages of doors | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-29 |  | Construction | 2022-05-02 |  |  |  | V | EGAT-RFI-AR-GS-05606 |  |  | Construction
. | EGAT-RFI-AR-GS-05606.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-E | Doors and frames to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-29 |  | Construction | 2022-05-02 |  |  |  | V | EGAT-RFI-AR-GS-05606 |  |  | Construction
. | EGAT-RFI-AR-GS-05606.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-E | Adjust doors and handwares | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-29 |  | Construction | 2022-05-02 |  |  |  | V | EGAT-RFI-AR-GS-05606 |  |  | Construction
. | EGAT-RFI-AR-GS-05607.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1A-1/A-E | Stair columns and grinders are dirty | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-19 | 2022-07-21 | Construction | 2022-05-20 |  |  |  | V | EGAT-RFI-AR-GS-05607 |  |  | Construction
. | EGAT-RFI-AR-GS-05607.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1A-1/A-E | Concrete works are not finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-19 |  | Construction | 2022-05-20 |  |  |  | V | EGAT-RFI-AR-GS-05607 |  |  | Construction
. | EGAT-RFI-AR-GS-05640.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 4-11/A-C | Scratches to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 |  | Construction | 2022-04-28 |  |  |  | V | EGAT-RFI-AR-GS-05640 |  |  | Construction
. | EGAT-RFI-AR-GS-05640.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 4-11/A-C | Floor to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 |  | Construction | 2022-04-28 |  |  |  | V | EGAT-RFI-AR-GS-05640 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis C-E/1-4 | Corner of pedestral of HVAC to be repaired | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2022-08-11 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05560.01 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis C-E/1-4 | Connection of membrane and fasade to be sealed | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2022-08-11 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05560.02 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | All penetration though membrane should be sealed with liquid membrane | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 |  | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05561.01 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Metal support of the the equipment and the cables trays should not lay directly on the membrane. | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 |  | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05561.02 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.05 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | The liquid membrane between the equipment to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 |  | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05561.03 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.06 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Flashing in bent and slope is in wrong direction | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-01-11 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05587.01 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.07 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Damage flashing (and dents) should be replaced | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-01-11 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05587.02 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.08 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Gap between flashing and fasade is required | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-01-11 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05587.03 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.09 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Platform for ladder above flashing required (do not step on the flashing) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-02-24 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05587.04 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.10 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | All screws fastening the lightning system should be sealed | C | EL | HEC EL Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-04-07 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05587.05 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.11 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Flashing is bent on the (some word i can not read?) dog house | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-29 | 2022-08-11 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05588.01 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.12 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | Triangular shape oh the flashing on the top of the flashing to be sealed | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-29 | 2022-08-11 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05588.02 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.13 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-C | The bottom part of the dog house roofs are not finished | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-29 | 2022-08-11 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05588.03 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.14 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/C-E | Flashing is bent and slope is in wrong direction | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-01-11 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05589.01 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.15 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/C-E | Connection of fasade and flashing to be sealed. The flashing to be fastened | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2022-08-11 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05589.02 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.16 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/C-E | Damage flashing (and dents) should be replaced | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-01-11 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05589.03 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.17 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/C-E | Gap between flashing and fasade is required | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-01-11 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05589.04 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.18 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/C-E | Platform for ladder above flashing required (do not step on the flashing) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-02-24 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05589.05 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.19 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-4/C-E | All screws fastening the lightinig system sould be sealed | C | EL | HEC EL Construction | Mr. Andrzej Misiek | 2022-04-28 | 2023-04-07 | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05589.06 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05645.20 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/A-E | Fasteners to the fasade to be sealed and painted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-28 |  | Construction | 2022-04-30 12:00:00 AM | Duplicate : EGAT-RFI-AR-GS-05597.01 |  |  | V | EGAAT-RFI-AR-GS-05645 |  |  | Construction
. | EGAT-RFI-AR-GS-05659.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/ A-E | Visible cracks on the ground floor | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-29 |  | Construction | 2022-05-02 |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-05659 |  |  | Construction
. | EGAT-RFI-AR-GS-05659.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1-11/ A-E | Uneven surface to be repainted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-04-29 |  | Construction | 2022-05-02 |  |  |  | V | EGAT-RFI-AR-GS-05659 |  |  | Construction
. | EGAT-RFI-AR-GS-05736.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1A-1/D-E | Concrete damages to be repaired | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-20 | 2022-07-21 | Construction | 2022-05-20 |  |  |  | V | EGAT-RFI-AR-GS-05736 |  |  | Construction
. | EGAT-RFI-AR-GS-05736.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1A-1/D-E | Chamfering to be corrected | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-20 | 2022-07-21 | Construction | 2022-05-20 |  |  |  | V | EGAT-RFI-AR-GS-05736 |  |  | Construction
. | EGAT-RFI-AR-GS-05760.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1A-4/A-E, 11-11A/B-C | Concrete damages to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-20 |  | Construction | 2022-05-20 |  |  |  | V | EGAT-RFI-AR-GS-05760 |  |  | Construction
. | EGAT-RFI-AR-GS-05760.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1A-4/A-E, 11-11A/B-C | Chamfering to be corrected | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-20 | 2022-07-21 | Construction | 2022-05-20 |  |  |  | V | EGAT-RFI-AR-GS-05760 |  |  | Construction
. | EGAT-RFI-AR-GS-05760.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1A-4/A-E, 11-11A/B-C | Level of the north end of walkway to be checked and corrected if need | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-20 |  | Construction | 2022-05-20 |  |  |  | V | EGAT-RFI-AR-GS-05760 |  |  | Construction
. | EGAT-RFI-AR-GS-05760.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1A-4/A-E, 11-11A/B-C | Surface around the collumn to be finished | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-05-20 | 2022-07-21 | Construction | 2022-05-20 |  |  |  | V | EGAT-RFI-AR-GS-05760 |  |  | Construction
. | EGAT-RFI-AR-GS-06546.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1A-1/A-E | Chamfering to be done | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-08-27 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06546 |  |  | Construction
. | EGAT-RFI-AR-GS-06546.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1A-1/A-E | Side edges of steps to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-08-27 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06546 |  |  | Construction
. | EGAT-RFI-AR-GS-06546.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1A-1/A-E | Outside edge of balcony to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-08-27 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06546 |  |  | Construction
. | EGAT-RFI-AR-GS-06546.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis 1A-1/A-E | Stairs landing - have to be leveled | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-08-27 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06546 |  |  | Construction
. | EGAT-RFI-AR-GS-06570.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis C-E/4-5 | Top surface of concrete is not marked | A | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-08-31 | 2022-12-14 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06570 |  |  | Construction
. | EGAT-RFI-AR-GS-06570.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Axis C-E/4-5 | Top level of electrical pit to adjust | C | EL | HEC EL Construction | Mr. Andrzej Misiek | 2022-08-31 | 2023-04-21 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-06570 |  |  | Construction
. | EGAT-RFI-CI-CW-00216.01 | 800.00 | 1304-12-18 | 1000-SS-02 and 1000-RIB-12 | Instrument Installation | Pernament Tag missing | C | CI | HEC CI Construction | Ariel Lazaro | 2021-09-16 | 2022-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-00224.01 | 800.00 | 1304-12-18 | 1000-RIB-12, 1000-SS-02 | Control Room | Water Leaking down the wall inside the building. | A | CI | HEC CI Construction | J.W.JEONG | 2021-09-23 | 2022-03-02 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-00254.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Instrument Installation | Pernament Tag missing | C | CI | HEC CI Construction | Ariel Lazaro | 2021-09-29 | 2022-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-00407.01 | 800.00 | 1304-12-18 | Auxilliary | 1000-GD-6904 | Permanent steel tag to be provide | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-27 | 2022-08-22 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-00407.02 | 800.00 | 1304-12-18 | Auxilliary | 1000-GD-6905 | Permanent steel tag to be provided | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-27 | 2022-08-22 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-00476.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Beacon and Sounder | Permanent tag missing (3ea) | B | CI | HEC CI Construction | Mr. Tomasz Jozel | 2021-12-01 | 2022-08-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-00568.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Beacon and Sounder(21ea) | Permanent tag missing (21ea) | B | CI | HEC CI Construction | Mr. Tomasz Jozel | 2021-12-21 | 2022-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01405.01 | 800.00 | 1304-12-18 | 1000-RIB-12 | CNBOP Tray | Mounting bracket support to be change | B | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-03 | 2022-06-11 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-HD-00017.01 | 800.00 | 1304-12-18 | 1000-SS-02 & RIB-12 | EGAT-HEC-1000-ELE-DLP-05002_6 | Battery test to be done before 30 April 2022 | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-04-07 | 2022-06-09 | SAT |  |  |  |  | V | EGAT-RFI-EL-HD-00017 |  |  | Construction
. | EGAT-RFI-EL-HD-00017.02 | 800.00 | 1304-12-18 | 1000-SS-02 & RIB-12 | EGAT-HEC-1000-ELE-DLP-05002_6 | CZF cable installation and connection between normal lighting panel and CBS panel to be done. Common failure connection to be done verified. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-04-07 | 2022-04-21 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-HD-00017.03 | 800.00 | 1304-12-18 | 1000-SS-02 & RIB-12 | EGAT-HEC-1000-ELE-DLP-05002_6 | Two cable between CBS panel and lighting fixture installation and connection to be done. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-04-07 | 2022-04-26 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-HD-00017.04 | 800.00 | 1304-12-18 | 1000-SS-02 & RIB-12 | EGAT-HEC-1000-ELE-DLP-05002_6 | Remote monitoring function for 05-CBS-001 shall be provided. TECHNICAL JUSTIFICATION: Based onlocal regulation, route test is required for central battery system and escape lighting. (Daily/ Monthly/ Annually). The contractor has not informed that remote monitoring of CBS's would not be installed earlier on whcih is normal practice in CBS that all the systems are integrated and monitored remotely so that to avoid time-consuming testing CBS's by going to them in person. Addionally, the daily testing consisitng in checking all the indicators requires additional competent person for only checking all the above indicators by going to all CBS's (located in at least 13 buildings) daily whcih was not known earlier on. Therefore, The contractor is requested to consider remote monitoring of CBS's. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-04-07 | 2023-03-29 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-HD-00017.05 | 800.00 | 1304-12-18 | 1000-SS-02& RIB-12 | EGAT-HEC-1000-ELE-DLP-05002_6 | Illumination test to be conducted. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-04-07 | 2022-04-28 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-HD-00017.06 | 800.00 | 1304-12-18 | 1000-SS-02 & RIB-12 | EGAT-HEC-1000-ELE-DLP-05502_6 | AC power source MCB Trip/open position (aux contact) is not indicated in central battery monitoring system. | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-04-07 | 2023-01-30 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-HD-00017.07 | 800.00 | 1304-12-18 | 1000-SS-02 & RIB-12 | EGAT-HEC-1000-ELE-DLP-05002_6 | Revised documentation (three-line diagrams, etc.) shall be provided for owner's review. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-04-07 | 2023-04-20 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-HD-00017.08 | 800.00 | 1304-12-18 | 1000-SS-02 & RIB-12 | EGAT-HEC-1000-ELE-DLP-05002_6 | The contractor will prepare documenatation in the scope of escape lighting in the form required by polish law for fire brigade acceptance during permit for use. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-04-07 | 2023-05-22 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-HD-00017.09 | 800.00 | 1304-12-18 | 1000-SS-02 & RIB-12 | EGAT-HEC-1000-ELE-DLP-05002_6 | Cable tray vendor (Baks) confirmation for lighting fixture installation to cable trays will be provided. | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-04-07 | 2022-06-09 | SAT |  |  |  |  | V | EGAT-RFI-EL-HD-00017 |  |  | Construction
. | EGAT-RFI-EL-SB-00290.01 | 800.00 | 1304-12-18 | 1000-SS-02 | MV Power Cable | Distance(100mm) between cables is not as per drawing. | B | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-05-27 | 2021-06-01 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00290 | C-EL-SB-00008 |  | Construction
. | EGAT-RFI-EL-SB-00290.02 | 800.00 | 1304-12-18 | 1000-SS-02 | MV Power Cable | Near wall of ss01 & ss02 shall not be backfill up-to 1 meter for duct seal filling purpose. | B | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-05-27 | 2021-06-15 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00290 | C-EL-SB-00008 |  | Construction
. | EGAT-RFI-EL-SB-00388.01 | 800.00 | 1304-12-18 | 1000-SS-02, 1000-RIB-12 | Cable tray | CNBOP cable trays vendor fittings will be used, no gaps between cable trays, do not use self made fittings | A | EL | Shinbo Electrical Subcon. | Mr. Szymon Woyke | 2021-07-01 | 2022-02-24 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00388 | C-EL-SB-00040 |  | Construction
. | EGAT-RFI-EL-SB-00405.01 | 800.00 | 1304-12-18 | 1000-SS-02, 1000-RIB-12 | Cable Tray | CNBOP Fittings should be used on CNBOP Cable Trays | C | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-07-16 | 2023-02-06 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-EL-SB-00405.01 | C-EL-SB-00032 |  | Construction
. | EGAT-RFI-EL-SB-00426.04 | 800.00 | 1304-12-18 | 1000-SS-01 | 01-MCC-1-1, 01-MCC-1-2, 01-MCC-1-3, 01-EMCC-1-1 | Lack of roof plates installation | C | EL | Shinbo Electrical Subcon. | Mr. Szymon Woyke | 2021-07-28 | 2023-02-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-EL-SB-00426.04 | C-EL-SB-00044 |  | Construction
. | EGAT-RFI-EL-SB-00430.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Lighting | Correct CNBOP Lighting cables connection to lighting fixture- max length of loose cable (without CNBOP fittings) 1,5m | A | EL | Shinbo Electrical Subcon. | Mr. Szymon Woyke | 2021-07-28 | 2021-12-02 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00430 | C-EL-SB-00043 |  | Construction
. | EGAT-RFI-EL-SB-00430.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Lighting | In room where lighting fixtures are above of other installation (cable trays ventilation duct) and shadowed lighting fixtures should be fitted in level of other installation | C | EL | Shinbo Electrical Subcon. | Mr. Szymon Woyke | 2021-07-28 | 2023-02-06 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-EL-SB-00430.02 | C-EL-SB-00043 |  | Construction
. | EGAT-RFI-EL-SB-00430.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Lighting | Emergency lighting drawing should be approved by fire expert | B | EL | Shinbo Electrical Subcon. | Mr. Szymon Woyke | 2021-07-28 | 2021-08-06 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00430.03 | C-EL-SB-00043 |  | Construction
. | EGAT-RFI-EL-SB-00430.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Lighting | No EL tags (emergency lighting) on lighting fixtures | B | EL | Shinbo Electrical Subcon. | Mr. Szymon Woyke | 2021-07-28 | 2021-12-02 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00430 | C-EL-SB-00043 |  | Construction
. | EGAT-RFI-EL-SB-00465.01 | 800.00 | 1304-12-18 | 1000-SS-02, 1000-RIB-12 | Cable Tray | CNBOP fitting will be used for emergency cable trays | A | EL | Shinbo Electrical Subcon. | Mr. Szymon Woyke | 2021-08-05 | 2022-02-24 | Construction |  | EGAT-RFI-EL-SB-00465 |  |  | V | EGAT-RFI-EL-SB-00465 | C-EL-SB-00060 |  | Construction
. | EGAT-RFI-EL-SB-00530.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Lighting | Emergency light have no CNBOP certificates | A | EL | Shinbo Electrical Subcon. | Mr. Szymon Woyke | 2021-09-01 | 2021-11-26 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00530 |  |  | Construction
. | EGAT-RFI-EL-SB-00541.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-ELE-DGA-00002_2 | Bushing cleaning and make sure no damage before energisation | A | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-09-01 | 2022-04-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00541.02 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-ELE-DGA-00002_2 | Fix and tighten of transformer base Anchor bolts | A | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-09-01 | 2022-01-10 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00541 |  |  | Construction
. | EGAT-RFI-EL-SB-00541.03 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-ELE-DGA-00002_2 | Name plate in Polish attached | C | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-09-01 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00541.04 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-ELE-DGA-00002_2 | Protocol of earthing connection | A | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-09-01 | 2022-03-11 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00541 |  |  | Construction
. | EGAT-RFI-EL-SB-00541.05 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-ELE-DGA-00002_2 | Valve position change before energisation | A | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-09-01 | 2022-01-05 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00541 |  |  | Construction
. | EGAT-RFI-EL-SB-00541.06 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-ELE-DGA-00002_2 | All instrument to check before energisation and fence fixing | A | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-09-01 | 2021-10-21 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00541 |  |  | Construction
. | EGAT-RFI-EL-SB-00541.07 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-ELE-DGA-00002_2 | FAT report to be closed | B | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-09-01 | 2021-10-21 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00541 |  |  | Construction
. | EGAT-RFI-EL-SB-00729.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Word "ZASILACZ" on tag =K10 =K13 =K14 shall be changed with word "ZASILANIE" | C | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-09-21 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00729.02 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Word "ODCINACZA" on tag =K12 shall be changed with word "ODŁĄCZNIKA" | C | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-09-21 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00729.03 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Earthing connection to be provided | A | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-09-21 | 2022-01-05 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00729 |  |  | Construction
. | EGAT-RFI-EL-SB-00729.04 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | FAT test should be attached | B | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-09-21 | 2021-10-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00763.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-200-ELE-DGA-00001_3 | Earthing Connection to be provided | A | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-09-21 | 2022-01-05 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00763 |  |  | Construction
. | EGAT-RFI-EL-SB-00763.02 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-200-ELE-DGA-00001_3 | damage voltage switch have to replace | A | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-09-21 | 2021-11-16 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00763 |  |  | Construction
. | EGAT-RFI-EL-SB-00883.01 | 800.00 | 1304-12-18 | 200-PR-001 | EGAT-HEC-900-ELE-DLP-01020_4 & EGAT-HEC-900-ELE-DLP-03012_1 | Provide earthing connection to maingrid | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-10-08 | 2023-03-29 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00883.02 | 800.00 | 1304-12-18 | 200-PR-001 | EGAT-HEC-900-ELE-DLP-01020_4 & EGAT-HEC-900-ELE-DLP-03012_1 | Permanent cable route number to be provide | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-10-08 | 2023-05-02 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00946.01 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DGA-00001_2 | MCC Panel. Tag no. A10F-DA001, A10F-EB001, A06F-MA001, A01F Incomer A-BA001, AB01F-Bus Tie BA001, B01F Incomer B-BA001 & A09B-KA001 CB to be installed | C | EL |  | Mr. Adam Siewiorek | 2021-10-25 | 2023-04-03 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00946.02 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DGA-00001_2 | Roof plate to be installed on MCC Panel | C | EL |  | Mr. Adam Siewiorek | 2021-10-25 | 2023-04-07 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00946.03 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DGA-00001_2 | Clean the all MCC Panels | C | EL |  | Mr. Adam Siewiorek | 2021-10-25 | 2023-03-29 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00946.04 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DGA-00001_2 | Floor opening of the left side to be clarify | C | EL |  | Mr. Adam Siewiorek | 2021-10-25 | 2023-03-29 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00947.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00001_2 | Earthing connection to be done for bus duct & supports | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-10-25 | 2022-04-19 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00947 |  |  | Construction
. | EGAT-RFI-EL-SB-00947.02 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00001_2 | Bus duct connection to be done at transformer side. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-10-25 | 2022-04-19 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00947 |  |  | Construction
. | EGAT-RFI-EL-SB-00947.03 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00001_2 | Bus duct name plate to be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-10-25 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00947.04 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00001_2 | Closed all wall opening with approved fire sealant. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-10-25 | 2022-04-19 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00947 |  |  | Construction
. | EGAT-RFI-EL-SB-00947.05 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00001_2 | Installed joint cover of bus duct after torque test | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-10-25 | 2022-04-21 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00947 |  |  | Construction
. | EGAT-RFI-EL-SB-00947.06 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00001_2 | Flexible connection to be provided. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-10-25 | 2022-05-13 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00988.01 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.1 MV SWGR should heating and cleaning before energization | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-21 | Construction |  | EGAT-RFI-EL-SB-00988 |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00988.02 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.2 No tablets for observation the earth switch position | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-21 | Construction |  | EGAT-RFI-EL-SB-00988 |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00988.03 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.3 ZCT's not connected (after connect should perform promary injection test)-outgoing feeders | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2023-03-29 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00988.04 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.4 Interface test with ECMS (after ECMS installation & start-up) | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  | EGAT-RFI-EL-SB-00988 |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00988.05 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.5 Insulation resistance of the CB's below the minimum required value | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  | EGAT-RFI-EL-SB-00988 |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00988.06 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.6 Missing setting for bender and TR1200 & Epcos devise | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  | EGAT-RFI-EL-SB-00988 |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00988.07 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.7 VT test and HV test date to be confirmed,it should be minimum one month before energization (Point 7-2.12 & point-9) | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  | EGAT-RFI-EL-SB-00988 |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00988.08 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.8 Signals from 01-SWGR-2-1 AND STG to be checked after installation cables | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00988.09 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.9 FO cable to 01-SWGR-2-1 missing (Differential protection to checked)missing cable between k10 and K11,K12,K11 & K12,K06 & K17 MISSING FO CABLES FROM ECMS in K01,K11,K12 & K25 | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  | EGAT-RFI-EL-SB-00988 |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00988.10 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.10 MIssing ethernet patchcords between P49 i n the K2 & P49 in unit K24 | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  | EGAT-RFI-EL-SB-00988 |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00988.11 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.11 The protectionsettings in relay coordination _Rev.2 not match the typical unit K20 | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-25 | Construction |  | EGAT-RFI-EL-SB-00988 |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00990.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | SS02 UPS Door leveling work to be done | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-03 | 2021-12-03 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00990 |  |  | Construction
. | EGAT-RFI-EL-SB-00990.02 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | SS02 UPS Back cover should be fix and align | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-03 | 2021-12-03 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00990 |  |  | Construction
. | EGAT-RFI-EL-SB-00990.03 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | RIB-12 UPDP Panel door are unable to open due to HVAC Equipment on front. confirm by HEC Engineering | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-03 | 2022-04-13 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00990 |  |  | Construction
. | EGAT-RFI-EL-SB-00990.04 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Clean the all panels | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-03 | 2022-04-15 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-00990 |  |  | Construction
. | EGAT-RFI-EL-SB-00990.05 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | All scratches touchup paint to be applied | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-03 | 2022-04-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.01 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MCC-1-1A/1B | 16.1 Missing CT BC5 in units A05F.RA001 and A06F.RA001 | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2023-03-29 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.02 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MCC-1-1A/1B | 16.2 The integrated module does not connect to the letter in B06B.KA001 and A11B.FA001 | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2023-04-03 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.03 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MCC-1-1A/B | 16.3 Switchgear should be cleaned, there is a lot of dust on the equipment before energized | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.04 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MCC-1-1A/B | 16.4 Missing setting of Modl | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2023-03-29 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.05 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MCC-1-1A/B | 16.5 Non compliance of the switchgear with the drawing (Missing pieces withdrawables unit and change name) | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.06 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MCC-1-1A/B | 16.5 Non compliance of the switchgear with the drawing (Missing pieces withdrawables unit and change name) | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2023-03-29 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.07 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MCC-1-1A/B | 16.7 Some non compliance found in EGAT-HEC-000-ELE-CAL-00005_Relay coordination_Rev.2 Attachment-3 & 4 | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.08 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MCC-1-1A/B | 16.8 Missing or damaged roof plates and damaged green 'SIVACON' sheet | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2023-05-19 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.09 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MCC-1-1A/B | 16.9 Signal B01.3 in IncA, IncB to be reprogrammed (CB open, withdrawable unit operation position)- not corresponding with SWGR documentation | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.10 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MCC-1-1A/B | 16.10 Functional testing of electrical interlocks between 02-MCC-1-1 and Upstream SWGR. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.11 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-EMCC-1-1A/B | 16.1 Some non compliance found in EGAT-HEC-000-ELE-CAL-00005_Relay coordination_Rev.2 Attachment-3 &4 (Point 5) | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.12 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-EMCC-1-1A/B | 16.2 Signal B01.3 in IncA, IncB to be reprogrammed (CB open, withdrawable unit operation position)- not corresponding with MVSWGR. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.13 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-EMCC-1-1A/B | 16.3 Switchgear should be cleaned, there is a lot of dust on the equipment before energized. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.14 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-EMCC-1-1A/B | 16.4 Interface test with ECMS should be performed (Point 10.1, 10.2, 10.3). | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.15 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-EMCC-1-1A/B | 16.5 Damaged Green 'SIVACON' Sheet to be repaired. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2023-05-24 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.16 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-EMCC-1-1A/B | 16.6 To be performed functional testing of electrical interlocks with other switchgears. | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01047.17 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-EMCC-1-1A/B | Withdraw units is inconsistent with GA 02-EMCC-1-1_202110920 | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01076.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-05002_3 | Fire sealant to be provided on fire wall TR Area | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-15 | 2022-02-08 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01076 |  |  | Construction
. | EGAT-RFI-EL-SB-01096.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Junction box battery rack & battery tag number plate to be provide | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-22 | 2023-03-17 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01096.02 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Battery junction box explosion class shall be verifying by (vendor of HEC) | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-22 | 2021-12-07 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01096 |  |  | Construction
. | EGAT-RFI-EL-SB-01096.03 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Apply touch up paint on scratched area (BCB) | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-22 | 2023-04-07 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01096.04 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Battery numbers to be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-22 | 2023-03-17 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01096.05 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Battery box earthing to be connected | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-22 | 2021-12-01 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01096 |  |  | Construction
. | EGAT-RFI-EL-SB-01096.06 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Battery & Junction box to be clean | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-22 | 2022-03-16 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01096 |  |  | Construction
. | EGAT-RFI-EL-SB-01117.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-05002_4 | Provide earthing connection to main grid | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-22 | 2022-04-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01117.02 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-05002_4 | Normal & Emergency cable tray number to be provide | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-22 | 2022-04-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01117.03 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-05002_4 | Provide CNBOP fitting for vertical upset point | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-22 | 2022-02-24 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01117 |  |  | Construction
. | EGAT-RFI-EL-SB-01117.04 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-05002_4 | Red markedup drawing will be update in next revision | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-22 | 2023-02-17 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01135.01 | 800.00 | 1304-12-18 | PDH | EGAT-HEC-200-ELE-DLP-04003_2 | Provide correct depth of PVC insulated cale at SS-01 in front of ABB TR | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2021-11-25 | 2023-04-05 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01169.01 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-900-ELE-SCH-00001_1 | In Battery room, additional cable support to be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-01 | 2023-04-06 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01169.02 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-900-ELE-SCH-00001_1 | Cable clamp to be provided for those big cable | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-01 | 2023-04-25 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01170.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-ELE-SCH-0001_1 | In battery room, additional cable support to be provided | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-01 | 2021-12-10 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01170 |  |  | Construction
. | EGAT-RFI-EL-SB-01170.02 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-ELE-SCH-0001_1 | Cable clamp to be provided for those big cables above 70 mm sq. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-01 | 2021-12-22 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01170 |  |  | Construction
. | EGAT-RFI-EL-SB-01186.01 | 800.00 | 1304-12-18 | 1000-RIB-12 | V-VTV-E06-000-00000-00009 | 12-UPS-1-1 - MCB's to be changed Q014A, Q015A, Q030D, Q031D, HEC must provide information when it will be done m because during visit of VERTIV's Engineer no changes were made | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-13 | 2023-04-07 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01186.02 | 800.00 | 1304-12-18 | 1000-RIB-12 | V-VTV-E06-000-00000-00009 | After above changes functionality of UPS/UPDP in case of common fault need to be verified. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-13 | 2023-04-03 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01186.03 | 800.00 | 1304-12-18 | 1000-RIB-12 | V-VTV-E06-000-00000-00009 | 12-UPS-1-1 A fault of electric FAN present on Display - due date needs to be agreed. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-13 | 2023-02-24 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01186.04 | 800.00 | 1304-12-18 | 1000-RIB-12 | V-VTV-E06-000-00000-00009 | BMS to be installed and SAT to be carried out. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-13 | 2023-02-20 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01189.01 | 800.00 | 1304-12-18 | PDH | EGAT-HEC-200-ELE-DGA-05015_3 | CNBOP fitting & riser vertical tray installation to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-08 | 2023-05-25 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01193.01 | 800.00 | 1304-12-18 | 1000-SS-02, 1000-RIB-12 | EGAT-HEC-1000-ELE-DGA-00002_2 | Earthing connection to be provided | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-02 | 2022-01-05 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01193 |  |  | Construction
. | EGAT-RFI-EL-SB-01193.02 | 800.00 | 1304-12-18 | 1000-SS-02, 1000-RIB-12 | EGAT-HEC-1000-ELE-DGA-00002_2 | Provide touch up paint on scratches area & clean all glue spots | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-02 | 2023-05-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01194.01 | 800.00 | 1304-12-18 | 1000-SS-02, 1000-RIB-12 | EGAT-HEC-1000-ELE-DGA-00002_2 | Earthing connection to be provided | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-02 | 2022-01-05 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01194 |  |  | Construction
. | EGAT-RFI-EL-SB-01194.02 | 800.00 | 1304-12-18 | 1000-SS-02, 1000-RIB-12 | EGAT-HEC-1000-ELE-DGA-00002_2 | Provide touch up paint on cratches area & clean all glue spots | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-02 | 2023-05-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01197.01 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-DP-001 | 16.1 No ATS Settings | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01197.03 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-DP-001 | 16.3 Interface test with ECMS not complete | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01197.04 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-DP-001 | 16.4 Non-compliance of the switchgear with the V-SPL-E02-02DP01-00206_Electrical Schematic Diagram (Manufacture scope) | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01197.05 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-DP-001 | 16.1 No ATS Settings | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01197.06 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-DP-001 | 16.2 Some non compliance found in EGAT-HEC-000-ELE-CAL-00005_Relay coordination_Rev.2 Attachment-4. MCC Setting table. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01197.08 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-DP-001 | 16.4 To much window in A01, for main breaker o keep IP2X, when open the door (where it is possible to touch the live part) (Manufacture scope) | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01198.01 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MDB-001 | 16.1 No ATS Settings | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01198 |  |  | Construction
. | EGAT-RFI-EL-SB-01198.02 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MDB-001 | 16.2 Some non compliance found in EGAT-HEC-000-ELE-CAL-00005_Relay coordination_Rev.2 Attachment-4. MCC Setting table. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01198 |  |  | Construction
. | EGAT-RFI-EL-SB-01198.03 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MDB-001 | 16.3 Interface test with ECMS not complete | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01198.04 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MDB-001 | 16.4 No covers on the switches S1, S2, S3 (Manufacture scope) | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01198 |  |  | Construction
. | EGAT-RFI-EL-SB-01198.05 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MDB-001 | 16.5 K2 relay not properly working in A03.JA001 (Manufacture scope) | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01198 |  |  | Construction
. | EGAT-RFI-EL-SB-01198.06 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MDB-001 | 16.6 No possibility to reset the trip on the breaker in A05.FA001 (Manufacture scope) | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-11 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01198 |  |  | Construction
. | EGAT-RFI-EL-SB-01225.01 | 800.00 | 1304-12-18 | PR-1 | EGAT-HEC-200-ELE-DGA-05033_3 | CNBOP fitting & riser installation to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-08 | 2023-05-11 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01225.02 | 800.00 | 1304-12-18 | PR-1 | EGAT-HEC-200-ELE-DGA-05033_3 | Emergency & normale lighting tag to be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-08 | 2023-03-28 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01225.03 | 800.00 | 1304-12-18 | PR-1 | EGAT-HEC-200-ELE-DGA-05033_3 | Red markup drawing update in next revision | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-08 | 2023-02-17 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01225.04 | 800.00 | 1304-12-18 | PR-1 | EGAT-HEC-200-ELE-DGA-05033_3 | Earthing connection & bounding jumper to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-08 | 2023-04-26 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01226.01 | 800.00 | 1304-12-18 | PR-2-3 | EGAT-HEC-200-ELE-DGA-05034_3 | CNBOP fitting & riser installation to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-08 | 2023-04-03 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01226.02 | 800.00 | 1304-12-18 | PR-2-3 | EGAT-HEC-200-ELE-DGA-05034_3 | Emergency & normale lighting tag to be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-08 | 2023-03-23 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01226.03 | 800.00 | 1304-12-18 | PR-2-3 | EGAT-HEC-200-ELE-DGA-05034_3 | Earthing connection & bounding umper to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-08 | 2023-04-26 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01234.01 | 800.00 | 1304-12-18 | STR-1-2 | EGAT-HEC-200-ELE-DGA-05032_3, 05012_5 | Provide touch up paint on supports | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-09 | 2023-04-26 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01234.02 | 800.00 | 1304-12-18 | STR-1-2 | EGAT-HEC-200-ELE-DGA-05032_3, 05012_5 | Lighting tag to be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-09 | 2023-04-26 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01235.02 | 800.00 | 1304-12-18 | PDH | EGAT-HEC-200-ELE-DGA-05015_3 | Emergency & normale lighting tag to be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-08 | 2023-04-18 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01235.03 | 800.00 | 1304-12-18 | PDH | EGAT-HEC-200-ELE-DGA-05015_3 | Earthing connection & bounding jumper to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-08 | 2023-04-26 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01253.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-05002_4 | CNBOP fitting riser shall be install as per manufacturer manual | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-09 | 2022-02-24 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01253 |  |  | Construction
. | EGAT-RFI-EL-SB-01253.02 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-05002_4 | Emergency lighting support fix as per correct installation details Max-1.5 meters | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-09 | 2022-02-11 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01253 |  |  | Construction
. | EGAT-RFI-EL-SB-01256.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-05002_4 | Red markup drawing update in next revision | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-09 | 2023-02-17 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01256.02 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-05002_4 | Earthing connection to be done in socket outlet | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-09 | 2022-01-05 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01256 |  |  | Construction
. | EGAT-RFI-EL-SB-01256.03 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-05002_4 | Clean the wall paint and provide temporary cover for protection from dust & paint | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-09 | 2022-04-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01256.04 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-05002_4 | Close the gaps above the socket outlet in MV, UPS-RIB12, UPS-02 & Rack room on gypsum wall | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-09 | 2022-01-05 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01256 |  |  | Construction
. | EGAT-RFI-EL-SB-01256.05 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DGA-05002_4 | External the conduit for outlet socket in LV room east side wall | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-09 | 2022-02-11 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01256 |  |  | Construction
. | EGAT-RFI-EL-SB-01261.01 | 800.00 | 1304-12-18 | 1000-SS-01 | V-VTV-E06-000-00000-00009 | 02-UPS-1-2 - MCB to be changed Q01, HEC must provide information when it will be done because during visit of VERTIV's emgineer no changes were made. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-13 | 2023-04-07 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01261.02 | 800.00 | 1304-12-18 | 1000-SS-01 | V-VTV-E06-000-00000-00009 | After above changes functionality of UPS/UPDP in case of common fault need to be verified. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-13 | 2023-04-07 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01261.03 | 800.00 | 1304-12-18 | 1000-SS-01 | V-VTV-E06-000-00000-00009 | BMS for AC UPS and DC UPS to be installed and SAT to be carried out. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-13 | 2023-02-20 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01306.01 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E04-000-00000-00012 | Point 9.1 -Cleaning & drying required before Energization | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2022-04-27 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01306 |  |  | Construction
. | EGAT-RFI-EL-SB-01306.02 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E04-000-00000-00012 | Lack of oil tests (point 6 of V_SAN-E04-000-000000-00012) | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2022-05-12 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01306 |  |  | Construction
. | EGAT-RFI-EL-SB-01306.03 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E04-000-00000-00012 | Insulation resistance of the control circuits value result to be indicated in the SAT report. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2022-03-14 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01306 |  |  | Construction
. | EGAT-RFI-EL-SB-01306.04 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E04-000-00000-000012 | 71Q (Oil level trip Signal) to be wired and tested | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2022-04-06 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01306 |  |  | Construction
. | EGAT-RFI-EL-SB-01306.05 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E04-000-00000-00012 | Point 9.1 -Cleaning & drying required before Energization | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2022-04-27 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01306 |  |  | Construction
. | EGAT-RFI-EL-SB-01306.06 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E04-000-00000-00012 | Lack of oil tests (point 6 of V_SAN-E04-000-000000-00012) | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2022-05-12 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01306 |  |  | Construction
. | EGAT-RFI-EL-SB-01306.07 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E04-000-00000-00012 | Insulation resistance of the control circuits value result to be indicated in the SAT report. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2022-03-14 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01306 |  |  | Construction
. | EGAT-RFI-EL-SB-01306.08 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E04-000-00000-000012 | 71Q (Oil level trip Signal) to be wired and tested | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2022-04-06 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01306 |  |  | Construction
. | EGAT-RFI-EL-SB-01308.01 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00684 | Point 15.1- Confirm point (2, 3.3, 3.4, 7.1, 8, 9.3, 9.4, 10, 13.1) in shinbo scope | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2022-05-12 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01308.02 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00684 | Point 15.2- Connect the busduct to the transformer in the shinbo scope, the remark must be removed before energization. | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2022-08-26 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01308.03 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00684 | Point 15.3- Busduct insulation resistance below the minimum value. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2022-04-08 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01308.04 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00684 | Point 15.1- Confirm point 2, 3.3, 3.4, 7.1, 8, 9.3, 10, 13.1 in shinbo scope. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-02-10 | 2022-05-12 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01308.05 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SLP-E02-000-00000-00684 | Point 15.2- Connect the busduct to the transformer in the shinbo scope, the remark must be removed before energization. | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2022-08-26 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01323.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-INC-DGA-00311 | Provide additional support & grommet in cellar room. | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-03-08 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01323 |  |  | Construction
. | EGAT-RFI-EL-SB-01323.02 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-INC-DGA-00311 | Install the cable tray & bonding jumper that removed during fire alarm testing in MV Room. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-03-08 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01323 |  |  | Construction
. | EGAT-RFI-EL-SB-01330.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DLP-03001 | Battery room 1000-SS-02, Provide additional support for vertical cable tray to avoid shaking. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-12-30 | 2022-03-16 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01330 |  |  | Construction
. | EGAT-RFI-EL-SB-01342.01 | 800.00 | 1304-12-18 | SS-02 & RIB-12 | EGAT-HEC-1000-ELE-DLP-06002_5 | Provide JB Tag & should be update in Red Marked-up drawing | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-11 | 2023-02-17 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01365.01 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-00002_2 | Provide single line diagram for 02-CK-1-1A/1B | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-13 | 2023-05-30 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01365.02 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-00002_2 | Clarify correct type of LV Capacitor Banks (on document MGK Type/ on Panel KMDn 800 Type) | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-13 | 2023-03-29 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.01 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | FTB Spare cable entry opening to be fixed with blind plug | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-05-09 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.02 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Fire Barrier to be installed in all cable entry exits(at least 10 cm of fire seal on cables - both sides). Nameplates included. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-05-09 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.03 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Fire equipment CNBOP Glow in dark labels to be provided e.g. MCP, fire eqstinguisher | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-03-23 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.04 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | UPS Room 2 sounder and beacon to be installed. | A | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2022-04-26 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.05 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Network connection to be checked during final SAT | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.06 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | All fire equipment logical tags to be installed next to the elements e.g. SD, MCP, FH, FB, HD, RI, I/O modules. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.07 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Fire damper tags to be installed. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-05-11 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.08 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Certified fire damper controller to installed and tested. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.09 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | All faults(not connected to network problems) to be cleared from the panel. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.10 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | All fire alarm devices certificates to be submitted. Especially: CNBOP for outdoor sounders, cable fixing equipment(anchor). | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.11 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | ISB connected cables calculation to be submitted. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.12 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Printer missing | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-06-07 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.13 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | English description of equipment(configuration) to be changed to Polish | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.14 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | FACP langauge to be changed to Poilsh | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.15 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | FACP Tested as Stand alone - network to be tested in the SAT with full ring topology. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.16 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Devices quantity in one zone is 30 shall NOT exceed 30. | A | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2022-04-14 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.17 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Name plate in FACP second door to be changed to bilingual and with correct "CE" mark - both cases. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-05-09 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.18 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | T01 to be checked after HVAC operation in building. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-04-24 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.19 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | All MCP glasses to be installed correctly and not broken | A | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2022-04-14 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.20 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Vertical cable tray cover to be installed. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-05-11 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.21 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Design tags to be attached with two cable ties so they shall be easily visible from the ground. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-05-11 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.22 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Few cable and device tags missing. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-05-11 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.23 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Cable tags going through the wall to be tagged at the both sides near the wall. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-06-07 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.24 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Earthing cables to be provided with spring washers | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-04-11 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.25 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Duct SD covers to be mounted. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-05-09 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.26 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Fire equipment to be cleaned e.g. sounders, beacons | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-03-28 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.27 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Batteries for FACP are 38Ah instead of 40Ah as in documentation. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.28 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Printer openings to be protected against rust. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-06-13 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.29 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | CU05 device wiring and purpose to be checked. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.30 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | T02, T03, T04, T08 and T09 documentation to be provided. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.31 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | T05 remaining loops to be connected and tested. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.32 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | T06 and T07 permanent main power cable to be connected and tested. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-04-26 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.33 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | HVAC room beacon to be installed(and sounder if needed after wall, roof and floor openings are sealed). | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-06-13 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.34 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Rearanging of the RI based on the detectors placement(AV on the wall in the same line as the detector, duct detector RI to be placed under the detector on false celing) | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.35 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Duct SD C&E to be confirmed. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-02-09 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.36 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | HVAC room roof opening area not fire protected(no somke detector). | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.37 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | SD 6801 logical missconnection to RI with tag 6849. | B | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2022-03-14 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.38 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | SD 6849(UPS Room AV SD) smoke detection fault. Working after reset. | B | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2022-03-14 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01430.39 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-06002_5 | Check if there are two independent power supplies to power the FACP. One regular and UPS. UPS for 1 hour. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-03-28 | 2023-02-07 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01493.01 | 800.00 | 1304-12-18 | RP-01 & 02 | EGAT-HEC-200-ELE-DLP-05016, 05017, 05019, 05020 | Earthing connection to be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2023-05-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01493.02 | 800.00 | 1304-12-18 | RP-01 & 02 | EGAT-HEC-200-ELE-DLP-05016, 05017, 05019 , 05020 | Provide tray tag numbers on normal & emergency tray | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-10 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01558.01 | 800.00 | 1304-12-18 | RP-01 | EGAT-HEC-200-ELE-DLP-05021, 05024 | Earthing connection to be provide. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-21 | 2023-05-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01558.02 | 800.00 | 1304-12-18 | RP-01 | EGAT-HEC-200-ELE-DLP-05021, 05024 | Provide tray tag number on normal & emergency tray. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-21 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01742.02 | 800.00 | 1304-12-18 | SS-05 |  | Cable entry point on the panel should be closed | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-02 | 2023-02-01 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01776.01 | 800.00 | 1304-12-18 | SS-02 | V-SPL-E02-000-00000-00382_2 | There are no accessories mentioned in the point 2.1, 2.8 and 8.1, 8.8 | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-07 | 2022-11-23 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01776.02 | 800.00 | 1304-12-18 | SS-0-2 | V-SPL-E02-000-00000-00382_2 | Checking if all cover have been fitted. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-07 | 2022-04-21 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01910.01 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-05002 | Provide 01-CBS-002 Panel tag & label | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-18 | 2023-03-28 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01945.01 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-05002 | Provide blind plug for CNBOP Junction box | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-06 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01945 |  |  | Construction
. | EGAT-RFI-EL-SB-01945.02 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-05002 | Change the all screw to anchor bolts cable clamp in SS-02 on Gypsum wall. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-06 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01945 |  |  | Construction
. | EGAT-RFI-EL-SB-01945.03 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-05002 | MV/LV SWGR room escape light location fix as per approved drawing for correct lux illumination. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-26 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01945 |  |  | Construction
. | EGAT-RFI-EL-SB-01945.04 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-05002 | Change the dirty ceiling board in rack room fixture tag-02-CBS-001/05/58 | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-06 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01945 |  |  | Construction
. | EGAT-RFI-EL-SB-01945.05 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-05002 | Provide red marked up drawing for all changes in SS-02 | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-26 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01945 |  |  | Construction
. | EGAT-RFI-EL-SB-01945.06 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DLP-05002 | Rack room escape lighting fixture solid ceiling fixing is required. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-25 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01945 |  |  | Construction
. | EGAT-RFI-EL-SB-01958.01 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.1 MV Switchgear should heating and cleaning before energization. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-21 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01958 |  |  | Construction
. | EGAT-RFI-EL-SB-01958.02 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.2 No tablets for observation the earth switch position | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-21 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01958 |  |  | Construction
. | EGAT-RFI-EL-SB-01958.03 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.3 ZCT's not connected (after connect should perform primary injection test) outgoing feeders | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-11-23 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01958.04 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.4 Interface test with ECMS (after ECMS installation and start up) | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-08 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01958 |  |  | Construction
. | EGAT-RFI-EL-SB-01958.05 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.5 Insulation resistance of the CB's below the minimum required value. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-08 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01958 |  |  | Construction
. | EGAT-RFI-EL-SB-01958.06 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.6 Missing settings for bender and TR1200 and Epcos devise. | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-08 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01958 |  |  | Construction
. | EGAT-RFI-EL-SB-01958.07 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.7 VT Test and HV Test date to be confirmed, it should be maximum one month before energization (point 7-2.12 and point 9) | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-08 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01958 |  |  | Construction
. | EGAT-RFI-EL-SB-01958.08 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.8 Signals from 01-Swgr-2-1 and STG to be checked after installation cables. | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-11-23 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01958.09 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-0000-00182 | 12.9 FO Cable to 01-swgr-2-1 missing (Differential protection to be checked) missing cable between K10, and K12, K06 and K17, missing FO Cables from ECMS in K01, K11, K12 and K25 | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-08 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01958 |  |  | Construction
. | EGAT-RFI-EL-SB-01958.10 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 12.10 Missing ethernet patch cords between P49 in the unit K2 and P49 in unit K24 | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-08 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01958 |  |  | Construction
. | EGAT-RFI-EL-SB-01958.11 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-SWGR2-1A/B | 12.11 The protection settings in relay coordinationRev.2 do not match the typical unit K20. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-25 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-01958 |  |  | Construction
. | EGAT-RFI-EL-SB-01958.12 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-SWGR2-1A/B | 12.12 All surge arrester are connected. | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-11-23 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01959.01 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-EO2-000-00000-00182 | It is possible to open the box connecting the bus bar with the live switchgear. | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-08-30 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01959.02 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 10.2 Shinbo confirm the correctness of the points 3.2, 3.3, 3.4 | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-04-08 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01959.03 | 800.00 | 1304-12-18 | 1000-SS-02 | V-SPL-E02-000-00000-00182 | 10.3 Confirmation of the correctness of tighting torque the busbar to the switchgear in the shinbo scopr. This remark must be removed before energizing. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-24 | 2022-05-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02046.01 | 800.00 | 1304-12-18 | PDH Area | EGAT-HEC-200-ELE-DLP-01016, 01018 | Provide elbow below the tray at LCS Area | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-03-31 | 2023-05-02 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02106.01 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-200-ELE-SCH-00001_1 | Cable opening should be close of proper material. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-04-08 | 2022-09-07 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-02106 |  |  | Construction
. | EGAT-RFI-EL-SB-02107.01 | 800.00 | 1304-12-18 | SS-02 & SS-01 | EGAT-HEC-900-ELE-SCH-00001_1 | Earthing cable clarification related to CT should be provided. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-04-08 | 2022-09-07 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-02107 |  |  | Construction
. | EGAT-RFI-EL-SB-02107.02 | 800.00 | 1304-12-18 | SS-02 & SS-01 | EGAT-HEC-900-ELE-SCH-00001_1 | Grommet should be provide for CT & earthing cable on the gland plate. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-04-08 | 2022-09-07 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-02107 |  |  | Construction
. | EGAT-RFI-EL-SB-02107.03 | 800.00 | 1304-12-18 | SS-02 & SS-01 | EGAT-HEC-900-ELE-SCH-00001_1 | Cable gland document and MRIR should be provide. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-04-08 | 2022-09-07 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-02107 |  |  | Construction
. | EGAT-RFI-EL-SB-02108.01 | 800.00 | 1304-12-18 | SS-01 | EGAT-HEC-200-ELE-SCH-00001_1 | Cable opening should be close of proper material. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-04-08 | 2022-09-07 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-02108 |  |  | Construction
. | EGAT-RFI-EL-SB-02113.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-200-ELE-DLP-05003 | Provide emergency lighting label as per standard procedure. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-04-08 | 2023-04-11 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02136.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-ELE-DLP-05002 | Provide emergency lighting label as per standard procedure | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-04-08 | 2023-04-11 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02220.01 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-900-ELE-SCH-00001_1 | Fire stopper should be provided inside the panel and transformer cable entrance point. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-04-22 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02220.02 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-900-ELE-SCH-00001_1 | Metal tie should be provide inside the transformer for the cable. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-04-22 | 2022-04-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02234.01 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Earthing connection should be provided for VSD Panel. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-04-22 | 2023-04-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02234.02 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Clean the VSD Panel before energize. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-04-22 | 2023-03-29 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02496.03 | 800.00 | 1304-12-18 | SS-03 | V-SPL-E02-000-00000-00012 rev.0 | Touch up paint is required on top side of transformer | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-06-03 | 2022-06-03 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02722.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DLP-03002 | Provide missing grommet to all edge areas | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-06-06 | 2023-04-06 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02722.02 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DLP-03002 | Complete the damaged bonding jumper in cable pit | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-06-06 | 2023-04-06 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02722.03 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-1000-ELE-DLP-03002 | Clean the all cable tray in SS-02 after cable pulling | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-06-06 | 2023-03-30 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03345.01 | 800.00 | 1304-12-18 | Aux | EGAT-HEC-900-ELE-DLP-06002 | FACP to JB Cable tag mismatch with cable schedule clarify it and provide correct tag as per schedule | A | EL | HEC EL Construction | Mr. Michal Cwiklak | 2022-07-21 | 2022-12-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03540.01 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-ELE-DGA-00002 | Missing device to be provide in PAGA Cabinet | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-30 | 2023-03-17 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03540.02 | 800.00 | 1304-12-18 | 1000-SS-02 | EGAT-HEC-900-ELE-DGA-00002 | Earthing connection to be provided | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-30 | 2023-03-17 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04077.01 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Provide Panel name tag. | C | EL |  | Mr. Arkadiusz Tryniszewski | 2022-08-31 | 2023-04-03 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04077.02 | 800.00 | 1304-12-18 | SS-02 | EGAT-HEC-1000-ELE-DGA-00002_2 | Provide earthing connection to the main grid. | C | EL |  | Mr. Arkadiusz Tryniszewski | 2022-08-31 | 2023-03-24 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04388.01 | 800.00 | 1304-12-18 | SS-02 | V-SPL-E02-000-00000-000382_2 | Emergency switch is not working, not connected | C | EL |  | Mr. Arkadiusz Tryniszewski | 2022-11-22 | 2023-04-24 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04388.02 | 800.00 | 1304-12-18 | SS-02 | V-SPL-E02-000-00000-00382_2 | Capacitor test is not performed | B | EL |  | Mr. Arkadiusz Tryniszewski | 2022-11-22 | 2022-11-23 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04388.03 | 800.00 | 1304-12-18 | SS-02 | V-SPL-E02-000-00000-00382_2 | PFC Regulator settings is not available | B | EL |  | Mr. Arkadiusz Tryniszewski | 2022-11-22 | 2022-11-23 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-00326.01 | 800.00 | 1304-12-18 | 1000-SS-02 | PW Installation | Lack of acess to PW valve - cable room | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2021-12-10 | 2022-03-31 | Construction | 2021-12-21 |  |  |  | V | EGAT-RFI-HV-JW-00326 |  |  | Construction
. | EGAT-RFI-HV-JW-00326.02 | 800.00 | 1304-12-18 | 1000-SS-02 | PW Installation | Lack od sealing pipe entering to building - cable room | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2021-12-10 | 2022-03-24 | Construction | 2021-12-21 |  |  |  | V | EGAT-RFI-HV-JW-00326 |  |  | Construction
. | EGAT-RFI-HV-JW-00326.03 | 800.00 | 1304-12-18 | 1000-SS-02 | PW Installation | To be installed missing clamps on PW - 1st floor | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2021-12-10 | 2022-03-08 | Construction | 2021-12-21 |  |  |  | V | EGAT-RFI-HV-JW-00326 |  |  | Construction
. | EGAT-RFI-HV-JW-00326.04 | 800.00 | 1304-12-18 | 1000-SS-02 | PW Installation | To be fixed metal profiles for PW installation - 2nd floor | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2021-12-10 | 2022-03-24 | Construction | 2021-12-21 |  |  |  | V | EGAT-RFI-HV-JW-00326 |  |  | Construction
. | EGAT-RFI-HV-JW-00326.05 | 800.00 | 1304-12-18 | 1000-SS-02 | PW Installation | To be fixed installation in vertical and horizontal position | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2021-12-10 | 2022-02-15 | Construction | 2021-12-21 |  |  |  | V | EGAT-RFI-HV-JW-00326 |  |  | Construction
. | EGAT-RFI-HV-JW-00326.06 | 800.00 | 1304-12-18 | 1000-SS-02 | PW Installation | PW in cable room should be procected against frost | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2021-12-10 | 2022-03-31 | Construction | 2021-12-21 |  |  |  | V | EGAT-RFI-HV-JW-00326 |  |  | Construction
. | EGAT-RFI-HV-JW-00369.01 | 800.00 | 1304-12-18 | 1000-SS-02 | PW Installation | To be fixed assembly of pipes under cable tray | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-01-10 | 2022-02-15 | Construction | 2022-01-14 |  |  |  | V | EGAT-RFI-HV-JW-00369 |  |  | Construction
. | EGAT-RFI-HV-JW-00369.02 | 800.00 | 1304-12-18 | 1000-SS-02 | PW Installation | To be modifield PW pipe to get proper distance from cable trays | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-01-10 | 2022-02-15 | Construction | 2022-01-14 |  |  |  | V | EGAT-RFI-HV-JW-00369 |  |  | Construction
. | EGAT-RFI-HV-JW-00369.03 | 800.00 | 1304-12-18 | 1000-SS-02 | PW Installation | To be installed strainer on PW pipe | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-01-10 | 2022-02-15 | Construction | 2022-01-14 |  |  |  | V | EGAT-RFI-HV-JW-00369 |  |  | Construction
. | EGAT-RFI-HV-JW-00427.01 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG pipe installation | To be cleaned external connections of brainzing | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-01 | Construction | 2022-02-16 |  |  |  | V | EGAT-RFI-HV-JW-00427 |  |  | Construction
. | EGAT-RFI-HV-JW-00427.02 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG pipe installation | To be fixed cabling and refrigerant pipes next to equipment - wraping | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2023-01-16 | Construction | 2022-02-16 | category changed A-> B (2022-04-14) evidence attached |  |  | V | EGAT-RFI-HV-JW-00427 |  |  | Construction
. | EGAT-RFI-HV-JW-00427.03 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG pipe installation | To be checked radius of bending pipes | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-04-11 | Construction | 2022-02-16 |  |  |  | V | EGAT-RFI-HV-JW-00427 |  |  | Construction
. | EGAT-RFI-HV-JW-00427.04 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG pipe installation | To be fixed clamping pipes to cable trays | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-01 | Construction | 2022-02-16 |  |  |  | V | EGAT-RFI-HV-JW-00427 |  |  | Construction
. | EGAT-RFI-HV-JW-00428.01 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG pipe installation | To be cleaned external connections of brainzing | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-01 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00428 |  |  | Construction
. | EGAT-RFI-HV-JW-00428.02 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG pipe installation | To be fixed cabling and refrigerant pipes next to equipment - wraping | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2023-01-16 | Construction | 2022-02-14 | category changed A-> B (2022-04-14) evidence attached |  |  | V | EGAT-RFI-HV-JW-00428 |  |  | Construction
. | EGAT-RFI-HV-JW-00428.03 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG pipe installation | To be checked radius of bending pipes | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-04-11 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00428 |  |  | Construction
. | EGAT-RFI-HV-JW-00428.04 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG pipe installation | To be fixed clamping pipes to cable trays | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-24 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00428 |  |  | Construction
. | EGAT-RFI-HV-JW-00429.01 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG pipe installation | To be cleaned external connections of brainzing | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-01 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00429 |  |  | Construction
. | EGAT-RFI-HV-JW-00429.02 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG pipe installation | To be fixed cabling and refrigerant pipes next to equipment - wraping | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2023-01-16 | Construction | 2022-02-14 | category changed A-> B (2022-04-14) evidence attached |  |  | V | EGAT-RFI-HV-JW-00429 |  |  | Construction
. | EGAT-RFI-HV-JW-00429.03 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG pipe installation | To be checked radius of bending pipes | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-04-11 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00429 |  |  | Construction
. | EGAT-RFI-HV-JW-00429.04 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG pipe installation | To be fixed elbow with pipe 90 degree next to one unit on roof | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-01 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00429 |  |  | Construction
. | EGAT-RFI-HV-JW-00429.05 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG pipe installation | To be fixed clamping pipes to cable trays | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-08 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00429 |  |  | Construction
. | EGAT-RFI-HV-JW-00431.01 | 800.00 | 1304-12-18 | 1000-SS-02 | ED Pipe Installation | To be clarified fire crossings pipe thru all building partitions | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-07 | 2022-04-14 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00431 |  |  | Construction
. | EGAT-RFI-HV-JW-00432.01 | 800.00 | 1304-12-18 | 1000-SS-02 | ED Pipe Installation | To be clarified fire crossings pipe thru all building partitions | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-07 | 2022-04-14 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00432 |  |  | Construction
. | EGAT-RFI-HV-JW-00436.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Fan Installation | To be added anchor bolt on top of both fans | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-24 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00436 |  |  | Construction
. | EGAT-RFI-HV-JW-00436.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Fan Installation | To be cut bolts - both fans | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-24 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00436 |  |  | Construction
. | EGAT-RFI-HV-JW-00436.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Fan Installation | To be added bolt with nut for assembly a louver | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-24 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00436 |  |  | Construction
. | EGAT-RFI-HV-JW-00436.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Fan Installation | To be finished sealing on one of a fan | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-24 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00436 |  |  | Construction
. | EGAT-RFI-HV-JW-00437.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Fan Installation | To be clarified location of installed sensors of PDS acc. to DWG PiD | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2023-06-02 | Construction | 2022-02-14 | category changed A-> B (2022-04-11) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-00437 |  |  | Construction
. | EGAT-RFI-HV-JW-00438.01 | 800.00 | 1304-12-18 | 1000-SS-02 | SAC Installation | To be installed rubber washers for SAC - UPS 2 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-10 | 2022-04-04 | Construction | 2022-02-16 | category changed A-> B (2022-03-24) evidence attached |  |  | V | EGAT-RFI-HV-JW-00438 |  |  | Construction
. | EGAT-RFI-HV-JW-00438.02 | 800.00 | 1304-12-18 | 1000-SS-02 | SAC Installation | Instruments cables not connected to SAC - UPS 2 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-10 | 2022-03-31 | Construction | 2022-02-16 |  |  |  | V | EGAT-RFI-HV-JW-00438 |  |  | Construction
. | EGAT-RFI-HV-JW-00438.03 | 800.00 | 1304-12-18 | 1000-SS-02 | SAC Installation | Drainage trays to be cleaned from traces of corrosion | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-10 | 2022-03-24 | Construction | 2022-02-16 | category changed A-> B (2022-03-24) evidence attached |  |  | V | EGAT-RFI-HV-JW-00438 |  |  | Construction
. | EGAT-RFI-HV-JW-00438.04 | 800.00 | 1304-12-18 | 1000-SS-02 | SAC Installation | To be fixed fins at evaporations in SAC - UPS 1 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-10 | 2022-04-05 | Construction | 2022-02-16 |  |  |  | V | EGAT-RFI-HV-JW-00438 |  |  | Construction
. | EGAT-RFI-HV-JW-00438.05 | 800.00 | 1304-12-18 | 1000-SS-02 | SAC Installation | To be chec location of SAC due of close location to electrical gabinet - UPS 1 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-10 | 2022-04-14 | Construction | 2022-02-16 |  |  |  | V | EGAT-RFI-HV-JW-00438 |  |  | Construction
. | EGAT-RFI-HV-JW-00447.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Installation | Opening for ductworks going to roof are to small - MV room. | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2023-03-20 | Construction | 2022-02-14 | category changed A-> B (2022-03-24) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-00447 |  |  | Construction
. | EGAT-RFI-HV-JW-00447.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Installation | Lack of sealing ducts between MV and LV room | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-08 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00447 |  |  | Construction
. | EGAT-RFI-HV-JW-00447.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Installation | Lack of inspection revision - Fire dampers | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2023-01-02 | Construction | 2022-02-14 | category changed A-> B (2022-04-04) evidence attached |  |  | V | EGAT-RFI-HV-JW-00447 |  |  | Construction
. | EGAT-RFI-HV-JW-00447.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Installation | Lack of inspection verision (acces doors) for cleaning ducts - acc. To PN-EN | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2023-01-02 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00447 |  |  | Construction
. | EGAT-RFI-HV-JW-00448.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Installation | Flexible connection are too stiff, required loose - HVAC Room. | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-08 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00448 |  |  | Construction
. | EGAT-RFI-HV-JW-00448.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Installation | To be filled and sealed gaps around ducts- battery and HVAC room | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-31 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00448 |  |  | Construction
. | EGAT-RFI-HV-JW-00448.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Installation | Lack of inspection revision - Fire dampers | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2023-01-02 | Construction | 2022-02-14 | category changed A-> B (2022-04-04) evidence attached |  |  | V | EGAT-RFI-HV-JW-00448 |  |  | Construction
. | EGAT-RFI-HV-JW-00448.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Installation | Lack of access doors for cleaning the ducts - acc. To. PW-EN | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2023-01-02 | Construction | 2022-02-14 | category changed A-> B (2022-04-04) evidence attached |  |  | V | EGAT-RFI-HV-JW-00448 |  |  | Construction
. | EGAT-RFI-HV-JW-00450.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Support Installation | Threaded rods, profiles to be adjusted - all rooms | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-24 | Construction | 2022-02-14 | category changed A-> B (2022-03-24) evidence attached |  |  | V | EGAT-RFI-HV-JW-00450 |  |  | Construction
. | EGAT-RFI-HV-JW-00451.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Support Installation | Threaded rods, profiles to be adjusted - all rooms | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-03-24 | Construction | 2022-02-14 | category changed A-> B (2022-03-24) evidence attached |  |  | V | EGAT-RFI-HV-JW-00451 |  |  | Construction
. | EGAT-RFI-HV-JW-00452.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Support Installation | Support structures are not acc. to DWG - Roof. | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2023-01-13 | Construction | 2022-02-14 | category changed A-> B (2022-03-24) evidence attached |  |  | V | EGAT-RFI-HV-JW-00452 |  |  | Construction
. | EGAT-RFI-HV-JW-00452.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Support Installation | Lack of rubber gaskets under ducts without insulation | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-02-24 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00452 |  |  | Construction
. | EGAT-RFI-HV-JW-00452.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Support Installation | To be fixed support for Intake louver, proper level, rubber gusket, move from flange | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-02-24 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00452 |  |  | Construction
. | EGAT-RFI-HV-JW-00452.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Support Installation | Profiles and threaded rods to be adjusted | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-09 | 2022-02-24 | Construction | 2022-02-14 |  |  |  | V | EGAT-RFI-HV-JW-00452 |  |  | Construction
. | EGAT-RFI-HV-JW-00475.01 | 800.00 | 1304-12-18 | 1000-SS-02 | ED Insulation | To be added insulation on clamp band next to SAC - UPS 2 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-18 | 2022-03-08 | Construction | 2022-02-23 |  |  |  | V | EGAT-RFI-HV-JW-00475 |  |  | Construction
. | EGAT-RFI-HV-JW-00475.02 | 800.00 | 1304-12-18 | 1000-SS-02 | ED Insulation | To be claryfied fire crossing pipes thru building partition - fire - non fire rated wall | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-18 | 2022-04-14 | Construction | 2022-02-23 |  |  |  | V | EGAT-RFI-HV-JW-00475 |  |  | Construction
. | EGAT-RFI-HV-JW-00476.01 | 800.00 | 1304-12-18 | 1000-SS-02 | ED Insulation | To be fixed small mechanical damages on insulation - HVAC room | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-18 | 2022-03-24 | Construction | 2022-02-23 | category changed A-> B (2022-03-24) evidence attached |  |  | V | EGAT-RFI-HV-JW-00476 |  |  | Construction
. | EGAT-RFI-HV-JW-00476.02 | 800.00 | 1304-12-18 | 1000-SS-02 | ED Insulation | To be claryfied fire crossing pipes thru building partition - fire - non fire rated wall | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-18 | 2022-04-14 | Construction | 2022-02-23 |  |  |  | V | EGAT-RFI-HV-JW-00476 |  |  | Construction
. | EGAT-RFI-HV-JW-00476.03 | 800.00 | 1304-12-18 | 1000-SS-02 | ED Insulation | To be cleaned insulation from dust, paint etc. | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-18 | 2022-04-29 | Construction | 2022-02-23 |  |  |  | V | EGAT-RFI-HV-JW-00476 |  |  | Construction
. | EGAT-RFI-HV-JW-00499.01 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG Pipe Insulation | To be fixed lack of insulation on pipes | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-28 | 2022-03-31 | Construction | 2022-03-04 |  |  |  | V | EGAT-RFI-HV-JW-00499 |  |  | Construction
. | EGAT-RFI-HV-JW-00499.02 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG Pipe Insulation | To be fixed connection of cut insulation, proper wrapping | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-28 | 2022-03-31 | Construction | 2022-03-04 |  |  |  | V | EGAT-RFI-HV-JW-00499 |  |  | Construction
. | EGAT-RFI-HV-JW-00499.03 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG Pipe Insulation | To be fixed insulation next to equipment | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-28 | 2022-03-24 | Construction | 2022-03-04 |  |  |  | V | EGAT-RFI-HV-JW-00499 |  |  | Construction
. | EGAT-RFI-HV-JW-00499.04 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG Pipe Insulation | To be fixed unglued black tapes | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-28 | 2022-03-24 | Construction | 2022-03-04 |  |  |  | V | EGAT-RFI-HV-JW-00499 |  |  | Construction
. | EGAT-RFI-HV-JW-00500.01 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG Pipe Insulation | To be fixed lack of insulation on pipes | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-28 | 2022-03-24 | Construction | 2022-03-04 |  |  |  | V | EGAT-RFI-HV-JW-00500 |  |  | Construction
. | EGAT-RFI-HV-JW-00500.02 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG Pipe Insulation | To be fixed connection of cut insulaion, proper wrapping | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-28 | 2022-03-24 | Construction | 2022-03-04 |  |  |  | V | EGAT-RFI-HV-JW-00500 |  |  | Construction
. | EGAT-RFI-HV-JW-00500.03 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG Pipe Insulation | To be fixed insulation next to equipment | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-28 | 2022-03-24 | Construction | 2022-03-04 |  |  |  | V | EGAT-RFI-HV-JW-00500 |  |  | Construction
. | EGAT-RFI-HV-JW-00500.04 | 800.00 | 1304-12-18 | 1000-SS-02 | RL/RG Pipe Insulation | To be fixed unglued black tapes | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-02-28 | 2022-03-24 | Construction | 2022-03-04 |  |  |  | V | EGAT-RFI-HV-JW-00500 |  |  | Construction
. | EGAT-RFI-HV-JW-00554.01 | 800.00 | 1304-12-18 | 1000-SS-02 | AHU Installation | To be connected electric louver in all AHU | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-22 | 2022-04-14 | Construction | 2022-03-29 |  |  |  | V | EGAT-RFI-HV-JW-00554 |  |  | Construction
. | EGAT-RFI-HV-JW-00554.02 | 800.00 | 1304-12-18 | 1000-SS-02 | AHU Installation | To be provide access to all AHU | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-22 |  | Construction | 2022-03-29 |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00554 |  |  | Construction
. | EGAT-RFI-HV-JW-00554.03 | 800.00 | 1304-12-18 | 1000-SS-02 | AHU Installation | To be translated description into polish language - all AHU | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-22 | 2023-02-07 | Construction | 2022-03-29 |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00554 |  |  | Construction
. | EGAT-RFI-HV-JW-00554.04 | 800.00 | 1304-12-18 | 1000-SS-02 | AHU Installation | To be corrected drain for AHU 002 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-22 | 2022-04-14 | Construction | 2022-03-29 | category changed A-> B (2022-04-11) evidence attached |  |  | V | EGAT-RFI-HV-JW-00554 |  |  | Construction
. | EGAT-RFI-HV-JW-00554.05 | 800.00 | 1304-12-18 | 1000-SS-02 | AHU Installation | To be clarified assembly of actuators on dampers | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-22 | 2022-04-14 | Construction | 2022-03-29 |  |  |  | V | EGAT-RFI-HV-JW-00554 |  |  | Construction
. | EGAT-RFI-HV-JW-00554.06 | 800.00 | 1304-12-18 | 1000-SS-02 | AHU Installation | Surface damages point | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-22 | 2023-03-20 | Construction | 2022-03-29 | category changed A-> B (2022-04-11) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-00554 |  |  | Construction
. | EGAT-RFI-HV-JW-00558.01 | 800.00 | 1304-12-18 | 1000-SS-02 | HVAC Control System | Please provide IR and continuity test reports | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-06 | 2022-04-14 | Construction | 2022-04-11 |  |  |  | V | EGAT-RFI-HV-JW-00558 |  |  | Construction
. | EGAT-RFI-HV-JW-00559.01 | 800.00 | 1304-12-18 | 1000-SS-02 | HVAC Control System | Please provide IR and continuity test reports | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-06 | 2022-04-14 | Construction | 2022-04-11 |  |  |  | V | EGAT-RFI-HV-JW-00559 |  |  | Construction
. | EGAT-RFI-HV-JW-00560.01 | 800.00 | 1304-12-18 | 1000-SS-02 | HVAC Control System | Please provide IR and continuity test reports | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-06 | 2022-04-14 | Construction | 2022-04-11 |  |  |  | V | EGAT-RFI-HV-JW-00560 |  |  | Construction
. | EGAT-RFI-HV-JW-00561.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Control Panel Installation | To be translated into PL description of all switches on from panel | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-07 | 2023-03-20 | Construction | 2022-04-11 |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00561 |  |  | Construction
. | EGAT-RFI-HV-JW-00562.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | To be cleaning insulation on RL/RG pipes | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-28 | 2023-01-16 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-HV-JW-00562 |  |  | Construction
. | EGAT-RFI-HV-JW-00562.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | Jacketing is not done | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-28 | 2023-03-28 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-HV-JW-00562 |  |  | Construction
. | EGAT-RFI-HV-JW-00567.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | To be cleaned all ductwork insulation | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-28 | 2023-01-16 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-HV-JW-00567 |  |  | Construction
. | EGAT-RFI-HV-JW-00567.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | To be removed mechanical damages on insulation | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-28 | 2023-01-16 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-HV-JW-00567 |  |  | Construction
. | EGAT-RFI-HV-JW-00567.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | To be fixed silver tape where is missing or peel off | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-28 | 2022-04-05 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-HV-JW-00567 |  |  | Construction
. | EGAT-RFI-HV-JW-00567.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | To be removed remaining plastic foils from insulation, supports etc. | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-28 | 2022-07-28 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-HV-JW-00567 |  |  | Construction
. | EGAT-RFI-HV-JW-00568.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | To be cleaned all ductwork insulation | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-28 | 2022-04-29 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-HV-JW-00568 |  |  | Construction
. | EGAT-RFI-HV-JW-00568.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | To be removed mechanical damages on insulation | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-28 | 2023-01-16 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-HV-JW-00568 |  |  | Construction
. | EGAT-RFI-HV-JW-00568.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | To be fixed silver tape where is missing or peel off | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-28 | 2022-04-05 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-HV-JW-00568 |  |  | Construction
. | EGAT-RFI-HV-JW-00568.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | To be removed remaining plastic foils from insulation, support etc. | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-28 | 2022-04-29 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-HV-JW-00568 |  |  | Construction
. | EGAT-RFI-HV-JW-00568.05 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | To be corrected gluing insulation on flanges - HVAC Room | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-28 | 2022-04-05 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-HV-JW-00568 |  |  | Construction
. | EGAT-RFI-HV-JW-00568.06 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | To be corrected flexible connection on nozzles from main duct - Rack Room | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-28 | 2022-04-14 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-HV-JW-00568 |  |  | Construction
. | EGAT-RFI-HV-JW-00568.07 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | To be fixed threded rods and support - Air lock Room | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-03-28 | 2022-04-14 | Construction | 2022-03-30 |  |  |  | V | EGAT-RFI-HV-JW-00568 |  |  | Construction
. | EGAT-RFI-HV-JW-00570.01 | 800.00 | 1304-12-18 | 1000-SS-02 | ACCU Installation | To be corrected cables in ACCU - lack of conduits | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-04 | 2023-06-05 | Construction | 2022-04-06 |  |  |  | V | EGAT-RFI-HV-JW-00570 |  |  | Construction
. | EGAT-RFI-HV-JW-00575.01 | 800.00 | 1304-12-18 | 1000-SS-02 | PW pipe installation | To be removed value and install PRV | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-04 | 2022-04-29 | Construction | 2022-04-06 |  |  |  | V | EGAT-RFI-HV-JW-00575 |  |  | Construction
. | EGAT-RFI-HV-JW-00588.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | Before installing jaceting, the moisture of the insulation should be checked on a regular basis. Wet insulation elements should be removed. | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-06 | 2022-07-01 | Construction | 2022-04-08 |  |  |  | V | EGAT-RFI-HV-JW-00588 |  |  | Construction
. | EGAT-RFI-HV-JW-00596.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | To be corrected assembly of metal sheet on bottom of louver - Room No. 6 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2022-04-14 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00596 |  |  | Construction
. | EGAT-RFI-HV-JW-00596.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | To be corrected paint on louver - outside - Room No. 6 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2023-01-02 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00596 |  |  | Construction
. | EGAT-RFI-HV-JW-00597.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | Lack of indicator of Open and Closed position on dampers LV Room | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2022-04-14 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00597 |  |  | Construction
. | EGAT-RFI-HV-JW-00597.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | Lack of acces to MFD installed under ceiling - MV Room | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2022-07-28 | Construction | 2022-04-13 | category changed A-> B (2022-04-26) evidence attached |  |  | V | EGAT-RFI-HV-JW-00597 |  |  | Construction
. | EGAT-RFI-HV-JW-00597.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | Lack of access doors for cleaning ducts acc. PN-EN | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2023-03-20 | Construction | 2022-04-13 |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00597 |  |  | Construction
. | EGAT-RFI-HV-JW-00598.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Accessory Installation | Lack of indicator of Open and Closed position on dampers Battery Room | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2022-04-14 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00598 |  |  | Construction
. | EGAT-RFI-HV-JW-00598.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Accessory Installation | Lack of access doors for cleaning ducts acc. PN-EN | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2023-03-23 | Construction | 2022-04-13 |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00598 |  |  | Construction
. | EGAT-RFI-HV-JW-00599.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Accessory Installation | Lack of indicator of Open and Closed position on dampers Battery Room | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2022-04-14 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00599 |  |  | Construction
. | EGAT-RFI-HV-JW-00599.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Accessory Installation | Lack of access doors for cleaning ducts acc. PN-EN | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2023-03-07 | Construction | 2022-04-13 |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00599 |  |  | Construction
. | EGAT-RFI-HV-JW-00600.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | To be cleaned insulation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2022-07-28 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00600 |  |  | Construction
. | EGAT-RFI-HV-JW-00600.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | To be corrected of peeling off black tapes | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2022-07-28 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00600 |  |  | Construction
. | EGAT-RFI-HV-JW-00600.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | To be correced mechanical damages | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2022-07-28 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00600 |  |  | Construction
. | EGAT-RFI-HV-JW-00601.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | To be cleaned insulation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2022-04-14 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00601 |  |  | Construction
. | EGAT-RFI-HV-JW-00601.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | To be corrected of peeling off black tapes | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2023-01-16 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00601 |  |  | Construction
. | EGAT-RFI-HV-JW-00601.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | To be correced mechanical damages | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2022-04-14 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00601 |  |  | Construction
. | EGAT-RFI-HV-JW-00602.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | To be cleaned insulation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2022-04-14 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00602 |  |  | Construction
. | EGAT-RFI-HV-JW-00602.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | To be corrected of peeling off black tapes | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2022-04-14 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00602 |  |  | Construction
. | EGAT-RFI-HV-JW-00602.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Pipe Insulation | To be correced mechanical damages | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-11 | 2022-04-14 | Construction | 2022-04-13 |  |  |  | V | EGAT-RFI-HV-JW-00602 |  |  | Construction
. | EGAT-RFI-HV-JW-00604.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Fire Extinguisher installation | To be provided DWG in rev. 4 with actual location of potable extinguisher | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-19 | 2022-06-03 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-HV-JW-00604 |  |  | Construction
. | EGAT-RFI-HV-JW-00605.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Fire Extinguisher installation | To be provided DWG in rev. 3 with actual location of potable extinguisher | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-19 | 2022-06-03 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-HV-JW-00605 |  |  | Construction
. | EGAT-RFI-HV-JW-00610.01 | 800.00 | 1304-12-18 | 1000-SS-02 | PW Pipe Insulation | To be installed jacketing and inspection required | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-20 | 2022-04-29 | Construction | 2022-04-21 |  |  |  | V | EGAT-RFI-HV-JW-00610 |  |  | Construction
. | EGAT-RFI-HV-JW-00612.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | To be removed bottom parts of jackeing on indicated location of ductwork | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-20 | 2022-07-01 | Construction | 2022-04-21 | category changed A-> B (2022-04-28) evidence attached |  |  | V | EGAT-RFI-HV-JW-00612 |  |  | Construction
. | EGAT-RFI-HV-JW-00612.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Duct Insulation | To be sealed gaps between ductwork and AMW | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-04-20 | 2022-04-29 | Construction | 2022-04-21 |  |  |  | V | EGAT-RFI-HV-JW-00612 |  |  | Construction
. | EGAT-RFI-HV-JW-01422.01 | 800.00 | 1304-12-18 | 1000-SS-02 | Hvac Acceptance Inspection | Installation not connected to Fas | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-03-15 | 2023-03-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01422.02 | 800.00 | 1304-12-18 | 1000-SS-02 | Hvac Acceptance Inspection | Provide start-up report (point11) | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-03-15 | 2023-04-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01422.03 | 800.00 | 1304-12-18 | 1000-SS-02 | Hvac Acceptance Inspection | Points 2, 11 was not made, filters need to be changed (dirty) | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-03-15 | 2023-04-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01422.04 | 800.00 | 1304-12-18 | 1000-SS-02 | Hvac Acceptance Inspection | Points 2, 7, 10, 11 was not made | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-03-15 | 2023-05-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01422.05 | 800.00 | 1304-12-18 | 1000-SS-02 | Hvac Acceptance Inspection | Provide manufacturer start-up report (point 9) | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-03-15 | 2023-05-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01422.06 | 800.00 | 1304-12-18 | 1000-SS-02 | Hvac Acceptance Inspection | Point 6 was not made | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-03-15 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-SS-MK-01168.01 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 (Axis 1A-11A/A-E) | Curved toe - plates of the handrailings | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-15 | 2022-07-11 | Construction | 2022-02-17 |  |  |  | V | EGAT-RFI-SS-MK-01168 |  |  | Construction
. | EGAT-RFI-SS-MK-01168.02 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 (Axis 1A-11A/A-E) | Bent rungs | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-15 | 2022-07-11 | Construction | 2022-02-17 |  |  |  | V | EGAT-RFI-SS-MK-01168 |  |  | Construction
. | EGAT-RFI-SS-MK-01168.03 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 (Axis 1A-11A/A-E) | Closing not secured of slipping | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-15 | 2022-07-11 | Construction | 2022-02-17 |  |  |  | V | EGAT-RFI-SS-MK-01168 |  |  | Construction
. | EGAT-RFI-SS-MK-01168.04 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 (Axis 1A-11A/A-E) | Handrailing to adjust | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-15 |  | Construction | 2022-02-17 |  |  |  |  | EGAT-RFI-SS-MK-01168 |  |  | Construction
. | EGAT-RFI-SS-MK-01168.05 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 (Axis 1A-11A/A-E) | Touch up painting | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-15 |  | Construction | 2022-02-17 |  |  |  |  | EGAT-RFI-SS-MK-01168 |  |  | Construction
. | EGAT-RFI-SS-MK-01168.06 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 (Axis 1A-11A/A-E) | Circural rungs of ladders | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-15 | 2023-05-17 | Construction | 2022-02-17 |  |  |  | V | EGAT-RFI-SS-MK-01168 |  |  | Construction
. | EGAT-RFI-SS-MK-01168.07 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 (Axis 1A-11A/A-E) | Open NCR AR070 | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-18 |  | Construction | 2022-02-18 |  |  |  |  | EGAT-RFI-SS-MK-01168 |  |  | Construction
. | EGAT-RFI-SS-MK-01188.01 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 | Open NCR AR070 | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-04 | 2022-12-29 | Construction | 2022-03-11 |  |  |  | V | EGAT-RFI-SS-MK-01188 |  |  | Construction
. | EGAT-RFI-SS-MK-01188.02 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 | Circular rungs of ladders | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-04 | 2022-12-29 | Construction | 2022-03-11 |  |  |  | V | EGAT-RFI-SS-MK-01188 |  |  | Construction
. | EGAT-RFI-SS-MK-01188.03 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 | Touch up painting | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-04 | 2022-12-29 | Construction | 2022-03-11 |  |  |  | V | EGAT-RFI-SS-MK-01188 |  |  | Construction
. | EGAT-RFI-SS-MK-01188.04 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 | Handrailings to adjust | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-04 | 2022-12-29 | Construction | 2022-03-11 |  |  |  | V | EGAT-RFI-SS-MK-01188 |  |  | Construction
. | EGAT-RFI-SS-MK-01188.05 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 | Closing not secure of slipping | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-04 | 2022-04-19 | Construction | 2022-03-11 |  |  |  | V | EGAT-RFI-SS-MK-01188 |  |  | Construction
. | EGAT-RFI-SS-MK-01188.06 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 | Bent rungs | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-04 | 2022-07-11 | Construction | 2022-03-11 |  |  |  | V | EGAT-RFI-SS-MK-01188 |  |  | Construction
. | EGAT-RFI-SS-MK-01188.07 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 | Curved toe-plates of the handrailings | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-04 | 2022-07-11 | Construction | 2022-03-11 |  |  |  | V | EGAT-RFI-SS-MK-01188 |  |  | Construction
. | EGAT-RFI-SS-MK-01188.08 | 800.00 | 1304-12-18 | AUX | 1000-SS-02 | Ground handrailings are not fasted properly - move | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-04 |  | Construction | 2022-03-11 |  |  |  |  | EGAT-RFI-SS-MK-01188 |  |  | Construction
. | NCR-EL075.01 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-MCC-01A/B | Control cables are pulled from bottom to top on the left side of the panel fastened by plastic ties | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-05-21 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | NCR-EL079.01 | 800.00 | 1304-12-18 | 1000-SS-02 | 02-SWG-02-1A/B | Installation of the Core-balanced CT in MV switchgear is not proper | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-05-21 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21489 | 800.00 | 1304-10-14 | 820-SHT-SH-300 Steam Turbine Generator Shelter | Cladding | Openings in the cladding shall be covered with flashings. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-04 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 21490 | 800.00 | 1304-10-14 | 820-SHT-SH-300 Steam Turbine Generator Shelter | Safety | Missing safety rope system on the roof. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-04 | 2023-01-31 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21491 | 800.00 | 1304-10-14 | 820-SHT-SH-300 Steam Turbine Generator Shelter | Cladding | Roof sheets partially corroded, must be cleaned or exchange. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-04 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 21492 | 800.00 | 1304-10-14 | 820-SHT-SH-300 Steam Turbine Generator Shelter | Cladding | Damaged cladding must be exchanged. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-04 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 21493 | 800.00 | 1304-10-14 | 820-SHT-SH-300 Steam Turbine Generator Shelter | General | Limited functionality of the overhead crane and the loading bay, caused by the inability to pass the crane behind the platform +104.500 due to the collision of its motor with the service platform +112.600. | C | ME | HEC ME Construction | Mr. Sebastian Stępień | 2023-01-04 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 21494 | 800.00 | 1304-10-14 | 820-SHT-SH-300 Steam Turbine Generator Shelter | General | Steel structures must be cleaned and touch-up painting must be done. | C | SS | HEC SS Construction | Mr. Sebastian Stępień | 2023-01-04 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 21495 | 800.00 | 1304-10-14 | 820-SHT-SH-300 Steam Turbine Generator Shelter | Safety | All ditches and ducts must be covered. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-04 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 21496 | 800.00 | 1304-10-14 | 820-SHT-SH-300 Steam Turbine Generator Shelter | General | Rainwater system must be finished. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-04 | 2023-03-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 21497 | 800.00 | 1304-10-14 | 820-SHT-SH-300 Steam Turbine Generator Shelter | Safety | Gratings must be properly fixed, adjusted, rest of gratings must be removed from platforms. | C | SS | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-04 | 2023-02-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21498 | 800.00 | 1304-10-14 | 820-SHT-SH-300 Steam Turbine Generator Shelter | General | Handrail is not a load-bearing element. Fixing of any other installation to them shall be approved by construction designer. | C | EM | HEC EL Design | Mr. Sebastian Stępień | 2023-01-04 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 21499 | 800.00 | 1304-10-14 | 820-SHT-SH-300 Steam Turbine Generator Shelter | Cladding | Flashings must be finished. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-04 | 2023-03-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 21500 | 800.00 | 1304-10-14 | 820-SHT-SH-300 Steam Turbine Generator Shelter | Safety | Ladder not fixed to the platform, it's very unstable. | C | SS | HEC SS Construction | Mr. Sebastian Stępień | 2023-01-04 | 2023-02-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21501 | 800.00 | 1304-10-14 | Steam Turbine Generator shelter(820-SHT-SH-300) | EGAT-HEC-900-ELE-DLP-04017, EGAT-HEC-900-ELE-DLP-05002 | Plastic reducers to be replace with Metal reducers for lighting fixtures at steel structure column mounted | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-04 | 2023-03-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21502 | 800.00 | 1304-10-14 | Steam Turbine Generator shelter(820-SHT-SH-300) | EGAT-HEC-900-ELE-DLP-04017, EGAT-HEC-900-ELE-DLP-05002 | Lighting Fixture cable tag is missing to be provided. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-04 | 2023-03-16 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21503 | 800.00 | 1304-10-14 | Steam Turbine Generator shelter(820-SHT-SH-300) | EGAT-HEC-900-ELE-DLP-04017, EGAT-HEC-900-ELE-DLP-05002 | Tag no- 820-B0004-MP01A/1B earthing to be tightned. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-04 | 2023-02-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21504 | 800.00 | 1304-10-14 | Steam Turbine Generator shelter(820-SHT-SH-300) | EGAT-HEC-900-ELE-DLP-04017, EGAT-HEC-900-ELE-DLP-05002 | Lighting Junction box and lIghting fixture tags to be provided. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-04 | 2023-03-16 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21505 | 800.00 | 1304-10-14 | Steam Turbine Generator shelter(820-SHT-SH-300) | EGAT-HEC-900-ELE-DLP-04017, EGAT-HEC-900-ELE-DLP-05002 | Tag no- 820-B0004-MW01A/B for LCS cable SS ties to be install . | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-04 | 2023-03-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21506 | 800.00 | 1304-10-14 | Steam Turbine Generator shelter(820-SHT-SH-300) | EGAT-HEC-900-ELE-DLP-04017, EGAT-HEC-900-ELE-DLP-05002 | Stub-up conduit duct sealing to be provided. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-04 | 2023-03-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21507 | 800.00 | 1304-10-14 | Steam Turbine Generator shelter(820-SHT-SH-300) | EGAT-HEC-900-ELE-DLP-04017, EGAT-HEC-900-ELE-DLP-05002 | Lighting fixture Blind plug to be provided instead of PVC gland. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-04 | 2023-03-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21508 | 800.00 | 1304-10-14 | Steam Turbine Generator shelter(820-SHT-SH-300) | EGAT-HEC-900-ELE-DLP-04017, EGAT-HEC-900-ELE-DLP-05002 | Overhead crane Isolator box equipment tag is missing and cable tag is missing. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-04 | 2023-03-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21509 | 800.00 | 1304-10-14 | Steam Turbine Generator shelter(820-SHT-SH-300) | EGAT-HEC-900-ELE-DLP-04017, EGAT-HEC-900-ELE-DLP-05002 | Lighting cable tags to be provided | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-04 | 2023-03-16 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21510 | 800.00 | 1304-10-14 | Steam Turbine Generator shelter(820-SHT-SH-300) | EGAT-HEC-900-ELE-DLP-04017, EGAT-HEC-900-ELE-DLP-05002 | illumination test to be done | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-04 | 2023-03-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21511 | 800.00 | 1304-10-14 | Steam Turbine Generator shelter(820-SHT-SH-300) | EGAT-HEC-900-INC-DLP-00012 | Tag No- 900-CAP-P07 CCTV to be installed. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-01-04 | 2023-03-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 21512 | 800.00 | 1304-10-14 | Steam Turbine Generator shelter(820-SHT-SH-300) | EGAT-HEC-900-INC-DLP-00012 | Telecommunication Sat to be done | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-01-04 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22536 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Flashing | Wall openings and ladder mounting flashing to be done/finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 22537 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Cladding | Clading demage | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 22538 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Cladding | Lack of final inspection for clading | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 22539 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Cladding | cladding of pieces on the S side facade | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22540 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Cladding | Cut clading to be anti corrosion protected | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22541 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Cladding | cladding to be cleaned from rust and protected | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22542 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Downspout | Downspout and gutter to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22543 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Ground slab | Ground slab to be grinded and repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22544 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Ground slab | Sealant ground slab-foundation to be done | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22545 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Foundations | Foundation chamfering to be done | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22546 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Ground slab | different levels of te groun slab | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22547 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Trench | Lack of trench | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22548 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Cable pit | Lack of covers on cable pit | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22549 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Roof | Lack of security system | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 22550 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Wall | Lack of door on the outer wall at the crane landing | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-03 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 22551 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | SS | Lack of final inspection for SS | C | SS | HEC SS Construction | Mr. Andrzej Misiek | 2023-01-02 | 2023-02-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22552 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | SS | SS to be cleaned | C | SS | HEC SS Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 22553 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | SS | Coating demage | C | SS | HEC SS Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 22554 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | SS | Remaining bolts to be removed | C | SS | HEC SS Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22555 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | SS | Holes in the column footings are to be filled | C | SS | HEC SS Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22556 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Balustrades | cable trays mounted to balustrades | C | EM | HEC EL Design | Mr. Andrzej Misiek | 2023-01-02 | 2023-03-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22557 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Balustrades | Bent rungs, toe plates | B | SS | HEC SS Construction | Mr. Andrzej Misiek | 2023-01-02 | 2023-01-30 | Walkdown |  |  | 2023-02-12 |  | V |  |  |  | RFC/RFSU
. | 22558 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Balustrades | Balustrade to be fastened properly | C | SS | HEC SS Construction | Mr. Andrzej Misiek | 2023-01-02 | 2023-02-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22559 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Balustrades | The gate does not close | B | SS | HEC SS Construction | Mr. Andrzej Misiek | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 22560 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Ladder | Ladder not fastened to gratings | B | SS | HEC SS Construction | Mr. Andrzej Misiek | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 22561 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Gratings | Gratings to be fastened and adjusted | C | SS | HEC SS Construction | Mr. Andrzej Misiek | 2023-01-02 | 2023-05-08 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 22562 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Gratings | Cut gratings to be finished and anticorrosion protected | B | SS | HEC SS Construction | Mr. Andrzej Misiek | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | EGAT-RFI-AR-GS-04808.01 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | EC1 columns | Surface of the concrete should be grinded | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-12-20 |  | Construction | 2022-01-11 |  |  |  | V | EGAT-RFI-AR-GS-04808 |  |  | Construction
. | EGAT-RFI-AR-GS-04808.02 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | EC1 columns | Especialy repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-12-20 |  | Construction | 2022-01-11 |  |  |  | V | EGAT-RFI-AR-GS-04808 |  |  | Construction
. | EGAT-RFI-AR-GS-04947.01 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Equipment foundation (El. 104.462) | The concrete vertical surface should be straight | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-01-19 | 2022-01-28 | Construction | 2022-01-22 |  |  |  | V | EGAT-RFI-AR-GS-04947 |  |  | Construction
. | EGAT-RFI-AR-GS-05432.01 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Axis 1-3/B-C | Galvanized corners should be procected against concrete | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-06 |  | Construction | 2022-04-15 |  |  |  | V | EGAT-RFI-AR-GS-05432 |  |  | Construction
. | EGAT-RFI-AR-GS-05432.02 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Axis 1-3/B-C | The bottom of U-ditch must have appropriate slope | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-04-06 | 2022-09-07 | Construction | 2022-04-15 |  |  |  | V | EGAT-RFI-AR-GS-05432 |  |  | Construction
. | EGAT-RFI-AR-GS-05999.01 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | EF1, EF2 | Surface of the sealing to be grinded | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-15 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-05999 |  |  | Construction
. | EGAT-RFI-AR-GS-06032.01 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Axis 1-3/ A-B | Surface to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-15 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06032 |  |  | Construction
. | EGAT-RFI-AR-GS-06034.01 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Axis 1-3/A-C | Surface of ground slab to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-15 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06034 |  |  | Construction
. | EGAT-RFI-AR-GS-06034.02 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Axis 1-3/A-C | Different levels of the ground slab | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-15 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06034 |  |  | Construction
. | EGAT-RFI-AR-GS-06034.03 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Axis 1-3/A-C | Lack of sealant | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-15 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06034 |  |  | Construction
. | EGAT-RFI-AR-GS-06036.01 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | FDN, FG, PD1, PD2, Cable trench, EF3, EP1, GS1 | Lack of chamfering | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-15 | 2022-09-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06036 |  |  | Construction
. | EGAT-RFI-AR-GS-06036.02 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | FDN, FG, PD1, PD2, Cable trench, EF3, EP1, GS1 | Surface of the foundation to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-15 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06036 |  |  | Construction
. | EGAT-RFI-AR-GS-06036.03 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | FDN, FG, PD1, PD2, Cable trench, EF3, EP1, GS1 | Inner surface of the trench to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-15 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06036 |  |  | Construction
. | EGAT-RFI-AR-GS-07190.02 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Panel Installation | Foam from inside must be removed | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-28 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07190 |  |  | Construction
. | EGAT-RFI-AR-GS-07190.03 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Panel Installation | Bottom flashing to be installed inside windows | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-28 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07190 |  |  | Construction
. | EGAT-RFI-AR-GS-07240.01 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Cladding | Sheets to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07240 |  |  | Construction
. | EGAT-RFI-AR-GS-07240.02 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Cladding | Installation openings to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07240 |  |  | Construction
. | EGAT-RFI-AR-GS-07240.03 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Cladding | Cutted edge of metal sheet to be painted | B | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07240 |  |  | Construction
. | EGAT-RFI-AR-GS-07240.04 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | Cladding | Flashing to be done | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-02 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07240 |  |  | Construction
. | EGAT-RFI-AR-GS-07611.01 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | - | Cable pit under water to be cleaned | C | EL | HEC EL Construction | Mr. Andrzej Misiek | 2023-04-06 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07611.02 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | - | Trench to cleaned- slope to be done | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-06 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07611.03 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | - | Trench to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-06 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07611.04 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | - | External trench not finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-06 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07611.05 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | - | Fedetals to be repaired(holes, screws, etc) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-06 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07611.06 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | - | EF1 top slab to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-06 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07611.07 | 800.00 | 1304-10-14 | 820-SHT-SH-300 | - | Leaking marks to be cleaned-roof | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-06 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-EL-SB-04651.01 | 800.00 | 1304-10-14 | PP EDG | V-CUM-E05-03EG11-00004_0 | SAT report should be submit before Energization | C | EL | Shinbo Electrical Subcon. | Mr. Arkadiusz Tryniszewski | 2022-10-06 | 2023-04-06 | [5 empty] | V |  |  |  | Construction
. | 17570 | 800.00 | 1304-10-19 | 1304-10-19 | Demenaralization package shelter | Remove the foam residue. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-09 | 2023-03-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17571 | 800.00 | 1304-10-19 | 1304-10-19 | Demenaralization package shelter | All damages of steel structure should be repaired. | C | SS | HEC SS Construction | Mr. Andrzej Wójcikiewicz | 2022-12-09 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17572 | 800.00 | 1304-10-19 | 1304-10-19 | Demenaralization package shelter | The floor should be cleaned from the other materials. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-09 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17573 | 800.00 | 1304-10-19 | 1304-10-19 | Demenaralization package shelter | Sandwich panels should be cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-09 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17574 | 800.00 | 1304-10-19 | 1304-10-19 | Demenaralization package shelter | The doors should be repaired and cleaned. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-09 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17575 | 800.00 | 1304-10-19 | 1304-10-19 | Demenaralization package shelter | All passages through the walls should be finished | B | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-09 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17576 | 800.00 | 1304-10-19 | 1304-10-19 | Demenaralization package shelter | The canopy should be finished. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-09 | 2023-05-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17577 | 800.00 | 1304-10-19 | 1304-10-19 | Demenaralization package shelter | Incorrectly installed door stop | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-09 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17578 | 800.00 | 1304-10-19 | 1304-10-19 | Demenaralization package shelter | The damaged panels should be changed. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-09 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17579 | 800.00 | 1304-10-19 | 1304-10-19 | Demenaralization package shelter | No thermal insulation of foundation. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2022-12-09 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17580 | 800.00 | 1304-10-19 | General |  | Lack of SAT inspection | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-09 | 2023-03-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 17581 | 800.00 | 1304-10-19 | General |  | Lack of Final Inspection- HVAC/Plumbng | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-09 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 17582 | 800.00 | 1304-10-19 | General |  | Lack of Final Inspection- Fire Protection | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-09 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 17583 | 800.00 | 1304-10-19 | Shelter | Heating installation | Rust on unit heater - correct touch up should be provided | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-09 | 2023-01-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17584 | 800.00 | 1304-10-19 | Shelter | Ventilation system | To be perform silicone around louver | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-09 | 2023-01-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17585 | 800.00 | 1304-10-19 | Demenaralization package shelter | EGAT-HEC-900-ELE-DLP-05027 | Provide green label pictogram for exit light to be provide | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-09 | 2023-02-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 17586 | 800.00 | 1304-10-19 | Demenaralization package shelter | EGAT-HEC-900-ELE-DLP-05027 | Housekeeping inside demenaralization shelter to be done | C | COMM | HEC COMM | Mr. Arkadiusz Tryniszewski | 2022-12-09 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 17587 | 800.00 | 1304-10-19 | Demenaralization package shelter | EGAT-HEC-900-ELE-DLP-05027 | Earthing bonding and main earthing to be provide for the cable tray | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-09 | 2023-03-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 17588 | 800.00 | 1304-10-19 | Demenaralization package shelter | EGAT-HEC-900-ELE-DLP-05027 | Identification sticker to be provide for the JB and Lighting fixtures. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-09 | 2023-02-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 17589 | 800.00 | 1304-10-19 | Demenaralization package shelter | EGAT-HEC-900-ELE-DLP-05027 | Illumination test to be carried out inside shelter | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-09 | 2023-03-20 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 17590 | 800.00 | 1304-10-19 | Demenaralization package shelter | EGAT-HEC-900-ELE-DLP-06009 | Fire Alarm Installation to be complete and official inspection to be carried out in Demenaralization package shelter | A | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-09 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17591 | 800.00 | 1304-10-19 | Demenaralization package shelter | EGAT-HEC-900-ELE-DLP-06009 | Fire alarm SAT to be complete | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-12-09 | 2023-03-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | EGAT-RFI-AR-GS-01470.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | FDN Axis 1-2/A-F | To be attached bearing capacity confirmation | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2021-04-16 | 2022-11-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-01470 | C-AR-GS-00025 |  | Construction
. | EGAT-RFI-AR-GS-05117.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | EF1, EF2 | Correct horisontal chamfering | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-17 | 2022-11-25 | Construction | 2022-02-28 |  |  |  | V | EGAT-RFI-AR-GS-05117 |  |  | Construction
. | EGAT-RFI-AR-GS-05117.02 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | EF1, EF2 | Do the vertical chamfering | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-17 | 2022-11-25 | Construction | 2022-02-28 |  |  |  | V | EGAT-RFI-AR-GS-05117 |  |  | Construction
. | EGAT-RFI-AR-GS-05117.03 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | EF1, EF2 | Grinding the vertical walls of foundations | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-17 | 2022-11-25 | Construction | 2022-02-28 |  |  |  | V | EGAT-RFI-AR-GS-05117 |  |  | Construction
. | EGAT-RFI-AR-GS-05156.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | F1-F2, PD1-PD2, TG1-TG2, GS1, EP3-EP7 | Cleaning of concrete surfaces | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-02-23 |  | Construction | 2022-02-24 |  |  |  |  | EGAT-RFI-AR-GS-05156 |  |  | Construction
. | EGAT-RFI-AR-GS-05156.02 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | F1-F2, PD1-PD2, TG1-TG2, GS1, EP3-EP7 | Repairing of damages made of electrician | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-02-23 | 2023-03-02 | Construction | 2022-02-24 |  |  |  | V | EGAT-RFI-AR-GS-05156 |  |  | Construction
. | EGAT-RFI-AR-GS-05156.03 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | F1-F2, PD1-PD2, TG1-TG2, GS1, EP3-EP7 | Dilatations round postuments to finish | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-02-23 | 2022-09-07 | Construction | 2022-02-24 | Selant at joint to be done. |  |  | V | EGAT-RFI-AR-GS-05156 |  |  | Construction
. | EGAT-RFI-AR-GS-05807.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Axis B-F/1-2 | The double leaf door scratches, dent | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-01 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-05807 |  |  | Construction
. | EGAT-RFI-AR-GS-05807.02 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Axis B-F/1-2 | Doors to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-06-01 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-05807 |  |  | Construction
. | EGAT-RFI-AR-GS-06172.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Axis 1-2/A-F | Lack of base angle | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-08 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06172 |  |  | Construction
. | EGAT-RFI-AR-GS-06172.02 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Axis 1-2/A-F | Panel dents under the fasteners | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-08 | 2023-06-06 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-06172 |  |  | Construction
. | EGAT-RFI-AR-GS-06172.03 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Axis 1-2/A-F | Panel damages | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-08 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-06172 |  |  | Construction
. | EGAT-RFI-AR-GS-06172.04 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Axis 1-2/A-F | Three fasteners should be used to fix the lost panels | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-07-08 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06172 |  |  | Construction
. | EGAT-RFI-AR-GS-06486.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Trench and Sump pit | Method statement for repairing steel angle | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-08-17 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06486 |  |  | Construction
. | EGAT-RFI-AR-GS-06970.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Flashing | Bottom flashing - bended and dirty | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-06970 |  |  | Construction
. | EGAT-RFI-AR-GS-06970.02 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Flashing | Top flashing color is not correct | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-06970 |  |  | Construction
. | EGAT-RFI-AR-GS-06970.03 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Flashing | Wall penetrations to be closed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 | 2023-02-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06970 |  |  | Construction
. | EGAT-RFI-AR-GS-06970.04 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Flashing | Splash block to be installed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06970 |  |  | Construction
. | EGAT-RFI-AR-GS-06970.05 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Flashing | Collision between downspout and pipe - west wall | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2022-11-16 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-06970 |  |  | Construction
. | EGAT-RFI-AR-GS-07185.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Panel Installation | Bottom flashing to be installed inside windows | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-28 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07185 |  |  | Construction
. | EGAT-RFI-AR-GS-07614.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | Flashing above ramp to be done | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07614 |  |  | Construction
. | EGAT-RFI-AR-GS-07614.02 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | Door stop damaged | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 | 2023-06-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07614 |  |  | Construction
. | EGAT-RFI-AR-GS-07614.03 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | Cracks on GS - to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07614 |  |  | Construction
. | EGAT-RFI-AR-GS-07614.04 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | Sealant to be done - GS trench connection | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07614 |  |  | Construction
. | EGAT-RFI-AR-GS-07614.05 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | Trench to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07614 |  |  | Construction
. | EGAT-RFI-AR-GS-07614.06 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | Unused grounding wire in ground slab | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07614 |  |  | Construction
. | EGAT-RFI-AR-GS-07614.07 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | Repairs on pedestals to be grinded | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07614 |  |  | Construction
. | EGAT-RFI-AR-GS-07614.08 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | PED in axis 1/E to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07614 |  |  | Construction
. | EGAT-RFI-AR-GS-07614.09 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | Unused pedestals to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07614 |  |  | Construction
. | EGAT-RFI-AR-GS-07614.10 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | Epoxy paint inside dike to be corrected | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07614 |  |  | Construction
. | EGAT-RFI-AR-GS-07614.11 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | Surface for epoxy paint inside sike wall not prepared well | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07614 |  |  | Construction
. | EGAT-RFI-AR-GS-07647.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | Lack of flashing | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07647 |  |  | Construction
. | EGAT-RFI-AR-GS-07647.02 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | Lack of tie rods | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-GS-07647 |  |  | Construction
. | EGAT-RFI-AR-GS-07647.03 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | - | Rusted elements | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-02-27 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07647 |  |  | Construction
. | EGAT-RFI-HV-JW-01202.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Duct Installation | To be cleaned louvers and UD | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-08 | 2023-01-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01203.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Equipment Installation | To be installed local panels | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-07 | 2022-12-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01203.02 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | 810-SHT-CC-400 | To be re-pained support of UH | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-07 | 2022-12-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01204.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Roof | To be removed duct and paint fence | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-08 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01204.02 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | Roof | To be cennected electrical and earthing cables | C | EL | HEC EL Construction | Ms. Daria Pliszka | 2022-11-08 | 2023-03-28 | Construction |  | 'Discipline' changed HV -> EL (2022-11-25) evidence attached |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01369.01 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | HVAC start up inspection | To be eliminate noise from UH number 2 and 3 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-11 | 2023-02-15 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01369 |  |  | Construction
. | EGAT-RFI-HV-JW-01369.02 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | HVAC start up inspection | Sound level should be measurement inside shelter | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-11 | 2023-05-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01369 |  |  | Construction
. | EGAT-RFI-HV-JW-01369.03 | 800.00 | 1304-10-19 | 810-SHT-CC-400 | HVAC start up inspection | Difficult access to main switch of the heaters | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-11 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01369 |  |  | Construction
. | EGAT-RFI-SS-MK-00982.01 | 800.00 | 1304-10-19 | AUX | 810-SHT-CC-400 | All parts of the steel structure have been assembled and bolted, except the elements: GT0002 x2, GT0006 x2, GT0008, GT00012, GT00015, GT00015, GT00019, GT00025 | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2021-12-13 | 2022-03-21 | Construction | 2021-12-14 |  |  |  | V | EGAT-RFI-SS-MK-00982 |  |  | Construction
. | EGAT-RFI-SS-MK-00982.02 | 800.00 | 1304-10-19 | AUX | 810-SHT-CC-400 | Lack of (chemical) anchor bolts for secondary structure (siding support structure) | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2021-12-13 | 2022-03-21 | Construction | 2021-12-14 |  |  |  | V | EGAT-RFI-SS-MK-00982 |  |  | Construction
. | EGAT-RFI-SS-MK-01100.01 | 800.00 | 1304-10-19 | AUX | 810-SHT-CC-400 | Touch up | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-01 | 2022-03-21 | Construction | 2022-02-20 | 'Punch Category' changed A -> C (2022-02-20) evidence attached |  |  | V | EGAT-RFI-SS-MK-01100 |  |  | Construction
. | EGAT-RFI-SS-MK-01102.01 | 800.00 | 1304-10-19 | AUX | 810-SHT-CC-400 | Ladder rungs should not be circular | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-03 | 2023-05-17 | Construction | 2022-02-04 | 'Punch Category' changed A -> C (2022-02-20) evidence attached |  |  | V | EGAT-RFI-SS-MK-01102 |  |  | Construction
. | EGAT-RFI-SS-MK-01102.02 | 800.00 | 1304-10-19 | AUX | 810-SHT-CC-400 | Concrete gap | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-02-03 | 2022-11-03 | Construction | 2022-02-04 | discipline changed SS-> AR (2022-04-15) evidence attached / 'Punch Category' changed A -> C (2022-02-20) evidence attached |  |  | V | EGAT-RFI-SS-MK-01102 |  |  | Construction
. | EGAT-RFI-SS-MK-01102.03 | 800.00 | 1304-10-19 | AUX | 810-SHT-CC-400 | Gap between toe board and gratin coating damages | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-03 |  | Construction | 2022-02-04 | 'Punch Category' changed A -> C (2022-02-20) evidence attached |  |  | V | EGAT-RFI-SS-MK-01102 |  |  | Construction
. | EGAT-RFI-SS-MK-01225.01 | 800.00 | 1304-10-19 | AUX | 810-SHT-CC-400 | Ladder rungs should not be circular (EGAT-RFI-SS-MK-01102.01) | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-18 | 2022-12-29 | Construction | 2022-03-23 |  |  |  | V | EGAT-RFI-SS-MK-01225 |  |  | Construction
. | EGAT-RFI-SS-MK-01225.02 | 800.00 | 1304-10-19 | AUX | 810-SHT-CC-400 | Concrete gap (EGAT-RFI-SS-MK-01102.02) | A | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-03-18 | 2022-11-03 | Construction | 2022-03-23 | discipline changed SS-> AR (2022-04-15) evidence attached |  |  | V | EGAT-RFI-SS-MK-01225 |  |  | Construction
. | EGAT-RFI-SS-MK-01225.03 | 800.00 | 1304-10-19 | AUX | 810-SHT-CC-400 | Gap between toe board and grating coating damages (EGAT-RFI-SS-MK-01102.03) | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-18 | 2022-12-29 | Construction | 2022-03-23 |  |  |  | V | EGAT-RFI-SS-MK-01225 |  |  | Construction
. | EGAT-RFI-SS-MK-01225.04 | 800.00 | 1304-10-19 | AUX | 810-SHT-CC-400 | Coating damages due to other branches | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-18 |  | Construction | 2022-03-23 |  |  |  |  | EGAT-RFI-SS-MK-01225 |  |  | Construction
. | 05184 | 820.10 | 820-10-22 | Phosphate Dosing System | 820-X0001-ST01 | Final Inspection for 820-X0001-ST01 to be done | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-08-25 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05185 | 820.10 | 820-10-22 | Phosphate Dosing System | 820-X0001 | Box up for 820-X0001 to be done. | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-08-25 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05186 | 820.10 | 820-10-22 | Phosphate Dosing System | 820BF-CH-1001 | 820BF-CH-1001: Final Appearance Inspection to be done | C | IN | HEC IN Construction | Mr. Krzysztof Nolbert | 2022-08-25 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05187 | 820.10 | 820-10-22 | Phosphate Dosing System | 820-LT-1004 | 820-LT-1004: Inspection for Pulling / IR Test / Termination to be done | A | CI | HEC CI Construction | Mr. Adam Siewiorek | 2022-08-25 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05188 | 820.10 | 820-10-22 | Phosphate Dosing System | 820-PT-9102 | 820-PT-9102: Inspection for Pulling / IR Test / Termination to be done | A | CI | HEC CI Construction | Mr. Adam Siewiorek | 2022-08-25 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05189 | 820.10 | 820-10-22 | Phosphate Dosing System | 820-PT-9103 | 820-PT-9103: Inspection for Pulling / IR Test / Termination to be done | A | CI | HEC CI Construction | Mr. Adam Siewiorek | 2022-08-25 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05190 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00031 | Dameged insulation | C | IN | HEC IN Construction | Ms. Małgorzata Juszczyk | 2022-08-25 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05191 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00031 | Missing isolation on line 820-2"-CH-00103N4A1-ET and on drain valve | C | IN | HEC IN Construction | Ms. Małgorzata Juszczyk | 2022-08-25 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05192 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00031 | Piping support missing | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-08-25 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05193 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00031 | Missing sealing on isolation | C | IN | HEC IN Construction | Ms. Małgorzata Juszczyk | 2022-08-25 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05194 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00031 | Not enough space for isolation | C | IN | HEC PI Design | Ms. Małgorzata Juszczyk | 2022-08-25 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05195 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00031 | Safety issue: vent line from storage tank to be located in safe location. | A | PI | HEC PI Design | Ms. Małgorzata Juszczyk | 2022-08-25 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05196 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00031 | Locking device missing on LO valves | C | COMM | HEC COMM | Ms. Małgorzata Juszczyk | 2022-08-25 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05197 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00031 | PT-9103 to be tightened | A | CI | HEC CI Construction | Ms. Małgorzata Juszczyk | 2022-08-25 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 05198 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00031 | Lack of drain valve on line 820-2"-CH-00103N4A1-ET on P&ID | B | PI | HEC PI Design | Ms. Małgorzata Juszczyk | 2022-08-25 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05199 | 820.10 | 820-10-22 | Phosphate Dosing System | 820-1"-CH-91012-N4A1-N and 820-1"-CH-91002-N4A1-N | End bling missing on lines 820-1"-CH-91012-N4A1-N and 820-1"-CH-91002-N4A1-N | B | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2022-08-25 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05200 | 820.10 | 820-10-22 | Phosphate Dosing System | 820-1"-CH-91012-N4A1-N | Missing flange upstream block valve on line 820-1"-CH-91012-N4A1-N on P&ID | B | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2022-08-25 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05201 | 820.10 | 820-10-22 | Phosphate Dosing System | P01B | Plug missing on pump P01B | A | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2022-08-25 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05202 | 820.10 | 820-10-22 | Phosphate Dosing System | General | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PI Design | Ms. Małgorzata Juszczyk | 2022-08-25 | 2023-04-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05203 | 820.10 | 820-10-22 | Phosphate Dosing System |  | Skid grounding cables to be install | A | EL | HEC EL Construction | Mr. Krzysztof Kaliszyk | 2022-08-25 | 2022-10-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05204 | 820.10 | 820-10-22 | Phosphate Dosing System |  | Stud bolts to be protected with molecote | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-25 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05205 | 820.10 | 820-10-22 | Phosphate Dosing System |  | Calibration pot to be tighten | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-25 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05206 | 820.10 | 820-10-22 | Phosphate Dosing System |  | Rusted stud bolts on top nozzle flanges needs to be protected with anti seize | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-25 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05207 | 820.10 | 820-10-22 | Phosphate Dosing System |  | Touch up paint required in modified handrail. | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-25 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05208 | 820.10 | 820-10-22 | Phosphate Dosing System | 820-1"-CH-91002-N4A1-N and 820-1"-CH-91012-N4A1-N | Permanent blind to installed at 820-1"-CH-91002-N4A1-N and 820-1"-CH-91012-N4A1-N | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-25 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05209 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00051 | Missing initial ATEX inspection for instruments. | B | PER | HEC permit team | Owner Maintenance team | 2022-08-25 | 2023-01-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05210 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00051 | Missing or wrong CE mark on skid nameplate | B | ME | HEC ME Construction | Owner Maintenance team | 2022-08-25 | 2022-12-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05211 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00051 | GENERAL PUNCH: All the devices missing Ex plugs. | A | CI | HEC CI Construction | Mr. Adam Siewiorek | 2022-08-25 | 2022-11-24 | Walkdown |  | 2022-11-21 | 2022-11-18 |  | V |  |  |  | RFC/RFSU
. | 05212 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00051 | LT-1004 Tubing to be done. | A | CI | HEC CI Construction | Mr. Adam Siewiorek | 2022-08-25 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 05213 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00051 | PT-9102 cable tray grommet missing. | A | CI | HEC CI Construction | Mr. Adam Siewiorek | 2022-08-25 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 05214 | 820.10 | 820-10-22 | Phosphate Dosing System | EGAT-HEC-820-PRO-PID-00051 | PT-9103 Transmitter mounting to be tightened, it shoul be fixed in place not rotate. | A | CI | HEC CI Construction | Mr. Adam Siewiorek | 2022-08-25 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 06469 | 820.10 | 820-10-22 | 820BF | 820BF-820CH00103-01 | Pipeline wall pass through mark missing. To be reflected in ISO drawing. | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-06 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06470 | 820.10 | 820-10-22 | 820BF | 820BF-820CH00103-01 | Piping Insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06471 | 820.10 | 820-10-22 | 820BF | 820BF-820CH00103-01 | Cladding, bonding straps to be installed properly | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06472 | 820.10 | 820-10-22 | 820BF | 820BF-820CH00103-01 | Mastic to be applied at all pipe elbows (cladding) | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06473 | 820.10 | 820-10-22 | 820BF | 820BF-820CH00103-01 | All supports going out from cladding to be sealed by mastic | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06474 | 820.10 | 820-10-22 | 820BF | 820BF-820CH00103-01 | Paint touch up for support to be done. | B | PA | HEC PA Construction | Mr. Zenon Palamarz | 2022-09-06 | 2022-10-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07118 | 820.10 | 820-10-20 | Boiler Blow Down System | 820-V0002 | Final Inspection | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-19 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07119 | 820.10 | 820-10-20 | Boiler Blow Down System | 820-E0001 | Box Up | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-19 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07120 | 820.10 | 820-10-20 | Boiler Blow Down System | 810WT-SC-1001 | Final Appeareance Inspection | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-19 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07121 | 820.10 | 820-10-20 | Boiler Blow Down System | 820BF-SC-1001 | Final Appeareance Inspection | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-19 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07122 | 820.10 | 820-10-20 | Boiler Blow Down System | 820BF-SC-1002 | Final Appeareance Inspection | C | IN | HEC IN Construction | J.W.JEONG | 2022-09-19 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07123 | 820.10 | 820-10-20 | Boiler Blow Down System | 820BF-TRE-1001 | Final Appeareance Inspection | C | IN | HEC IN Construction | J.W.JEONG | 2022-09-19 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07124 | 820.10 | 820-10-20 | Boiler Blow Down System | 820BF-TRV-1001 | Final Appeareance Inspection | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-19 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07125 | 820.10 | 820-10-20 | Boiler Blow Down System | 820BF-TRV-1002 | Final Appeareance Inspection | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-19 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07126 | 820.10 | 820-10-20 | Boiler Blow Down System | 820-FE-1008 | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07127 | 820.10 | 820-10-20 | Boiler Blow Down System | 820-FE-1009 | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07128 | 820.10 | 820-10-20 | Boiler Blow Down System | 820-LT-1006 | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07129 | 820.10 | 820-10-20 | Boiler Blow Down System | 820-LG-M-1002 | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-07 | Walkdown |  |  | 2022-11-05 |  | V |  |  |  | RFC/RFSU
. | 07130 | 820.10 | 820-10-20 | Boiler Blow Down System | 820-FT-1008 | Inspection for Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07131 | 820.10 | 820-10-20 | Boiler Blow Down System | 820-FT-1009 | Inspection for Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07132 | 820.10 | 820-10-20 | Boiler Blow Down System | 820-PG-0611B | Inspection for Installation | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07133 | 820.10 | 820-10-20 | Boiler Blow Down System | 820-TG-1020 | Inspection for Installation | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07134 | 820.10 | 820-10-20 | Boiler Blow Down System | 820-FV-1009 | Inspection for Calibration / Installation / Pulling / IR Test / Termination / Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07135 | 820.10 | 820-10-20 | Boiler Blow Down System | 820-LV-1006 | Inspection for Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07136 | 820.10 | 820-10-20 | Boiler Blow Down System | EGAT-RFI-CI-CW-01393.01 | Torquing to be done | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-10-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07137 | 820.10 | 820-10-20 | Boiler Blow Down System | EGAT-RFI-CI-CW-02291.01 | Spare hole ATEX blind plug to be provide | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-24 | Walkdown |  | 2022-11-18 | 2022-11-18 |  | V |  |  |  | RFC/RFSU
. | 07138 | 820.10 | 820-10-20 | 820-V0002 | 820-V0002 | Rust on the lifting lug and nameplate to be touch-up painted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-19 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07139 | 820.10 | 820-10-20 | 820-V0002 | 820-V0002 | 10'' flange at line 820-10"-LS-00114-MS-11-P to be touch up painted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-19 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07140 | 820.10 | 820-10-20 | 820-V0002 | 820-V0002 | 4'' pipe insulation not yet completed at the (VG1C13H) | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2023-02-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07141 | 820.10 | 820-10-20 | 820-V0002 | 820-V0002 | VG1C13H 4'' pipe plastic cover to be remove and touch-up painting to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07142 | 820.10 | 820-10-20 | 820-V0002 | 820-V0002 | Platform and ladder to be touch-up painted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07143 | 820.10 | 820-10-20 | 820-V0002 | 820-V0002 | Open insulation around flanges to be temporary protected against water ingres | B | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07144 | 820.10 | 820-10-20 | 820-V0002 | 820-V0002 | Broken mastic sealing to be repaired | B | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07145 | 820.10 | 820-10-20 | 820-V0002 | 820-V0002 | Rusted cladding to be repaired | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07146 | 820.10 | 820-10-20 | 820-V0002 | 820-V0002 | Wet insulation around all flanges to be replaced | B | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07147 | 820.10 | 820-10-20 | 820-V0002 | 820-V0002 | Housekeeping to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07148 | 820.10 | 820-10-20 | 820-P0001A/B | 820-P0001A/B | Insulation to be completed | B | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07149 | 820.10 | 820-10-20 | 820-P0001A | 820-P0001A | 1/2'' pipe is almost touching with the pipe connected to sight glass | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07150 | 820.10 | 820-10-20 | 820-P0001A/B | 820-P0001A/B | Rusted bolts and nuts to be cleaned | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07151 | 820.10 | 820-10-20 | 820-P0001A/B | 820-P0001A/B | bent pipe masking tape cover to be removed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07152 | 820.10 | 820-10-20 | 820-P0001A/B | 820-P0001A/B | Housekeeping to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07153 | 820.10 | 820-10-20 | 820-P0001A/B | 820-P0001A/B | Touch-up painting on pump flange | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07154 | 820.10 | 820-10-20 | 820-TE-1003 | 820-TE-1003 | bolt to be tigthened | A | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-11-14 | Walkdown |  |  | 2022-11-10 |  | V |  |  |  | RFC/RFSU
. | 07155 | 820.10 | 820-10-20 | 820-E0001 | 820-E0001 | Damage wet insulation to be repalced | B | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07156 | 820.10 | 820-10-20 | 820-E0001 | 820-E0001 | Rusted bolts and nuts at flange to be cleaned upstream and downstream | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07157 | 820.10 | 820-10-20 | 820-E0001 | 820-E0001 | Spectacle blind to be installed permanently upstream and downstream | A | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07158 | 820.10 | 820-10-20 | 820-E0001 | 820-E0001 | Rusted flanges (inlet/outlet) to be cleaned and touch-up painted. | B | PA | HEC PA Construction | Mr. Krzysztof Kaliszyk | 2022-09-08 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07159 | 820.10 | 820-10-20 | Boiler Blow Down System |  | Safety switches do not meet the Machinery Directive 06/42 / EC- Polish law, Ordinance of the Ministry of Economy of October 21, 2008 in clause 1.2.4.3 "The emergency stop device must: be equipped with CLEARLY RECOGNIZABLE, VISIBLE and QUICKLY ACCESSIBLE controls." | C | EM | HEC EL Design | Mr. Krzysztof Nolbert | 2022-09-20 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07160 | 820.10 | 820-10-20 | Boiler Blow Down System |  | Part of installation indicated as LIVE LINE, not fixed to the rest part | A | COMM | HEC COMM | Mr. Krzysztof Nolbert | 2022-09-20 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07161 | 820.10 | 820-10-20 | Boiler Blow Down System |  | Transmitter 820-TE-0003, not properly fixed to the installation | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-20 | 2022-11-18 | Walkdown |  | 2022-11-18 | 2022-11-18 |  | V |  |  |  | RFC/RFSU
. | 07162 | 820.10 | 820-10-20 | Boiler Blow Down System |  | No access to transmitter 820-TE-1006 | C | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-20 |  | Walkdown | [8 empty] | RFC/RFSU
. | 07163 | 820.10 | 820-10-20 | Boiler Blow Down System |  | transmitter 820-TE-1006 Display should be rotated 90° counter clockwise | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-20 | 2022-11-14 | Walkdown |  |  | 2022-11-10 |  | V |  |  |  | RFC/RFSU
. | 07164 | 820.10 | 820-10-20 | Boiler Blow Down System |  | Part of installation not insulated | B | IN | HEC IN Construction | Mr. Krzysztof Nolbert | 2022-09-20 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07165 | 820.10 | 820-10-20 | Boiler Blow Down System |  | Partially insulation not finished | C | IN | HEC IN Construction | Mr. Krzysztof Nolbert | 2022-09-20 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07166 | 820.10 | 820-10-20 | Boiler Blow Down System |  | Touchpainting incorrectly performed - rust | C | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-20 | 2023-05-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07167 | 820.10 | 820-10-20 | Boiler Blow Down System | EGAT-HEC-820-PRO-PID-00061 | Loose bolts and missing bolts on LG-1002 and LT-1005, LT-1006 | A | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2022-09-20 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07168 | 820.10 | 820-10-20 | Boiler Blow Down System | EGAT-HEC-820-PRO-PID-00061 | Hanging tag missing for LG-1002 and LT-1006 | B | CI | HEC CI Construction | Ms. Małgorzata Juszczyk | 2022-09-20 | 2022-11-15 | Walkdown |  |  | 2022-11-11 |  | V |  |  |  | RFC/RFSU
. | 07169 | 820.10 | 820-10-20 | Boiler Blow Down System | EGAT-HEC-820-PRO-PID-00061 | Insulation finish not protected from rain water | C | IN | HEC IN Construction | Ms. Małgorzata Juszczyk | 2022-09-20 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07170 | 820.10 | 820-10-20 | Boiler Blow Down System | EGAT-HEC-820-PRO-PID-00061 | Intrument air line for FV-1009 damaged | A | CI | HEC CI Construction | Ms. Małgorzata Juszczyk | 2022-09-20 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 07171 | 820.10 | 820-10-20 | Boiler Blow Down System | EGAT-HEC-820-PRO-PID-00061 | Missing name plate for cable for FV-1009 | B | CI | HEC CI Construction | Ms. Małgorzata Juszczyk | 2022-09-20 | 2022-11-15 | Walkdown |  |  | 2022-11-11 |  | V |  |  |  | RFC/RFSU
. | 07172 | 820.10 | 820-10-20 | Boiler Blow Down System | EGAT-HEC-820-PRO-PID-00061 | Missing tag for sampling point 0611 | C | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-09-20 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07173 | 820.10 | 820-10-20 | Boiler Blow Down System | EGAT-HEC-820-PRO-PID-00061 | End blind connection type for vent and drain valve on 820-E0001 to be verified(inconsistency on P&ID) | B | EM | HEC PI Design | Ms. Małgorzata Juszczyk | 2022-09-20 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07174 | 820.10 | 820-10-20 | Boiler Blow Down System | EGAT-HEC-820-PRO-PID-00061 | Damaged insulation on line 820-4"-SC-00112-MS-11-ET between pumps and piperack | C | IN | HEC IN Construction | Ms. Małgorzata Juszczyk | 2022-09-20 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07175 | 820.10 | 820-10-20 | AUX/820-V0002/E0001/P0001A/B | General | Provide grommet for the edge of cable tray | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-30 | Walkdown |  | 2022-11-29 | 2022-11-25 |  | V |  |  |  | RFC/RFSU
. | 07176 | 820.10 | 820-10-20 | AUX/820-V0002/E0001 | 820-TE/TT-1003/TG-1020/LT-1005/1006 | Bolt torquing to be done | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-17 | Walkdown |  |  | 2022-11-13 |  | V |  |  |  | RFC/RFSU
. | 07177 | 820.10 | 820-10-20 | AUX/820-E0001 | 820-TE/TT-1003 | Mounting installation of temperature transmitter should be tightened properly | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-14 | Walkdown |  |  | 2022-11-10 |  | V |  |  |  | RFC/RFSU
. | 07178 | 820.10 | 820-10-20 | AUX/820-E0001 | 820-TE/TT-1006 | No access for temperature transmitter | C | EM | HEC PI Design | Owner Maintenance team | 2022-09-19 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07179 | 820.10 | 820-10-20 | AUX/820-V0002 | 820-FT-1008/1009 | Missing drain tube on enclosure box of level transmitter | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-14 | Walkdown |  |  | 2022-11-10 |  | V |  |  |  | RFC/RFSU
. | 07180 | 820.10 | 820-10-20 | AUX/820-E0001 | 820-FV-1009 | Tubing of flow control valve should be replace(have damage) | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07181 | 820.10 | 820-10-20 | AUX/820-V0002 | 820-LT-1006/LG-M-1002 | Missing hanging tag for instrument | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 07182 | 820.10 | 820-10-20 | AUX/820-V0002 | 820-LT-1005/1006 | Blind plug for spare cable entry of level trasmitter should be tightened properly | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 07183 | 820.10 | 820-10-20 | AUX/820-P0001A/B | 820-LT-8010/8011/PT-8010/8011 | Blind plug for spare cable entry of instrument at package must be replace with Atex specification | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 07184 | 820.10 | 820-10-20 | AUX/820-E0001 | 820-SN-0611 | Please provide nameplate with tag for sampling point. | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-30 | Walkdown |  | 2022-11-30 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 07185 | 820.10 | 820-10-20 | AUX/820-V0002/E0001/P0001A/B | General | Please provide double direction for cable labeling. | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-19 | 2022-11-30 | Walkdown |  | 2022-11-29 | 2022-11-25 |  | V |  |  |  | RFC/RFSU
. | 07186 | 820.10 | 820-10-20 | AUX/820-V0002/E0001/P0001A/B | General | Initial Atex Inspection | B | PER | HEC permit team | Mr. Krzysztof Nolbert | 2022-09-19 | 2023-01-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07923 | 820.10 | 820-10-28 | AUX/820-Phosphate Injection BFW Treatment Shelter | 820-LT-1003A | Missing drain tube of instrument | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-20 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 07924 | 820.10 | 820-10-28 | AUX/820-Phosphate Injection BFW Treatment Shelter | 820-LT-1003A/PT-9202/9203 | No blind plug on instrument spare cable entry | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-20 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 07925 | 820.10 | 820-10-28 | AUX/820-Phosphate Injection BFW Treatment Shelter | 820-PG-9205/9206/9207/9208 | Atex specification of all pressure gauge shall be verified | A | EM | HEC MR Design | Mr. Krzysztof Nolbert | 2022-09-20 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07926 | 820.10 | 820-10-28 | AUX/820-Phosphate Injection BFW Treatment Shelter | 820-PT-9202/9203 | Mounting installation of instrument to be tightened properly | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-20 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 07927 | 820.10 | 820-10-28 | AUX/820-Phosphate Injection BFW Treatment Shelter | 820-LG-M-9204 | The isolation valve on vent side of level gauge is missing | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-20 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07928 | 820.10 | 820-10-28 | AUX/820-Phosphate Injection BFW Treatment Shelter | General | Initial ATEX inspection | B | PER | HEC permit team | Owner Maintenance team | 2022-09-20 | 2023-01-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07929 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00041 | Blind flange missing on line 820-1"-CH-92012-N1A1-N | A | ME | HEC ME Construction | Ms. Alicja Sulżyc | 2022-09-20 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07930 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00041 | Blind flange missing on line 820-1"-CH-92002-N1A1-N | A | ME | HEC ME Construction | Ms. Alicja Sulżyc | 2022-09-20 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07931 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00041 | Loose bolts on PT-9202 | A | ME | HEC ME Construction | Ms. Alicja Sulżyc | 2022-09-20 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07932 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00011 | Wrongly mounted of check valve, line 820-2"-CH-00102-N1A1-ET, near 820-V0003 | A | PI | HEC PI Construction | Ms. Alicja Sulżyc | 2022-09-20 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07933 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00011 | Valve handle to be cleaned and repainted | B | ME | HEC ME Construction | Ms. Alicja Sulżyc | 2022-09-20 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07934 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00041 | Anti-acid coating damaged | A | AR | HEC AR Construction | Ms. Alicja Sulżyc | 2022-09-20 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07935 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00041 | Anti-acid coating to be provided | A | AR | HEC AR Construction | Ms. Alicja Sulżyc | 2022-09-20 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07936 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00041 | Vent not in safe location | A | PI | HEC PI Construction | Ms. Alicja Sulżyc | 2022-09-20 | 2022-10-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07937 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00041 | Missing vent valve on LG-M9204 | A | ME | HEC ME Construction | Ms. Alicja Sulżyc | 2022-09-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07938 | 820.10 | 820-10-28 | 820-X0006 | 820-X0006-ST01 | Rusted U-Bolt to be cleaned | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-20 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07939 | 820.10 | 820-10-28 | 820-X0006 | 820-X0006-ST01 | Housekeeping to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-20 | 2023-01-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07940 | 820.10 | 820-10-28 | 820-X0006 | 820-X0006-ST01 | SS flange with CS bolt and nuts to be verefied w/ engineering | C | EM | HEC MR Design | Mr. Krzysztof Kaliszyk | 2022-09-20 | 2023-03-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07941 | 820.10 | 820-10-28 | 820-X0006 | 820-X0006-ST01 | Plastic cover to be removed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-20 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07942 | 820.10 | 820-10-28 | 820-X0006 | 820-X0006-P01B | Housekeeping and cleaning to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-20 | 2023-01-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07943 | 820.10 | 820-10-28 | 820-X0006 | 820-LG-M-9204 | Rusted bolts and nuts upstream and downstream to be cleaned | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-20 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07944 | 820.10 | 820-10-28 | 820-X0006 | 820-X0006-P01A | Water coming from the ceiling exhaust need to be modified in order for rainwater not to come inside the skid | A | AR | HEC AR Construction | Mr. Krzysztof Kaliszyk | 2022-09-20 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07945 | 820.10 | 820-10-28 | 820-X0006 | 820-X0006 | Rusted wheel of the gate valve to be touch-up painted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-20 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07946 | 820.10 | 820-10-28 | 820-X0006 | 820-X0006-ST01 | Rusted bolts and nuts above the tank to be properly cleaned and molykote | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-20 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07947 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00041 | Duct sealing to be done for cable stub-up conduit pipe | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-20 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07948 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00041 | Provide yellow tag sticker for LCS EMERGENCY PUSH BOTTON at cover side written with Polish Language [ WYŁĄCZNIK AWARYJNY ] for all LCS and ES.. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-20 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07949 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00041 | Earthing to be provided for monkey ladder & Tank 820-X0006 - ST01. | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-20 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07950 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00041 | For all motors terminal box spare hole Blind Plug to be provided. | A | ME | HEC ME Construction | Mr. Arkadiusz Tryniszewski | 2022-09-20 | 2022-11-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07951 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00041 | For all motors body earthing is missing | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-20 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 07952 | 820.10 | 820-10-28 | Amine Dosing System | EGAT-HEC-820-PRO-PID-00041 | Provide Exd blind plug for LCS gland spare hole 860-MP0002A/B | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-20 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08411 | 820.10 | 820-10-28 | 820BF | 820BF-820CH00102-01 | Pipe wall pass through mark missing. Drawing to be updated | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-20 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08412 | 820.10 | 820-10-28 | 820BF | 820BF-820CH00102-01 | Pipe wall pass through not finished (not sealed) | B | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-20 | 2023-01-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08413 | 820.10 | 820-10-28 | 820BF | 820BF-820CH00102-01 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08414 | 820.10 | 820-10-28 | 820BF | 820BF-820CH00102-01 | Mastic missing on supports | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-20 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08415 | 820.10 | 820-10-28 | 820BF | 820BF-820CH00102-01 | Piping Insulation to be installed properly. Gaps on cladding | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-20 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08416 | 820.10 | 820-10-28 | 820BF | 820BF-820CH00102-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-20 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08417 | 820.10 | 820-10-28 | 810PR | 810PR-820CH00102-01 | Wrong flow direction of check valve. Valve to be reoriented at site and Iso drawing to be revised. | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-20 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08418 | 820.10 | 820-10-28 | 810PR | 810PR-820CH00102-01 | Trunion support in touch contact with grating | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-20 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08419 | 820.10 | 820-10-28 | 810PR | 810PR-820CH00102-01 | Paint touch up for valve stem to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08420 | 820.10 | 820-10-28 | 810PR | 810PR-820CH00102-01 | Mastic missing on support | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-20 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08421 | 820.10 | 820-10-28 | 810PR | 810PR-820CH00102-01 | Line close to steel structure, insulation thickness not proofed. Cladding in clash with steel structure not sealed by mastic | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-20 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08422 | 820.10 | 820-10-28 | 810PR | 810PR-820CH00102-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-20 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08520 | 820.10 | 820-10-18 | HP Boiler Package | 820-B0001-X01 | Final Inspection | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08521 | 820.10 | 820-10-18 | HP Boiler Package | 820-B0001-X02 | Final Inspection | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08522 | 820.10 | 820-10-18 | HP Boiler Package | 820-B0001-X04 | Final Inspection | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08523 | 820.10 | 820-10-18 | HP Boiler Package | 820-B0001-X05 | Final Inspection | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08524 | 820.10 | 820-10-18 | HP Boiler Package | 820-B0001 -W01 & 820-B0001-W02 | Final Inspection | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08525 | 820.10 | 820-10-18 | HP Boiler Package | 820-B0001 -X05 | Final Inspection | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08526 | 820.10 | 820-10-18 | HP Boiler Package | 820-B0001(Steam Boiler Package) | Final Inspection | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08527 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-FG-1001 | Re-instatement | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-11-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08528 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-FG-1003 | Re-instatement | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08529 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-H-1001 | Re-instatement | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08530 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-H-1002 | Re-instatement | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08531 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-H-1003 | Re-instatement | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08532 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-HS-1002 | Re-instatement | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-09-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08533 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-VG-1001 | Re-instatement | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08534 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-VG-1002 | Re-instatement | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08535 | 820.10 | 820-10-18 | HP Boiler Package | CHEM-820-B0001 | Akaline Cleaning for HP Boiler (Water Drum & Steam Drum) | C | COMM | HEC COMM | Ms. Paulina Bajer | 2022-09-23 | 2023-03-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08536 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-AV-1001 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08537 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-BW-1001 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08538 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-BW-1002 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08539 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-FG-1001 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08540 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-FG-1002 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08541 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-FG-1003 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08542 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-H-1001 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08543 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-H-1003 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08544 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-HS-1007 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08545 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-HS-1003 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08546 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-N-1001 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08547 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-NY-1002 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08548 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-NY-1003 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08549 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-NY-1004 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08550 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-NY-1005 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08551 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-NY-1006 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08552 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-SC-1004 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08553 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-SC-1007 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08554 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-SC-1001 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08555 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-SC-1002 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08556 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-SC-1003 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08557 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-SOL-1002 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08558 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-TR-1001 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08559 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-H-1002 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08560 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-HS-1009 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08561 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-HS-1002 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08562 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-SOL-1001 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08563 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-SC-1006 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08564 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-SC-1009 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08565 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-VG-1002 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08566 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-CH-1001 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08567 | 820.10 | 820-10-18 | HP Boiler Package | 820BFV-SC-1005 | Final Appeareance Inspection | B | IN | HEC IN Construction | Mr. Zenon Palamarz | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08568 | 820.10 | 820-10-18 | HP Boiler Package | R.820-B0001-MW01 | Cable Termination & Test | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08569 | 820.10 | 820-10-18 | HP Boiler Package | R.820-B0001-MW02 | Cable Termination & Test | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08570 | 820.10 | 820-10-18 | HP Boiler Package | C1.820-B0001/GCP/ECMS | Cable Termination & Test | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-11-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08571 | 820.10 | 820-10-18 | HP Boiler Package | C2.820-B0001/GCP/ECMS | Cable Termination & Test | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-11-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08572 | 820.10 | 820-10-18 | HP Boiler Package | LP.820-JP-531-1 | Cable Termination & Test | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08573 | 820.10 | 820-10-18 | HP Boiler Package | LP.820-JP-532-1 | Cable Termination & Test | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08574 | 820.10 | 820-10-18 | HP Boiler Package | 820-FT-9163 | Cable Pulling, Cable Termination & Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08575 | 820.10 | 820-10-18 | HP Boiler Package | 820-FZT-9198 | Cable Pulling, Cable Termination & Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-12-01 | Walkdown |  | 2022-11-30 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 08576 | 820.10 | 820-10-18 | HP Boiler Package | 820-HS-1011 | Installation | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08577 | 820.10 | 820-10-18 | HP Boiler Package | 820-AC-001 | Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08578 | 820.10 | 820-10-18 | HP Boiler Package | 820-AT-9160 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08579 | 820.10 | 820-10-18 | HP Boiler Package | 820-BE-9171A | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08580 | 820.10 | 820-10-18 | HP Boiler Package | 820-BE-9171B | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08581 | 820.10 | 820-10-18 | HP Boiler Package | 820-BE-9172 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08582 | 820.10 | 820-10-18 | HP Boiler Package | 820-BE-9173 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08583 | 820.10 | 820-10-18 | HP Boiler Package | 820-BE-9180A | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08584 | 820.10 | 820-10-18 | HP Boiler Package | 820-BE-9180B | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08585 | 820.10 | 820-10-18 | HP Boiler Package | 820-FE-9170 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08586 | 820.10 | 820-10-18 | HP Boiler Package | 820-FE-9171 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08587 | 820.10 | 820-10-18 | HP Boiler Package | 820-FT-9153 | Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08588 | 820.10 | 820-10-18 | HP Boiler Package | 820-FT-9163 | Installation | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  | Rejected.. RFI Not Signed |  |  | V |  |  |  | RFC/RFSU
. | 08589 | 820.10 | 820-10-18 | HP Boiler Package | 820-FT-9170 | Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08590 | 820.10 | 820-10-18 | HP Boiler Package | 820-FT-9171 | Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08591 | 820.10 | 820-10-18 | HP Boiler Package | 820-FT-9172 | Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08592 | 820.10 | 820-10-18 | HP Boiler Package | 820-FV-9160 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08593 | 820.10 | 820-10-18 | HP Boiler Package | 820-FV-9161 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08594 | 820.10 | 820-10-18 | HP Boiler Package | 820-KE-9186 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08595 | 820.10 | 820-10-18 | HP Boiler Package | 820-LG-9150 | Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08596 | 820.10 | 820-10-18 | HP Boiler Package | 820-MOV-9150 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08597 | 820.10 | 820-10-18 | HP Boiler Package | 820-MOV-9151 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08598 | 820.10 | 820-10-18 | HP Boiler Package | 820-MOV-9152 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08599 | 820.10 | 820-10-18 | HP Boiler Package | 820-PCV-9170 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08600 | 820.10 | 820-10-18 | HP Boiler Package | 820-PCV-9171 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08601 | 820.10 | 820-10-18 | HP Boiler Package | 820-PCV-9172 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08602 | 820.10 | 820-10-18 | HP Boiler Package | 820-PG-9170 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08603 | 820.10 | 820-10-18 | HP Boiler Package | 820-PRV-9173 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08604 | 820.10 | 820-10-18 | HP Boiler Package | 820-PSV-9150 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08605 | 820.10 | 820-10-18 | HP Boiler Package | 820-PSV-9151 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08606 | 820.10 | 820-10-18 | HP Boiler Package | 820-PSV-9152 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08607 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9150 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08608 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9151 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08609 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9152 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08610 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9153 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08611 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9154 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08612 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9155 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08613 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9156 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08614 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9157 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08615 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9158 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08616 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9160 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08617 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9161 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08618 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9162 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08619 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9170 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08620 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9171 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08621 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9172A | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08622 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9172B | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08623 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9172C | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08624 | 820.10 | 820-10-18 | HP Boiler Package | 820-TE-9198 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08625 | 820.10 | 820-10-18 | HP Boiler Package | 820-TG-9153 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08626 | 820.10 | 820-10-18 | HP Boiler Package | 820-VE-9180 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08627 | 820.10 | 820-10-18 | HP Boiler Package | 820-VE-9181 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08628 | 820.10 | 820-10-18 | HP Boiler Package | 820-VXE-9182 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08629 | 820.10 | 820-10-18 | HP Boiler Package | 820-VXE-9183 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08630 | 820.10 | 820-10-18 | HP Boiler Package | 820-VXE-9184 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08631 | 820.10 | 820-10-18 | HP Boiler Package | 820-VXE-9185 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08632 | 820.10 | 820-10-18 | HP Boiler Package | 820-XY-9179 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08633 | 820.10 | 820-10-18 | HP Boiler Package | 820-XY-9180 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08634 | 820.10 | 820-10-18 | HP Boiler Package | 820-AT-1006 (Hook-Up) | Installation & Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08635 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-02485.03 | Thermostat loosed need to be fix | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  | 2022-11-21 | 2022-11-18 |  | V |  |  |  | RFC/RFSU
. | 08636 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-02510.02 | Missing sunshade to be provide | A | CI | HEC CI Construction | J.W.JEONG | 2022-09-23 | 2022-12-22 | Walkdown |  |  | 2022-12-22 |  | V |  |  |  | RFC/RFSU
. | 08637 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-02483.05 | Torquing to be done | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  | 2022-11-21 | 2022-11-18 |  | V |  |  |  | RFC/RFSU
. | 08638 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-02510.01 | All on-off valve should be properly clean | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-20 | 2022-11-07 | Walkdown |  |  | 2022-11-05 |  | V |  |  |  | RFC/RFSU
. | 08639 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-02484.03 | Torquing to be done | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  | 2022-11-21 | 2022-11-18 |  | V |  |  |  | RFC/RFSU
. | 08640 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-02485.02 | Enclosure clamp damage | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-29 | 2022-11-25 |  | V |  |  |  | RFC/RFSU
. | 08641 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-02483.01 | SS hanging tag to be provide | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 08642 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-02483.02 | Thermostat should be properly fix | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 08643 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-01878.02 | Calibration of FT need to be done | A | CI | HEC CI Construction | J.W.JEONG | 2022-09-23 | 2022-12-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08644 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-02484.02 | Thermostat should be properly fix | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 08645 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-02484.01 | SS hanging tag to be provide | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 08646 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-02485.01 | SS hanging tag to be provide | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08647 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-02547.02 | 820-PG-9163,9162 Missing hanging tag | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-10-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08648 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-02483.04 | Additional support to be provide | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  | 2022-11-21 | 2022-11-18 |  | V |  |  |  | RFC/RFSU
. | 08649 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-CI-CW-00830.01 | Pressure test to be perform | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08650 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-RFI-EL-SB-01815.01 | Earthing connection to be provided at 820-B0001-MW01 | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-23 | Walkdown |  | 2022-11-22 |  |  | V |  |  |  | RFC/RFSU
. | 08651 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | LCS Blind plug to be install for spare holes 820-B0001-MW01&2 | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08652 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | Provide yellow tag sticker for LCS EMERGENCY PUSH BOTTON at cover side written with Polish Language [ WYŁĄCZNIK AWARYJNY ] for all LCS and ES.. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08653 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | LCSearthing connection to be tightned for 820-B0001-MW01&2 | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08654 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | Instrument JB earthing is missing 820-JA-531.532,502,503,504,505, 820-JD-531,532 and 820-JS-531,532 | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08655 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | Instrument JB earthing is missing 820-JA-533,507, 820-JD-533,534,501,537and 820-JS-533,534. | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08656 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | 820-JP-531,532 Upper burner Ignition transformer box body earthing is missing | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08657 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | 820-LP-531,532 junction box earthing is missing. | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08658 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | 820-LP-507, 503 Heat racing panel earthing is missing. | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08659 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | 820-LP-505 (UPS PDP), 820-LP-504 (Normal PDP) earthing is missing | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08660 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | Monkey ladder and Stair case earthing is missing | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08661 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | Electrical Cable tray is obstructing to 820-LT-9150A instrument ABS enclosure box door. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08662 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | 820-MOV-9150 cable tag to be fix properly. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08663 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | 820-LP-506 (Analyzer panel) earthing is missing. | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08664 | 820.10 | 820-10-18 | HP Boiler Package | EGAT-HEC-820-PRO-PID-00031A~I | Conduit sealing to be done. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08665 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-FT-9153/PT-9152A/B/C/PT-9153 | Drain plug on the cell pot should be tightened properly | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08666 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-FT-9150/PT-9150/PT-9152A/B/C/PT-9161/PT-9197/PT-9180A/B/C/PT-9179/FT-9153/9162/9198/PT-9196 | Provide drain plug on the manifold of instruments | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 08667 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-PT-9178A/B/C/PT-9177/PT-9173A/B/C/PT-9172/FT-9162/9193/820-PDT-9160/LT-9151A/PT-9181 | Provide drain plug on the manifold of instruments | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-18 | Walkdown |  | 2022-11-18 | 2022-11-18 |  | V |  |  |  | RFC/RFSU
. | 08668 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-FV-9161/FV-9160 | Provide drain plug on the positioner of control valve | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-14 | Walkdown |  |  | 2022-11-10 |  | V |  |  |  | RFC/RFSU
. | 08669 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-TG-9154/TG-9160 | Bolt torquing to be done | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-10-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08670 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-TT-9158 | Mounting installaton of instrument to be tightened properly | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 08671 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-TT-9158/BE-9173 | Bonding ground cable of instrument to be connected | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 08672 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-PT-9152A/B/C & PT-9153 | installed additional suport for the drain tube of pressure transmitter | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-18 | Walkdown |  | 2022-11-1 2022-11-18 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 08673 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-FV-9172 | Provide grommet for the edge of cable tray | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 08674 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-FT-9172/FT-9171/FT-9170 | Cable gland in the spare cable entry of flow transmitter should be replace by metal bind plug | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 08675 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-XV-9160 | Air regulator gauge of on/off valve should be in accesible position | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 08676 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-PT-9196 | The cable of pressure transmitter have an insulation damage at loop side | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-29 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 08677 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-FV-9170 | Air breathing cap screw of control valve is missing | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-23 | Walkdown |  | 2022-11-22 | 2022-11-21 |  | V |  |  |  | RFC/RFSU
. | 08678 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-MOV-9150/9151/9152 | Plastic plug on the spare cable entry of MOV should be replace by metal blind plug | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 08679 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-PT-9182 | The cover of pressure transmitter should be tightened properly | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 08680 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-TT-9161 | Replace the blind plug of instrument with Atex specification | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08681 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-XV-9170A | Cable of on/off valve could be arrange properly in order to avoid touching on the ground | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-14 | Walkdown |  |  | 2022-11-10 |  | V |  |  |  | RFC/RFSU
. | 08682 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-PT-9194/PT-9195/VXE-9184 | Missing hanging tag for instrument | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 08683 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-XV-9179 | Metal plate for sensor limit switch to be tightened properly | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-26 |  | V |  |  |  | RFC/RFSU
. | 08684 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-BE-9172/BE-9173 | No hanging tag for flame ignition | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 08685 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General | Provide hanging tag for the air supply tubing of on/off valve on header isolation valve side | B | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08686 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General | Grounding cable of all junction box(JB) to be done | B | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08687 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-LT-9150B/LT-9151B/C/PT-9151/PT-9165C/FT-9152/FT-9151A/B/C | Provide drain plug on the manifold of instrument | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-30 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 08688 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-LP-501/502 | In Burner Start Up Panel & Lower Start Up Panel the name plate for breaker switch are not matching to the P&ID,to be verfied | B | EM | HEC MS Design | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08689 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-TT-9151 | No sunshade for the instrument | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-07 | Walkdown |  |  | 2022-11-05 |  | V |  |  |  | RFC/RFSU
. | 08690 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-TT-9151/TT-9152 | Missing blind plug on the spare cable entry of instrument | C | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 08691 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-TT-9155 | Tube cable tray to be fix | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-09 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 08692 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-LT-9151B | Heating element in the enclosure box to be move away to avoid abstruction during opening/closing of isolation valve | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-28 |  | V |  |  |  | RFC/RFSU
. | 08693 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-TT-9156/TT-9152 | The support of tube cable tray to be fix | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-14 | Walkdown |  |  | 2022-11-10 |  | V |  |  |  | RFC/RFSU
. | 08694 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-TT-9151 | The temperature element(sensor cable) of transmitter is missing | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-09 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 08695 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-VXE-9182 | Cable glanding to be fix | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 08696 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-JA-506 | Provide cable tag for all vibraton transmitter at JB side | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-12-01 | Walkdown |  | 2022-11-30 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 08697 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-FT-9161C | Tubing installation is not completed | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-14 | Walkdown |  |  | 2022-11-10 |  | V |  |  |  | RFC/RFSU
. | 08698 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-LT-9150 | The cable tray support for the power of analyzer should be move away to avoid abstruction during opening of enclosure box | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08699 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001 (820-AT-1007, 820-AT-1010) | Provide additional support (or cable tray) for heated sample line | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08700 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001 (820-AT-1007, 820-AT-1010) | Sample pressure reducer with pressure gauge ATEX marking shall be verified & provide nameplate as (PR1) as refer VENDOR documentation no: V-SEC-I14-000-00000-00024 | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08701 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001 (820-AT-1007, 820-AT-1010) | Nameplate with 820-AT-1007 & 820-AT-1010 for the main door of analyzer cabinet shall be provided according V-SEC-I14-000-00000-00022 | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08702 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001 (820-AT-1007, 820-AT-1010) | Missing ground cable for the power switch of analyzer as well as for cables | A | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08703 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001 (820-AT-1007, 820-AT-1010) | The nameplate of analyzer panel shall be according to V-SEC-I14-000-00000-00024 | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08704 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001 (820-AT-1007, 820-AT-1010) | The cable nameplate with TAG NO is not vissible, it is obstructed by cable tray. | B | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08705 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001 (820-AT-1007, 820-AT-1010) | Atmosphere vent tube shall be installed | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08706 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001 (820-AT-1007, 820-AT-1010) | The nameplate of analyzer panel shall be bilingual (Polish nameplate shall be added). | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08707 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001 (820-AT-1007, 820-AT-1010) | Calibration cylinders shall be installed & all the necessary document shall be provided inside cabinet pocket | B | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-12 |  | V |  |  |  | RFC/RFSU
. | 08708 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001 (820-AT-1007, 820-AT-1010) | Aluminium part of isolation was demaged in several places - it shall be repaired. | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-28 |  | V |  |  |  | RFC/RFSU
. | 08709 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001 (820-AT-1007, 820-AT-1010) | There is discrepancy between site and V-SEC-I14-000-00000-00022 (horn direction installation) - it shall be verified. | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08710 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001 (820-AT-1007, 820-AT-1010) | There is discrepancy between site and V-SEC-I14-000-00000-00022 (instrument air flange direction installation) - it shall be verified. Also the flange shall be plugged for protection against dust and water. | C | CI | CW Office | Owner Maintenance team | 2022-09-23 |  | Walkdown |  |  | 2022-12-20 | Rejected... DWG need to update as per site condition (ENG) | V |  |  |  | RFC/RFSU
. | 08711 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001 (820-AT-1007, 820-AT-1010) | All tubes (i.e. for calibration gases) shall be plugged for protection against dust and water. | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-26 |  | V |  |  |  | RFC/RFSU
. | 08712 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | All nameplates shall be according to V-KWB-M10-820-B0001-00083 | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08713 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | Transmitter and sensor cables shall have TAG NO. | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-26 |  | V |  |  |  | RFC/RFSU
. | 08714 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | All tubes on analyzer rack shall be described according to V-KWB-M10-820-B0001-00083 | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08715 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | Transmitter (820-AT-9160) LO O2/HI O2/HI tubes connection shall be verified | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2023-01-11 | Walkdown |  |  | 2022-12-23 |  | V |  |  |  | RFC/RFSU
. | 08716 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | Signal cable between transmitter and sensor shall be mounted and secured properly | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-23 | Walkdown |  | 2022-11-22 | 2022-11-21 |  | V |  |  |  | RFC/RFSU
. | 08717 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | Power cable shall be mounted and secured properly | A | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08718 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | Round box mounting method shall be corrected (metal junction box on the analyzer housing is loose - please verify the need for additional mounting due to heavy weight of the box). | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08719 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | Grounding cable for analyzer sensor shall be connected | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-23 | Walkdown |  | 2022-11-22 | 2022-11-21 |  | V |  |  |  | RFC/RFSU
. | 08720 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | The cover of junction box shall be tightened properly | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-18 | Walkdown |  | 2022-11-18 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 08721 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | To avoid shaking analyzer sensor additional support shall be added | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08722 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | All TAG NOs shall be according to V-KWB-M10-820-B0001-00083 | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08723 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | Cable tag plate inside the analyzer sensor was found to be broken off the screw mounting. Analyzer sensor shall be checked. | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08724 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | All tubes (i.e. for calibration gases) shall be plugged for protection against dust and water. | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-12-01 | Walkdown |  |  | 2022-11-30 |  | V |  |  |  | RFC/RFSU
. | 08725 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AR-003 (820-AT-9160) | Calibration cylinders shall be installed | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2023-01-11 | Walkdown |  |  | 2022-12-23 |  | V |  |  |  | RFC/RFSU
. | 08726 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-002 (820-AT-9191/9192/9193/9194/9195) | All nameplates shall be according to V-KWB-M10-820-B0001-00026 | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08727 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-002 (820-AT-9191/9192/9193/9194/9195) | The nameplate of analyzer panel shall be bilingual (Polish nameplate shall be added) | A | EM | HEC MS Design | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08728 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-002 (820-AT-9191/9192/9193/9194/9195) | Analyser sensors shall be installed | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 08729 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-002 (820-AT-9191/9192/9193/9194/9195) | 820-AC-002 electrical power supply shall be done | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-23 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08730 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-002 (820-AT-9191/9192/9193/9194/9195) | Cable glanding for analyzer sensors shall be fixed properly | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-12-01 | Walkdown |  | 2022-11-30 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 08731 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-002 (820-AT-9191/9192/9193/9194/9195) | All cables shall have TAG NO. | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-26 |  | V |  |  |  | RFC/RFSU
. | 08732 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-002 (820-AT-9191/9192/9193/9194/9195) | Missing analyzer cabinet TAG NO. | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-28 |  | V |  |  |  | RFC/RFSU
. | 08733 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-AC-001, 820-AT-9160, 820-AT-1007, 820-AC-002 | During Walk Down cannot be verified calibration for 820-AC-001, 820-AC-002, 820-AT-9160 and installation&pressure test&calibration for 820-AT-1006. Necessary additional Walk Down for these devices, during which the reported punch list of day 23.09.2022 will also be verified | A | CI | HEC CI Construction | Owner Maintenance team | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-06 |  | V |  |  |  | RFC/RFSU
. | 08734 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | 820-JA-501 | Grounding cables shall be connected to the cable gland side | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-24 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 08735 | 820.10 | 820-10-18 | 820-B0001 | 820-VGF-268 | Permanent blind to be installed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08736 | 820.10 | 820-10-18 | 820-B0001 | 820-VGF-268 | U-bolt to be fixed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08737 | 820.10 | 820-10-18 | 820-B0001 | 820-VGF-268 | Flange to be touch-up painted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08738 | 820.10 | 820-10-18 | 820-B0001-V02 | 820-TT-9152 / 9156 | Stand support need to be fixed | B | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-28 |  | V |  |  |  | RFC/RFSU
. | 08739 | 820.10 | 820-10-18 | 820-B0001 | 820-SG-9181 | Corrossion to be removed | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08740 | 820.10 | 820-10-18 | 820-B0001 | EGAT-HEC-820-PRO-PID-00031C | Missing tag ( beside KE-9186) | B | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-23 | Walkdown |  | 2022-11-22 | 2022-11-21 |  | V |  |  |  | RFC/RFSU
. | 08741 | 820.10 | 820-10-18 | 820-B0001 | EGAT-HEC-820-PRO-PID-00031C | Cover to be tigthened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08742 | 820.10 | 820-10-18 | 820-B0001 | 820-TE-9186 | To be tightened | B | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-26 |  | V |  |  |  | RFC/RFSU
. | 08743 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | Missing grease nipple cover | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08744 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | Manhole cover to be hand tight | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08745 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | Rust to be removed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08746 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | Drainage line to be provided on skid base frame | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08747 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | Motor (shaft) cover need to be tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08748 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | Motor cover is touching the motor shaft | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08749 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | Missing lock washer and loose bolt to be tighten and protected against self-loosening during fan operation | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08750 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | Proper access to be provided for fan and motor maintenance- handrails for existing steps, dimensioning according to HSE reqirements. | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08751 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X01 | missing bolt on the ladder | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08752 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X04/05 | Rusted steel structure support on the silencer to be touch-up painted | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08753 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X04/05 | Rust on checkered plate to be removed ( on the platform) | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08754 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X04/05 | Housekeeping to be done ( on silencer platform) | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08755 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X04/05 | Handrail to be touch-up painted | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08756 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X04/05 | Aluminum roof with CS screw to be repleaced | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  | Changed from Category B |  | IN |  |  |  | 2023-03-10 | RFC/RFSU
. | 08757 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X04/05 | Housekeeping to be done ( on the roof near to the silencer) | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-18 | Walkdown | [8 empty] | RFC/RFSU
. | 08758 | 820.10 | 820-10-18 | 820-B0001 | 820-VGD-068 / 069 | Temporary tape at the thread to be removed | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08759 | 820.10 | 820-10-18 | 820-B0001 | 820-VGF-020 / 018 | Corroded lock and key to be replaced | C | COMM | HEC COMM | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08760 | 820.10 | 820-10-18 | 820-B0001 | 820-VLF-019 | To be relocated at safe location | C | EM | HEC MS Design | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08761 | 820.10 | 820-10-18 | 820-B0001 | 820-VLF-019 | Rusted gate valve and valve handle to be touch-up painted | B | PA | HEC PA Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08762 | 820.10 | 820-10-18 | 820-B0001 | 820-VGF-025 | Corroded lock and key to be replaced | C | COMM | HEC COMM | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08763 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X04/05 | Handrail to be modified at the top platform of the silencer going to the notrh side platform ( Gadp between handrail to handrail is big) | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08764 | 820.10 | 820-10-18 | 820-B0001 | 820-PSV-9150 / 9151 | Rust to be removed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08765 | 820.10 | 820-10-18 | 820-B0001 | General | Safety gate designed to be verefied with Engineering | C | EM | HEC MS Design | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-02-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08766 | 820.10 | 820-10-18 | 820-B0001 | General | Safety gates works improperly - falling out barier | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08767 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Ladders is too close to the I-beam support platform need to be modified | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08768 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Crack paint near 820-VGD-080 to be repaired | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08769 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Handrail installation to be verefied with engineering near 820-VGD-086 | C | EM | HEC MS Design | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08770 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Drain line height to be verefied with engineering near 820-VGF-334 | C | EM | HEC MS Design | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-02-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08771 | 820.10 | 820-10-18 | 820-B0001 | Silencer | Ladder to be fixed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-01-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08772 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Loose gate valve handle ( Nut is missing) near 820-VGD-089 | A | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08773 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Permanent blind to be installed near PG-9162 | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08774 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Permanent blind to be installed near 820-VGF-266 | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08775 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | missing sight glasses | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08776 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | Motor to be touch-up painted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08777 | 820.10 | 820-10-18 | 820-B0001 | General | Gate valve handle to be touch-up painted | B | PA | HEC PA Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08778 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | missing bolt and nut on manhole | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08779 | 820.10 | 820-10-18 | 820-B0001 | 820-VGF-281 / 282 | flexible hose to be connected | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08780 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W02 | Broken handle for motor cover to be repaired | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08781 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W02 | Touch-up painiting on motor to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08782 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W02 | Missing lock washer and loose bolt to be tighten | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08783 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W02 | Proper access to be provided for fan and motor maintenance- handrails for existing steps, dimensioning according to HSE reqirements. | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08784 | 820.10 | 820-10-18 | 820-B0001 | 820-SG-9183 / 9182 | Loose bolt to be tightened and rust to be remove | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08785 | 820.10 | 820-10-18 | 820-B0001 | 820-SG-9183 / 9182 | Support to be fixed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08786 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W02 | Water insisde the skid to be removed and drain line to be installed | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08787 | 820.10 | 820-10-18 | 820-B0001 | 820-LT-9150A | When opening the cover it is colliding with the cable tray | B | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-28 |  | V |  |  |  | RFC/RFSU
. | 08788 | 820.10 | 820-10-18 | 820-B0001 | 1 st Level | Rust on the igniter to be cleaned | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08789 | 820.10 | 820-10-18 | 820-B0001 | 2nd Level | Drain line pipe support to be fixed | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08790 | 820.10 | 820-10-18 | 820-B0001 | 2nd Level | Rusted bolt on the igniter to be cleaned | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08791 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X01 | Ladder - upper part - missing bolts. | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08792 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X01 | Rusted platforms, ladders, handrails, gratings to be cleaned and painted. | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08793 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X01 | Safety gates are not fitted - don't close properly. | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08794 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X01 | Gratings on platforms not tightened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08795 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X01 | Rusted bracked / mounting clip for personal protection - "first flor". | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08796 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X01 | Noozles and flanges for sample probes rusted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08797 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X01 | Manhole bolts not tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08798 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X01 | Rusted bolts on flange connections | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08799 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X01 | Plastic covers to be removed from flange connections (test nozzles) | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08800 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X01 | Drain trench missing - see EGAT-HEC-820-PRO-PID-00031C | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-03-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08801 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X01 | General cleaning of the stack facility. | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08802 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | Both FD Fan compensators are rusted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08803 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W02 | Both GR Fan compensators are rusted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08804 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-X01 | Flue Gas to Stack compensator is rusted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08805 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Flue Gas compensators are rusted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08806 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Combustion Air compensators are rusted | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08807 | 820.10 | 820-10-18 | 820-B0001 | General | Destroyed Cladding to be repleaced | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  | Changed from Category B |  | IN |  |  |  | 2023-03-10 | RFC/RFSU
. | 08808 | 820.10 | 820-10-18 | 820-B0001 | General | Mastic sealing to be repleaced or supplemented where required | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  | Changed from Category B |  | IN |  |  |  | 2023-03-10 | RFC/RFSU
. | 08809 | 820.10 | 820-10-18 | 820-B0001 |  | Installation not finalized. Few connections not executed. | A | PI | HEC PI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08810 | 820.10 | 820-10-18 | 820-B0001 |  | Not finalized precommissioning activities and rust inside the valve and at the flange | C | COMM | HEC PI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2023-03-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08811 | 820.10 | 820-10-18 | 820-B0001 |  | Rust on safety valves elements and connection | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08812 | 820.10 | 820-10-18 | 820-B0001 |  | Not properly fixed I&C connection at Temperature Transmitter 820-TT-9154 | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-09 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 08813 | 820.10 | 820-10-18 | 820-B0001 |  | Not finalized inuslation works | C | IN | HEC IN Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08814 | 820.10 | 820-10-18 | 820-B0001 |  | Rust on every valve locking devices | C | COMM | HEC PI Construction | Mr. Krzysztof Nolbert | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08815 | 820.10 | 820-10-18 | 820-B0001 |  | Not possible to move wheel at valve 820-VGD-068 | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08816 | 820.10 | 820-10-18 | 820-B0001 |  | Touch paint required for many elements: steel structure, piping, flanges, handrails etc. | C | ME | HEC PA Construction | Mr. Krzysztof Nolbert | 2022-09-23 |  | Walkdown | [8 empty] | RFC/RFSU
. | 08817 | 820.10 | 820-10-18 | 820-B0001 |  | Draining from transmitter hook-up directed to the cable trace | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-12-21 | Walkdown |  |  | 2022-12-21 |  | V |  |  |  | RFC/RFSU
. | 08818 | 820.10 | 820-10-18 | 820-B0001 |  | Few boiler nozzles are protected by wooden blind flanges | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08819 | 820.10 | 820-10-18 | 820-B0001 |  | Rust and white dirt inside boiler nozzles (protected by wooden blind flanges | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08820 | 820.10 | 820-10-18 | 820-B0001 |  | Control boxes and Junction boxes are not properly closed (no bolts) | A | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08821 | 820.10 | 820-10-18 | 820-B0001 |  | Part of piping supports not properly adjusted (not supporting) | A | PI | HEC PI Construction | Mr. Krzysztof Nolbert | 2022-09-23 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08822 | 820.10 | 820-10-18 | AUX 2 | Drawing No. EGAT-HEC-820-PRO-PID-00031B / Line No. 820-3/4"-HS-91556-KS13H(65) | Support not resting | A | PI | HEC PI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08823 | 820.10 | 820-10-18 | AUX 2 | Drawing No. EGAT-HEC-820-PRO-PID-00031B / Line No. 820-3/4"-HS-91556-KS13H(65) | Temporary blind to be remove and BT report to be attached | A | PI | HEC PI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08824 | 820.10 | 820-10-18 | AUX 2 | Drawing No. EGAT-HEC-820-PRO-PID-00031B / Line No. 820-10"-HS-91552-MS-13-A-H(100) | Temporary gasket to be remove and BT report to be attached near the MOV 9150 | A | PI | HEC PI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08825 | 820.10 | 820-10-18 | AUX 2 | Drawing No. EGAT-HEC-820-PRO-PID-00031B | Near the TV 9159 3 supports not resting | A | PI | HEC PI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08826 | 820.10 | 820-10-18 | AUX 2 | Drawing No. EGAT-HEC-820-PRO-PID-00031B | Near the PG 9152 3/4" vent line support not resting properly (top of boiler) | A | PI | HEC PI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-10-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08827 | 820.10 | 820-10-18 | AUX 2 | Drawing No. EGAT-HEC-820-PRO-PID-00031A / Line No. 820-6"-BW-91502-MS-13-ET(40) | 6" Valve indicator missing | C | PI | HEC PI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2023-04-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08828 | 820.10 | 820-10-18 | AUX 2 | Drawing No.EGAT-HEC-820-PRO-PID-00031A / Line No. 820-6"-BW-91504-MS-13-A-H(50) | Item TE 9151 missing | A | CI | HEC CI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-11-14 | Walkdown |  |  | 2022-11-10 |  | V |  |  |  | RFC/RFSU
. | 08829 | 820.10 | 820-10-18 | AUX 2 | Drawing No. EGAT-HEC-820-PRO-PID-00031C | U-blot loose nuts near the LT 9151A | B | PI | HEC PI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08830 | 820.10 | 820-10-18 | AUX 2 | Drawing No. EGAT-HEC-820-PRO-PID-00031D | Flanges of the instruments PT 9176A, PT 9176B and PT 9176C to be painted and insulation to be done | A | PI | HEC PI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08831 | 820.10 | 820-10-18 | AUX 2 | Drawing No. EGAT-HEC-820-PRO-PID-00031D / Line No. 820-8"-FG-91722-B1A1-ET(25) | Item FE 9171 to be installed | A | PI | HEC PI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08832 | 820.10 | 820-10-18 | AUX 2 | Drawing No. EGAT-HEC-820-PRO-PID-00031D / Line No. 820-10"-FG-91723-B1A1-ET(25) | Flanges of the instruments PT 9177, PT 9178A, PT 9178B AND PT 9178C to be painted | A | PI | HEC PI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08833 | 820.10 | 820-10-18 | AUX 2 | Drawing No. EGAT-HEC-820-PRO-PID-00031E / Line No. 820-2"-MS-91571-MS-11-H(40) | Handwheel not proper fix near the PT 9179 | A | PI | HEC PI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08834 | 820.10 | 820-10-18 | AUX 2 | Drawing No. EGAT-HEC-820-PRO-PID-00031E / Line No. 820-3/4"-A-91909-B1A1-N | Not proper operate instrument support behind valve (Near the PT-9181). | A | CI | HEC CI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-25 |  | V |  |  |  | RFC/RFSU
. | 08835 | 820.10 | 820-10-18 | AUX 2 | Drawing No. EGAT-HEC-820-PRO-PID-00031F / Line No. 820-3/4"-SOL-91763-B1A1-N | Support not resting near the XV 9172A | A | PI | HEC PI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 08836 | 820.10 | 820-10-18 | AUX 2 |  | Verify with ISO dwg 9170103 | A | PI | HEC PI Construction | Mr. Krystian Iwanski | 2022-09-26 | 2022-10-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09108 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | Pneumatic actuator and control mechanism rusted - to be cleaned and painted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09109 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W02 | Pneumatic actuator and control mechanism rusted - to be cleaned and painted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09110 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | Oil leakage from luber mounted on the motor | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09111 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W01 | Loose tag plate 820-TE-9185 - (not attached to the instrument). | B | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 09112 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | According to V-KWB-M10-820-B0001-00031 Bolts/ screws used for securing jacketing sheets shall be compatible with the type of sheet. Aluminium sheet can not be fixed by carbon steel screws due to corrosion issue. | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09113 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Rust to be removed from the roof. | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09114 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Vent lines to be extended up to 3m above access platform: 820-3/4"-AV-91628-MS-11-P25 820-3/4"-AV-91629-MS-11-P25 820-3/4"-AV-91640-MS-11-P25 | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09115 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Wet unprotected wool insulation on Flue Gas Duct to be replaced and cladding to be finished. | B | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09116 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Rust to be removed from uninsulated / still visible parts of flue gas ducts - insulated already parts to be randomly verified if rust was removed before insulation works. | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-03-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09117 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 -Flue Gas Duct | Lamp lighting installed to low - shall be relocated where necessary | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09118 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 -Flue Gas Duct | Air Flue gas test ports (nozzles) temporary blinds and plasic protection to be changed to permament | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09119 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 -Flue Gas Duct | Missing foundation for ladder - not fixed ( close to the stack) | A | CV | HEC CV Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09120 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 -Flue Gas Duct | Access to the platform not safe, grating not supprted, saferty cage too large, safety gate doesn't work, | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09121 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 -Flue Gas Duct | Rusted supporting steel structure | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09122 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 -Flue Gas Duct | Gratings not fixed on platforms | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09123 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 -Flue Gas Duct | Cladding on nozzles not finished | B | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09124 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 - Flue Gas Duct | Cladding on Flue gas not fixed and tightened properly - missing nuts, unscrewed places - necessary selflocking nuts or other solution. | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-03-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09125 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 - E01 | Cladding on Economizer to be corrected - holes after screws to be sealed and missing screws to be supplemented. | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09126 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 - E01 | Flanges on Economizer are not permamently plinded | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09127 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 - E01 | Nameplate of Economizer rusted and destroyed | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09128 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 - W02 | Manhole size not in accordance with PID and BEED requirements | B | EM | HEC MS Design | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09129 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W02 | Missing grease nipple cover | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09130 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W02 | Cladding on Fan not fixed and tightened properly - missing nuts, unscrewed places - necessary selflocking nuts or other solution. Nut shall protrude stud bolts at least 2-3 threads. | B | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09131 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W02 | Wet wool around manhole to be repleaced / cladding to be finished | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09132 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001-W02 | CWS/ CWR lines not connected - open flanges | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09133 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Missing handrail in front of water drum (manhole area) - first floor | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09134 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Bank drain - nozzle (water drum) rusted. | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09135 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Bank drain - nozzle not blinded - temporary protection only. | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09136 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Shaking LT-9150A support to be fixed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2023-01-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09137 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Missing checkered plate on platform around pipe line no. 820-8"-FG-91723-B1A1-ET25 to be supplemented. | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09138 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Bolts on burner / igniter to be tightened. | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-23 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09139 | 820.10 | 820-10-18 | 820-B0001 | 820-B0001 | Steam traps type inconsistent with BEDD requirement - to be solved. | C | EM | HEC MS Design | Mr. Krzysztof Kaliszyk | 2022-09-23 |  | Walkdown | [8 empty] | RFC/RFSU
. | 09140 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | Insulation missing - walkdown to be repeated | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-09-23 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09141 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | Electrical tracing on pipelines and instruments missing - walkdown to be repeated | B | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09142 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | Insulation incomplete/wet/damaged to be replaced - walkdown to be repeated | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-09-23 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09143 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | Handwheels for manual valves to be tightened - walkdown to be repeated | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09144 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | Rusty elements (valves, pining, supports etc.) - walkdown to be repated | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09145 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | Housekeeping to be done | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-09-23 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09146 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031A | Missing plug on drain valve upstream of FV-9150 | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09147 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031A | 6'' manual valve upstream of FV-9150 incomplete | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09148 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | Drain outlets are too close to the ground - outlet pipelines to be shortened. | A | PI | HEC PI Construction | Mr. Piotr Słowik | 2022-09-23 | 2022-10-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09149 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031B | Drain line from E02 with 2 manual valves to be relocated downstream of TG-9152 in P&ID. | B | EM | HEC PI Design | Ms. Paulina Bajer | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09150 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031B | Drain valve missing in P&ID between spectacle blind and 4'' valve on continous blowdown line (no. 91608) | B | EM | HEC PI Design | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09151 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package |  | spectacle blind instead of spacer to be installed upstream of MOV-9150 | A | EM | HEC MS Design | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09152 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031B | Missing flange connection upstream of TG-9152 in P&ID. | B | EM | HEC PI Design | Ms. Paulina Bajer | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09153 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031B | Suppport for BFW line to X03 to be provided. | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09154 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | Several manual valves unable to operate - Walkdown to be repeated | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09155 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031B | MOV- 9150 - access to be provided to the handwheel. | C | EM | HEC MS Design | Ms. Małgorzata Juszczyk | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09156 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031B | 1 1/2'' valve on BFW line to desuperheater (no. 91509) - no access to the handwheel provided (to be isntalled horizontally) | C | EM | HEC MS Design | Mr. Piotr Słowik | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09157 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031B | Nameplates for XVs and MOVs to be verified according to the latest approved documentation. | C | EM | HEC MS Design | Ms. Paulina Bajer | 2022-09-23 | 2023-04-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09158 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031B | Missing information at Site that Air line is under pressure | A | COMM | HEC COMM | Mr. Piotr Słowik | 2022-09-23 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09159 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031B | Phosphate drain location to be verified (line no. 91541) - safe location for operators to be provided | C | EM | HEC MS Design | Ms. Małgorzata Juszczyk | 2022-09-23 | 2023-02-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09160 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | All temporary blinds to be replaced. | A | ME | HEC ME Construction | Mr. Jaroslaw Pykosz | 2022-09-23 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09161 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031C | FV-9160/9161 - hanging tags missing. | B | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-09-23 | 2022-11-14 | Walkdown |  |  | 2022-11-10 |  | V |  |  |  | RFC/RFSU
. | 09162 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031C | Leakage on dry vent (F.D. Fan) | A | ME | HEC ME Construction | Mr. Marek Łaskawski | 2022-09-23 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09163 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031C | VE-9184/9185 - hanging tags missing. | B | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-09-23 | 2022-11-14 | Walkdown |  |  | 2022-11-11 |  | V |  |  |  | RFC/RFSU
. | 09164 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031C | TE-9186 - double hanging tag with different tag nos. | B | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 09165 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031C | Safe acces to F.D. fan to be provided (e.g. railing) | C | ME | HEC ME Construction | Mr. Jaroslaw Pykosz | 2022-09-23 |  | Walkdown |  | Changed from Category B |  |  | V |  |  | 2023-03-10 | RFC/RFSU
. | 09166 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031C | PT-9161 to be replaced with PG in P&ID | B | EM | HEC PI Design | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-12-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09167 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031C | Boiler system to be cleaned | C | ME | HEC ME Construction | Mr. Piotr Słowik | 2022-09-23 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09168 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031C | Support for PT-9164/9165A/B/C/TE-9161/PG-9163/TG-9161 to be provided. | A | CI | HEC CI Construction | Mr. Piotr Słowik | 2022-09-23 | 2022-11-14 | Walkdown |  |  | 2022-11-11 |  | V |  |  |  | RFC/RFSU
. | 09169 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031C | FT-9160 : hanging tag missing. | B | CI | HEC CI Construction | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-11-15 | Walkdown |  |  | 2022-11-11 |  | V |  |  |  | RFC/RFSU
. | 09170 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031C | Only one drain from FGR present at Site - to be verified against P&ID. | A | ME | HEC ME Construction | Mr. Marek Łaskawski | 2022-09-23 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09171 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031C | Drain line (2''-NY-91662-MS-11) to be routed to the trench as per P&ID. | A | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09172 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031C | Manhole size of FGR to verified in P&ID. | B | EM | HEC PI Design | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-12-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09173 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031D | PG-9172 to be relocated for better visibility during valve operation | A | CI | HEC CI Construction | Mr. Piotr Słowik | 2022-09-23 | 2022-12-02 | Walkdown |  | Rejected.. 90 degree more need to rotate. | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 09174 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031D | PG-9170 not installed yet | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 09175 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031D | Hanging tags for PCVs to be verified (PRV specified in hanging tags) | B | CI | HEC CI Construction | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-12-01 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 09176 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031D | PG-9173 to be relocated with 180 degress for better visibility during operation | A | CI | HEC CI Construction | Mr. Piotr Słowik | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 09177 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031D | Manual 8'' valve on bypass line of FV-9170 incomplete | C | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-09-23 | 2023-04-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09178 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031D | No access to N2 nozzle on off-gas line (collision with cable trays) | B | ME | HEC ME Construction | Mr. Piotr Słowik | 2022-09-23 | 2022-11-21 | Walkdown |  | change category from A to B |  |  | V |  |  |  | RFC/RFSU
. | 09179 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031E | PT-9197/PG-9179 to be relocated in P&ID | B | EM | HEC PI Design | Mr. Jaroslaw Pykosz | 2022-09-23 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 9180 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031E | TT-9198 to be relocated in P&ID | B | EM | HEC PI Design | Mr. Jaroslaw Pykosz | 2022-09-23 | 2022-12-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09181 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031E | Missing plug on drain valve on MP steam | A | PI | HEC PI Construction | Mr. Jaroslaw Pykosz | 2022-09-23 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09182 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031E | incorrect position of spectacle blind on MP steam line. | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09183 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031E | PG-9175/9176 to be relocated for better visibility | A | CI | HEC CI Construction | Mr. Piotr Słowik | 2022-09-23 | 2022-11-10 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 09184 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031E | Drain valve on plant air valve to be relocated in P&ID downstream of PT-9182C | B | EM | HEC PI Design | Ms. Paulina Bajer | 2022-09-23 | 2022-12-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09185 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031E | PRV-9173 to be corrected to PCV in P&ID; hanging tag to be corrected | B | EM | HEC PI Design | Ms. Paulina Bajer | 2022-09-23 | 2022-12-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09186 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031E | Missing hanging tags on flame scanners | B | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-09-23 | 2022-12-01 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 09187 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031E | Hanging tags for hoses missing at Site | B | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 09188 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031E | Hanging tags for rods and flame scanners missing at Site - upper burner to be verified against P&ID | B | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 09189 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031E | Limited acces to instrument isolation valve when insulation will be added (e.g. PG-9188, PG-9185, 9180) | A | CI | HEC CI Construction | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 09190 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031G | missing labels on start-up panels. | A | CI | HEC CI Construction | Mr. Marek Łaskawski | 2022-09-23 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09191 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031G | Buttons on panel have no tag nos. | A | CI | HEC CI Construction | Mr. Marek Łaskawski | 2022-09-23 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09192 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031G | Improper Polish translation on control panels | B | EM | HEC MS Design | Mr. Marek Łaskawski | 2022-09-23 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 09193 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031G | Upper burner fuel gas stop button on control panel is green | A | EM | HEC MS Design | Mr. Marek Łaskawski | 2022-09-23 | 2022-12-27 | Walkdown |  |  | 2022-12-14 | 2022-12-15 | V |  |  |  | RFC/RFSU
. | 09194 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031I | Flexible hose not connected or blinded on cooling water system | A | PI | HEC PI Construction | Mr. Jaroslaw Pykosz | 2022-09-23 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09195 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031I | Cooling water inlet/outlet lines to FGR) shaking (additional support to be provided) | A | PI | HEC PI Construction | Mr. Jaroslaw Pykosz | 2022-09-23 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09196 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031I | Drain valve on CWS to FGR fan to be relocated in P&ID downstream of the bypass line | B | EM | HEC PI Design | Mr. Marek Łaskawski | 2022-09-23 | 2022-12-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09197 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031I | Drain valves on CWS/CWR line to/from FD Fan missing at Site | B | EM | HEC MS Design | Mr. Marek Łaskawski | 2022-09-23 | 2022-12-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09198 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | Dangerous sharp screws beyond the insulation | C | IN | HEC IN Construction | Ms. Małgorzata Juszczyk | 2022-09-23 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09199 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | Collision of ladder with other elements (e.g. cable trays) - safe walking impossible | B | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09200 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | MC Walkdown for the entire piping scope was not performed. The Owner is waiting for the Contractor's reply when piping inspector will be available to proceed with Walkdown. | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-23 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09201 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | Loose heaters in transmitter boxes | A | CI | HEC CI Construction | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 09202 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031B | Collision of the LT-9150A transmitter box housing with structural elements during opening | A | CI | HEC CI Construction | Ms. Małgorzata Juszczyk | 2022-09-23 | 2022-12-02 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 09203 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031H | No. Of CBD line to sampling system to be verified in P&ID (fluid code to be verified against PID 00031B - BD -> SC.) | B | EM | HEC PI Design | Ms. Paulina Bajer | 2022-09-23 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09204 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031B | No. Of BFW line from economizer to be verified in P&ID (fluid code to be corrected from HS to BW) | B | EM | HEC PI Design | Ms. Paulina Bajer | 2022-09-23 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09205 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031F | Loose limit switch limiter XZS9179 | A | CI | HEC CI Construction | Mr. Rożek | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-26 |  | V |  |  |  | RFC/RFSU
. | 09206 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | General comment | Missing washers on flange nuts. | B | ME | HEC ME Construction | Mr. Damian Drag | 2022-09-23 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09207 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031C | if possible please move the cylinder rack for AT-9160 to the ground level. | A | CI | HEC CI Construction | Mr. Damian Drag | 2022-09-23 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09208 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031A | Nameplate of FT-9150 to be verified against approved documentation. | B | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-29 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 09209 | 820.10 | 820-10-18 | AUX/820-HP Boiler Package | PRO-PID-00031D | FE-9171/9170 - namaplates, tags to be added at Site. | B | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-09-23 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-26 |  | V |  |  |  | RFC/RFSU
. | 09210 | 820.10 | 820-10-24 | 820-V0003 | n/a | 820-V0003: Final Inspection to be done | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09211 | 820.10 | 820-10-24 | 820-P0002A/B | n/a | 820-P0002A/B: Final Inspection to be done | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09212 | 820.10 | 820-10-24 |  | 810PR-BW-1001 | Re-instatement (after Hydro) 810PR-BW-1001 | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-29 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09213 | 820.10 | 820-10-24 |  | 820BF-BW-1004 | Inspection of Final Painting to be done | A | PA | HEC PA Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09214 | 820.10 | 820-10-24 |  | 810PR-BW-1002 | Final Appeareance Inspection to be done | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09215 | 820.10 | 820-10-24 |  | 810PR-LC-1003 | Final Appeareance Inspection to be done | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09216 | 820.10 | 820-10-24 |  | 810PR-LS-1002 | Final Appeareance Inspection to be done | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09217 | 820.10 | 820-10-24 |  | 810PR-LS-1004 | Final Appeareance Inspection to be done | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09218 | 820.10 | 820-10-24 |  | 810PR-LS-1003 | Final Appeareance Inspection to be done | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09219 | 820.10 | 820-10-24 |  | 810PR-TRV-1002 | Final Appeareance Inspection to be done | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09220 | 820.10 | 820-10-24 |  | 810PR-TRV-1001 | Final Appeareance Inspection to be done | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09221 | 820.10 | 820-10-24 |  | 820BF-BW-1002 | Final Appeareance Inspection to be done | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09222 | 820.10 | 820-10-24 |  | 820BF-BW-1003 | Final Appeareance Inspection to be done | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09223 | 820.10 | 820-10-24 |  | R.820-MP0002A/B | Cable Termination & Test to be done | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-29 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09224 | 820.10 | 820-10-24 |  | 820-AR-001 | Inspection for Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09225 | 820.10 | 820-10-24 |  | 820-AR-002 | Inspection for Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09226 | 820.10 | 820-10-24 |  | 820-FE-1003 | Inspection for Installation | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09227 | 820.10 | 820-10-24 |  | 820-FE-1004 | Inspection for Installation | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09228 | 820.10 | 820-10-24 |  | 820-FO-1001 | Inspection for Calibration / Installation | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09229 | 820.10 | 820-10-24 |  | 820-LT-1002A | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09230 | 820.10 | 820-10-24 |  | 820-LG-M-1001 | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09231 | 820.10 | 820-10-24 |  | 820-PT-1002 | Inspection for Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09232 | 820.10 | 820-10-24 |  | 820-PT-1003 | Inspection for Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09233 | 820.10 | 820-10-24 |  | 820-PT-1004A | Inspection for Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09234 | 820.10 | 820-10-24 |  | 820-PT-1004B | Inspection for Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09235 | 820.10 | 820-10-24 |  | 820-FT-1003 | Inspection for Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09236 | 820.10 | 820-10-24 |  | 820-FT-1004 | Inspection for Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09237 | 820.10 | 820-10-24 |  | 820-FV-1003 | Inspection for Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09238 | 820.10 | 820-10-24 |  | 820-FV-1004 | Inspection for Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09239 | 820.10 | 820-10-24 |  | 820-PRV-0001A | Inspection for Installation | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09240 | 820.10 | 820-10-24 |  | 820-PRV-0001B | Inspection for Installation | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09241 | 820.10 | 820-10-24 |  | EGAT-HEC-820-PRO-PID-00021 | Earthing bonding missing to be provided for Space heater Box to motor for 820-MP0002A | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-29 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09242 | 820.10 | 820-10-24 |  | EGAT-HEC-820-PRO-PID-00021 | Earthing Bonding Missing to be provided for WTD terminal box for 820-MP0002A | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-29 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09243 | 820.10 | 820-10-24 |  | EGAT-HEC-820-PRO-PID-00021 | Main earthing is missing to be provided for 820-JA-803(IS) & 820-JA-804 (IS) | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-29 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09244 | 820.10 | 820-10-24 |  | EGAT-HEC-820-PRO-PID-00021 | Earthing bonding is missing to be provided for LD 682 Seal cooler Stanchion support for 820-P0002A & 820-P0002B | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-29 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09245 | 820.10 | 820-10-24 |  | EGAT-HEC-820-PRO-PID-00021 | Proper Duct sealing to be done for Stub-up Conduit pipe. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-29 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09246 | 820.10 | 820-10-24 |  |  | C&I - Waldkown to be repeated due to late notification of Vendor training attended by Owner's C&I engineers. | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-29 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09247 | 820.10 | 820-10-24 | 820-P0002A | 820-P0002A | Rust on the pump to be removed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09248 | 820.10 | 820-10-24 | 820-P0002A | 820-P0002A | Pump to motor cover to be tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09249 | 820.10 | 820-10-24 | 820-P0002A | 820-MP0002A | Touch up painting of the motor | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09250 | 820.10 | 820-10-24 | 820-P0002A | 820-TE-8024A | to be fixed | B | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-30 | Walkdown |  | 2022-11-30 | 2022-11-24 |  | V |  |  |  | RFC/RFSU
. | 09251 | 820.10 | 820-10-24 | 820-P0002A | 820-MP0002A (DE) | Rust to be removed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09252 | 820.10 | 820-10-24 | 820-P0002A | 820-P0002A | Bended pipe for drain line to be repaired (1'') | B | EM | HEC MR Design | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09253 | 820.10 | 820-10-24 | 820-P0002A | 820-P0002A | U- bolt to be fixed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09254 | 820.10 | 820-10-24 | 820-P0002A | 820-P0002A | 2'' pipe to be connected and final bolting to be done | A | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09255 | 820.10 | 820-10-24 | 820-P0002A | 820-SG-8021A/B | to be touch up painted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09256 | 820.10 | 820-10-24 | 820-P0002A | 820-MP0002A | Cleaning and touch-up painting of the skid | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09257 | 820.10 | 820-10-24 | 820-P0002A | 820-P0002A | Houskeeping to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09258 | 820.10 | 820-10-24 | 820-P0002A | 820-P0002A | 1" drain line to be free from water stagnation | A | EM | HEC MR Design | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09259 | 820.10 | 820-10-24 | 820-P0002B | 820-P0002B | Rust on the pump to be removed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09260 | 820.10 | 820-10-24 | 820-P0002B | 820-P0002B | Pump to motor cover to be tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09261 | 820.10 | 820-10-24 | 820-P0002B | 820-P0002B | Touch up painting of the motor | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09262 | 820.10 | 820-10-24 | 820-P0002B | 820-MP0002B (DE) | Rust to be removed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09263 | 820.10 | 820-10-24 | 820-P0002B | 820-P0002B | Bended pipe for drain line to be repaired (1'') | B | EM | HEC MR Design | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09264 | 820.10 | 820-10-24 | 820-P0002B | 820-P0002B | U- bolt to be fixed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09265 | 820.10 | 820-10-24 | 820-P0002B | 820-P0002B | 2'' pipe to be connected and final bolting to be done | A | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09266 | 820.10 | 820-10-24 | 820-P0002B | 820-SG-8022A/B | to be touch up painted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09267 | 820.10 | 820-10-24 | 820-P0002B | 820-P0002B | Cleaning and touch-up painting of the skid | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09268 | 820.10 | 820-10-24 | 820-P0002B | 820-P0002B | Houskeeping to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09269 | 820.10 | 820-10-24 | 820-P0002B | 820-P0002B | 1" drain line to be free from water stagnation | A | EM | HEC MR Design | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09270 | 820.10 | 820-10-24 | 820-P0002A/B | 820-P0002A/B | Insulation to be completed | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09271 | 820.10 | 820-10-24 | 820-P0002B | 820-TG-80223 | to be fixed | B | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-30 | Walkdown |  | 2022-11-30 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 09272 | 820.10 | 820-10-24 | 820-P0002B | 820-P0002B | Corrosion on 3/4'' pipe to be removed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09273 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | Bolt and nuts to be protected | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09274 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | Tape on the manhole cover to be removed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09275 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | Platform to be cleaned and touch-up painted (manhole landing) | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09276 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | touch-up painting of handrail ( manhole hadrail) | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09277 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | Ladder to be fixed (loose bolting ) manhole ladder | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09278 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | Hanging wire to be remove | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09279 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | Downstream pipe rusted bolt and nuts to be cleaned and protected | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09280 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 ( Small tank) | Insulation to be cleaned and damage to be repaired, rust to be removed | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09281 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 ( Small tank) | platform to be cleaned and touch-up painting to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09282 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 ( Small tank) | manhole cover to be touch-up painted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09283 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 ( Small tank) | Rusted bolt and nut to be protected | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09284 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 ( Small tank) | Gate valve is unsafe to operate due to no platform and the only to operate it is on hanging on the ladder | C | EM | HEC PI Design | Mr. Krzysztof Kaliszyk | 2022-09-29 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09285 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | SS Flange with CS bolt and nuts to be verified with engineering | C | EM | HEC MS Design | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09286 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | Rusted shim plate to be cleand | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09287 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | Top platform to be cleaned and touch-up painting to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09288 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | Top platform bent pipe bird screen is missing | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09289 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | Grating clip to be fixed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09290 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | Insulation jacketing on 820-V0003 not tight, proper sheets overlap to be provided - especially eround nozzles | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09291 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | Mastic sealent to be supplemented / corrected. | B | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09292 | 820.10 | 820-10-24 | 820-V0003 | 820-V0003 | Wet wool around nozzles to be replaced before jacketing completion | B | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-29 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09294 | 820.10 | 820-10-24 | Common | N/A | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-29 | 2023-04-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09295 | 820.10 | 820-10-24 | Common | N/A | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-29 |  | Walkdown | [8 empty] | RFC/RFSU
. | 09296 | 820.10 | 820-10-24 | Common | General comment | Electrical tracing to be provided | B | EL | HEC EL Construction | Mr. Widecki | 2022-09-29 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09297 | 820.10 | 820-10-24 |  | General comment | Insulation to be provided | B | IN | HEC IN Construction | Mr. Widecki | 2022-09-29 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09298 | 820.10 | 820-10-24 |  | General comment | Corossion to be removed | A | PI | HEC PI Construction | Mr. Widecki | 2022-09-29 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09299 | 820.10 | 820-10-24 |  | 820-PRO-PID-00011 | Access ladder to the deaerator is too close to the railing - additional protection to be provided | C | ME | HEC ME Construction | Mr. Marek Łaskawski | 2022-09-29 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09300 | 820.10 | 820-10-24 |  | 820-PRO-PID-00011 | Gratings to be tightened | A | ME | HEC ME Construction | Mr. Widecki | 2022-09-29 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09301 | 820.10 | 820-10-24 |  | 820-PRO-PID-00011 | bird screens to be provided on air vents from deaerator | A | PI | HEC PI Construction | Mr. Marek Łaskawski | 2022-09-29 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09302 | 820.10 | 820-10-24 |  | 820-PRO-PID-00011 | SN-0111 - unable to take a sample | A | PI | HEC PI Construction | Mr. Jaroslaw Pykosz | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09303 | 820.10 | 820-10-24 |  | 820-PRO-PID-00011 | AT-1002/1003 - configuration to be revised in P&ID. | B | EM | HEC PI Design | Ms. Paulina Bajer | 2022-09-29 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09304 | 820.10 | 820-10-24 |  | 820-PRO-PID-00011 | Nameplate for 820-V0003 to be corrected based on approved documentation | C | ME | HEC ME Construction | Mr. Marek Łaskawski | 2022-09-29 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09305 | 820.10 | 820-10-24 |  | 820-PRO-PID-00021 | SN-0211 - unable to take a sample | A | PI | HEC PI Construction | Mr. Marek Łaskawski | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09306 | 820.10 | 820-10-24 |  | 820-PRO-PID-00021 | drain valve to be added in P&ID downstream of FV-1003 and FV-1004 | B | EM | HEC PI Design | Ms. Paulina Bajer | 2022-09-29 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09307 | 820.10 | 820-10-24 |  | 820-PRO-PID-00021 | FO-8022A, 8020B, 8021A, 8021B to be provided | B | EM | HEC MR Design | Mr. Marek Łaskawski | 2022-09-29 | 2023-01-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09308 | 820.10 | 820-10-24 |  | 820-PRO-PID-00021 | FO-8021A - duplicated tag no in P&ID (for pump A and B) | B | EM | HEC PI Design | Ms. Paulina Bajer | 2022-09-29 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09309 | 820.10 | 820-10-24 |  | 820-PRO-PID-00021 | No access to the valve on pump A suction line - valves location to be verified in order to provide better access for the operators. | C | EM | HEC PI Design | Mr. Jaroslaw Pykosz | 2022-09-29 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09310 | 820.10 | 820-10-24 |  | 820-PRO-PID-00021 | IA line not connected with FV-1003 | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-09-29 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09311 | 820.10 | 820-10-24 |  | 900-PRO-PID-05031 | Valve and drain valves on distribution line to unit 700 missing | A | PI | HEC PI Construction | Mr. Marek Łaskawski | 2022-09-29 | 2022-10-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09358 | 820.10 | 820-10-26 | 820-X0007 | EGAT-HEC-820-PRO-PID-00041 | Temporary blinds to be replaced | A | PI | HEC PI Construction | Mr. Jaroslaw Pykosz | 2022-10-05 | 2022-11-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09359 | 820.10 | 820-10-26 | 820-X0007 | EGAT-HEC-820-PRO-PID-00041 | PT-9302 to be tightened | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-10-05 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 09360 | 820.10 | 820-10-26 | 820-X0007 | EGAT-HEC-820-PRO-PID-00041 | 1/2'' valve on drain line to be marked as closed in P&ID. | B | EM | HEC PI Design | Mr. Jaroslaw Pykosz | 2022-10-05 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09361 | 820.10 | 820-10-26 | 820-X0007 | EGAT-HEC-820-PRO-PID-00041 | flange connection on drain line from the tank to be deleted in P&ID | B | EM | HEC PI Design | Ms. Małgorzata Juszczyk | 2022-10-05 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09362 | 820.10 | 820-10-26 | 820-X0007 | EGAT-HEC-820-PRO-PID-00041 | Locking device missing for LO valves | C | COMM | HEC COMM | Ms. Małgorzata Juszczyk | 2022-10-05 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09363 | 820.10 | 820-10-26 | 820-X0007 | EGAT-HEC-820-PRO-PID-00041 | Safe location to be provided for vent to atmosphere | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-10-05 | 2022-10-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09364 | 820.10 | 820-10-26 | 820-X0007 (820-SHT-CC-200) | EGAT-HEC-820-PRO-PID-00041 | Air vent - piping sealing to be provided | B | AR | HEC CV Construction | Ms. Paulina Bajer | 2022-10-05 | 2023-01-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09365 | 820.10 | 820-10-26 | 820-V0003 | EGAT-HEC-820-PRO-PID-00041 | Anti-alkali coating to be provided | A | AR | HEC AR Construction | Ms. Paulina Bajer | 2022-10-05 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09366 | 820.10 | 820-10-26 | 820-V0003 | EGAT-HEC-820-00011 | Hanging tag missing for FT-1002 | B | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-10-05 | 2022-11-14 | Walkdown |  |  | 2022-11-10 |  | V |  |  |  | RFC/RFSU
. | 09367 | 820.10 | 820-10-26 | 820-V0003 | EGAT-HEC-820-00011 | Plug for vent valve on deaerator feed water tank provided at Site | A | PI | HEC PI Construction | Mr. Marek Łaskawski | 2022-10-05 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09368 | 820.10 | 820-10-26 | 820-V0003 | EGAT-HEC-820-00011 | No acces to the manual valve on bypass line of FV-1002 | A | EM | HEC PI Design | Ms. Małgorzata Juszczyk | 2022-10-05 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09369 | 820.10 | 820-10-26 | 820-V0003 | EGAT-HEC-820-00011 | Access ladder to the deaerator is too close to the insulation | B | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2022-10-05 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09370 | 820.10 | 820-10-26 |  | Common | Insulation to be completed | B | IN | HEC IN Construction | Mr. Marek Łaskawski | 2022-10-05 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09371 | 820.10 | 820-10-26 | 820-X0007 | 820-FE-1002 | Inspection for Installation to be done | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-10-05 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09372 | 820.10 | 820-10-26 | 820-X0007 | 820-FT-1002 | Inspection for Installation / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-10-05 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09373 | 820.10 | 820-10-26 | 820-X0007 | 820-FV-1002 | Cable Pulling / Temination / Inspection for Installation / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-10-05 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09374 | 820.10 | 820-10-26 | 820-X0007 | 820-LT-1003B | Inspection for Installation / Pulling / IR Test / Termination to be done | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-10-05 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09375 | 820.10 | 820-10-26 | 820-X0007 | 820-X0007-P01A | Sensor plastic cover is missing | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-10-05 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09376 | 820.10 | 820-10-26 | 820-X0007 | 820-X0007-P01B | Sensor cover is missing | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-10-05 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09377 | 820.10 | 820-10-26 | 820-X0007 | 820-LG-M9304 | Flange connection rusted bolt and nuts to cleaned and protected | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-10-05 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09378 | 820.10 | 820-10-26 | 820-X0007 | 820-X0007-MM01 | Rust on motor to be cleaned | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-10-05 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09379 | 820.10 | 820-10-26 | 820-X0007 | 820-X0007-ST01 | Flange plastic cover to be removed ( upside the tank) | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-10-05 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09380 | 820.10 | 820-10-26 | 820-X0007 | 820-X0007 | Cleaning of the skid to be done | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-10-05 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09411 | 820.10 | 820-10-26 | Oxigen Scavenger Dossing System | EGAT-HEC-820-PRO-PID-00041 | Blind Plug to be provided for motor Terminal box spare hole for 820-X0007-MP01A &B | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-10-03 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09714 | 820.10 | 820-10-26 | AUX/820-Phosphate Injection BFW Treatment Shelter | 820-LT-1003B | Missing drain tube of instrument | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-10-05 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 09715 | 820.10 | 820-10-26 | AUX/820-Phosphate Injection BFW Treatment Shelter | 820-LT-1003B/PT-9302/9303 | No blind plug on instrument spare cable entry | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-10-05 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 09716 | 820.10 | 820-10-26 | AUX/820-Phosphate Injection BFW Treatment Shelter | 820-PG-9305/93069307/9308 | Atex specification of all pressure gauge shall be verified | A | EM | HEC MR Design | Mr. Krzysztof Nolbert | 2022-10-05 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09717 | 820.10 | 820-10-26 | AUX/820-Phosphate Injection BFW Treatment Shelter | 820-PT-9303 | Cable glanding of instrument should be tightened properly | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-10-05 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 09718 | 820.10 | 820-10-26 | AUX/820-Phosphate Injection BFW Treatment Shelter | 820-PG-9305/93069307/9308 | Missing drain plug for the manifold of pressure gauge | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-10-05 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 09719 | 820.10 | 820-10-26 | AUX/810-SL-003 | 820-FT-1002 | Replace the blind plug with Atex specification & provide blind plug at drain tube side | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-10-05 | 2022-11-14 | Walkdown |  |  | 2022-11-10 |  | V |  |  |  | RFC/RFSU
. | 09720 | 820.10 | 820-10-26 | AUX/810-SL-003 | 820-FT-1002 | Heat tracing cable to be done | A | EL | HEC EL Construction | Mr. Jaroslaw Pykosz | 2022-10-05 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09721 | 820.10 | 820-10-26 | Oxygen Scavenger Dosing |  | Not blinded flange at emergency shower | C | EM | HEC SE Design | Mr. Krzysztof Nolbert | 2022-10-05 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09722 | 820.10 | 820-10-26 | Oxygen Scavenger Dosing |  | Equipments made of Stainless Steel are connected with Carbon Steel fixing elements | C | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-10-05 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09723 | 820.10 | 820-10-26 | Oxygen Scavenger Dosing |  | It is not easy to idicate control pannels associated with particular drive | B | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2022-10-05 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09724 | 820.10 | 820-10-26 | CONNECTION 820-X0007 | 820-2"-CH-00101-N1A1-N | RUSTED U-BOLTS | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-10-05 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09725 | 820.10 | 820-10-26 | 820-X0007 | 820-1"-CH-93012-N1A1-N | BLIND MISSING TO BE INSTALLED | A | ME | HEC ME Construction | Mr. Jakub Partyka | 2022-10-05 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09726 | 820.10 | 820-10-26 | 820-X0007 | 820-1"-CH-93002-N1A1-N | BLIND MISSING TO BE INSTALLED | A | ME | HEC ME Construction | Mr. Jakub Partyka | 2022-10-05 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09727 | 820.10 | 820-10-26 | 820-X0007 | 820-1"-AV-04109-N1A1-N | WALL PENETRTION TO BE DONE | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-10-05 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09728 | 820.10 | 820-10-26 | 820-V0003 | 820-2"-CH-00101-N1A1-N | INSULATION NOT FINISHED - TO BE DONE | B | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-10-05 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09729 | 820.10 | 820-10-26 | 820-V0003 | 820-2"-CH-00101-N1A1-N | PLUG TO BE INSTALLED | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-10-05 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09730 | 820.10 | 820-10-26 | 820-V0003 | 820-2"-CH-00101-N1A1-N | RUSTED HANDLE OF VALVE - TO BE CORRECTED | B | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-10-05 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09731 | 820.10 | 820-10-26 | 820-V0003 | 820-2"-CH-00101-N1A1-N | SUPPORT NOT RESTING PROPERLY - TO BE RECTIFY | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-10-05 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09732 | 820.10 | 820-10-26 | GENERAL |  | DAMAGED INSULATION TO BE RECTIFY - SEVERAL PLACES E.G.: PIPERACK, NEAR 820-V0003 | B | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-10-05 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09733 | 820.10 | 820-10-26 | GENERAL | EGAT-HEC-820-PRO-PID-00011 | TOE GUARD TO BE INSTALLED | C | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-10-05 | 2022-12-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09734 | 820.10 | 820-10-26 | GENERAL | EGAT-HEC-820-PRO-PID-00011 | WRONG MARKING OF SYSTEM ON PID | B | COMM | HEC PI Construction | Mr. Jakub Partyka | 2022-10-05 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09735 | 820.10 | 820-10-26 | GENERAL | 820-X0007 OXYGENE SCAVENGER TANK | CHEMICAL CLEANING OF WELDS & PIPES | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-10-05 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09736 | 820.10 | 820-10-26 | GENERAL | 820-X0007 OXYGENE SCAVENGER TANK | INSULATION NOT FINISHED - TO BE DONE | B | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-10-05 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 09737 | 820.10 | 820-10-26 | GENERAL |  | CHEMICAL CLEANING OF SS JOINTS AND PIPES | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-10-05 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10518 | 820.10 | 820-10-18 | 820 | 820A-91901-01 | Valve paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10519 | 820.10 | 820-10-18 | 820 | 820A-91901-01 | Fig-8 Plastic to be remove | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10520 | 820.10 | 820-10-18 | 820 | 820A-91901-01 | PT NO.11 Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10521 | 820.10 | 820-10-18 | 820 | 820A-91901-02 | Valve paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10522 | 820.10 | 820-10-18 | 820 | 820A-91901-02 | Duct Tape to be remove from Valve visor and cleaning properly | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10523 | 820.10 | 820-10-18 | 820 | 820FG-91721-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10524 | 820.10 | 820-10-18 | 820 | 820FG-91721-01 | Duct Tape to be remove from Valve visor and cleaning properly | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10525 | 820.10 | 820-10-18 | 820 | 820FG-91721-01 | Support touch up paint to be done-S12 | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10526 | 820.10 | 820-10-18 | 820 | 820FG-91721-01 | Fig-8 Plastic to be remove | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10527 | 820.10 | 820-10-18 | 820 | 820FG-91721-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10528 | 820.10 | 820-10-18 | 820 | 820FG-91721-02 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10529 | 820.10 | 820-10-18 | 820 | 820FG-91721-02 | PRV-9172 Rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10530 | 820.10 | 820-10-18 | 820 | 820FG-91721-03 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10531 | 820.10 | 820-10-18 | 820 | 820FG-91721-03 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10532 | 820.10 | 820-10-18 | 820 | 820FG-91721-04 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10533 | 820.10 | 820-10-18 | 820 | 820FG-91721-04 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10534 | 820.10 | 820-10-18 | 820 | 820FG-91722-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10535 | 820.10 | 820-10-18 | 820 | 820FG-91722-01 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10536 | 820.10 | 820-10-18 | 820 | 820FG-91722-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10537 | 820.10 | 820-10-18 | 820 | 820FG-91722-01 | Support touch up paint to be done-S12 | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10538 | 820.10 | 820-10-18 | 820 | 820FG-91722-02 | FT-9171 Rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10539 | 820.10 | 820-10-18 | 820 | 820FG-91722-02 | FE-9171 to be installed with permanent gasket and bolts | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10540 | 820.10 | 820-10-18 | 820 | 820FG-91722-03 | Duct Tape to be remove from Valve visor and cleaning properly | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10541 | 820.10 | 820-10-18 | 820 | 820FG-91722-03 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10542 | 820.10 | 820-10-18 | 820 | 820FG-91722-04 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10543 | 820.10 | 820-10-18 | 820 | 820FG-91722-04 | Duct Tape to be remove from Valve visor and cleaning properly | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10544 | 820.10 | 820-10-18 | 820 | 820FG-91722-04 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10545 | 820.10 | 820-10-18 | 820 | 820FG-91722-04 | PT-9176A flange painting to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10546 | 820.10 | 820-10-18 | 820 | 820FG-91722-05 | Vent area insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10547 | 820.10 | 820-10-18 | 820 | 820FG-91722-05 | Secondary support C-channel end to be closed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10548 | 820.10 | 820-10-18 | 820 | 820FG-91722-05 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10549 | 820.10 | 820-10-18 | 820 | 820FG-91722-06 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10550 | 820.10 | 820-10-18 | 820 | 820FG-91722-06 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10551 | 820.10 | 820-10-18 | 820 | 820FG-91722-06 | Duct Tape to be remove from Valve visor and cleaning properly | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10552 | 820.10 | 820-10-18 | 820 | 820FG-91723-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10553 | 820.10 | 820-10-18 | 820 | 820FG-91723-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10554 | 820.10 | 820-10-18 | 820 | 820FG-91723-01 | Damaged cladding to be rectify | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10555 | 820.10 | 820-10-18 | 820 | 820FG-91723-02 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10556 | 820.10 | 820-10-18 | 820 | 820FG-91723-02 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10557 | 820.10 | 820-10-18 | 820 | 820FG-91723-02 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10558 | 820.10 | 820-10-18 | 820 | 820FG-91723-03 | Flange connection (XV-9155)rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10559 | 820.10 | 820-10-18 | 820 | 820FG-91723-03 | Pipe line clashing with grating to be rectify | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10560 | 820.10 | 820-10-18 | 820 | 820FG-91723-03 | Mastic to be applied properly on end of the cladding | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10561 | 820.10 | 820-10-18 | 820 | 820FG-91723-03 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10562 | 820.10 | 820-10-18 | 820 | 820FG-91724-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10563 | 820.10 | 820-10-18 | 820 | 820FG-91724-01 | Mastic to be applied near by the branch line | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10564 | 820.10 | 820-10-18 | 820 | 820FG-91724-01 | Flange connection (XV-9174A )rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10565 | 820.10 | 820-10-18 | 820 | 820FG-91724-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10566 | 820.10 | 820-10-18 | 820 | 820FG-91724-02 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10567 | 820.10 | 820-10-18 | 820 | 820FG-91724-03 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10568 | 820.10 | 820-10-18 | 820 | 820FG-91724-03 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10569 | 820.10 | 820-10-18 | 820 | 820FG-91725-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10570 | 820.10 | 820-10-18 | 820 | 820FG-91725-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10571 | 820.10 | 820-10-18 | 820 | 820FG-91725-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10572 | 820.10 | 820-10-18 | 820 | 820FG-91725-02 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10573 | 820.10 | 820-10-18 | 820 | 820FG-91725-02 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10574 | 820.10 | 820-10-18 | 820 | 820FG-91725-03 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10575 | 820.10 | 820-10-18 | 820 | 820FG-91725-03 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10576 | 820.10 | 820-10-18 | 820 | 820H-91741-01 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10577 | 820.10 | 820-10-18 | 820 | 820H-91741-01 | Fig-8 Plastic to be remove | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10578 | 820.10 | 820-10-18 | 820 | 820H-91741-01 | PT-10 Hand wheel pin missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10579 | 820.10 | 820-10-18 | 820 | 820H-91741-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10580 | 820.10 | 820-10-18 | 820 | 820H-91741-02 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10581 | 820.10 | 820-10-18 | 820 | 820H-91741-03 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10582 | 820.10 | 820-10-18 | 820 | 820H-91741-03 | PG-9170 missing | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 10583 | 820.10 | 820-10-18 | 820 | 820H-91742-01 | FE-9170 missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10584 | 820.10 | 820-10-18 | 820 | 820H-91742-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10585 | 820.10 | 820-10-18 | 820 | 820H-91742-01 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10586 | 820.10 | 820-10-18 | 820 | 820H-91742-03 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10587 | 820.10 | 820-10-18 | 820 | 820H-91742-03 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10588 | 820.10 | 820-10-18 | 820 | 820H-91742-03 | Duct Tape to be remove from Valve visor and cleaning properly | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10589 | 820.10 | 820-10-18 | 820 | 820H-91742-04 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10590 | 820.10 | 820-10-18 | 820 | 820H-91742-04 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10591 | 820.10 | 820-10-18 | 820 | 820H-91742-05 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10592 | 820.10 | 820-10-18 | 820 | 820H-91742-06 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10593 | 820.10 | 820-10-18 | 820 | 820H-91742-06 | Duct Tape to be remove from Valve visor and cleaning properly | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10594 | 820.10 | 820-10-18 | 820 | 820H-91742-06 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10595 | 820.10 | 820-10-18 | 820 | 820H-91742-07 | Valve body and hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10596 | 820.10 | 820-10-18 | 820 | 820H-91742-07 | Duct Tape to be remove from Valve visor and cleaning properly | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10597 | 820.10 | 820-10-18 | 820 | 820H-91742-07 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10598 | 820.10 | 820-10-18 | 820 | 820H-91742-08 | Valve stem guard missing | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2023-04-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10599 | 820.10 | 820-10-18 | 820 | 820H-91743-01 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10600 | 820.10 | 820-10-18 | 820 | 820H-91743-01 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10601 | 820.10 | 820-10-18 | 820 | 820H-91743-02 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10602 | 820.10 | 820-10-18 | 820 | 820H-91744-01 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10603 | 820.10 | 820-10-18 | 820 | 820H-91744-02 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10604 | 820.10 | 820-10-18 | 820 | 820H-91744-02 | Flange connection rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10605 | 820.10 | 820-10-18 | 820 | 820H-91744-02 | Grating kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10606 | 820.10 | 820-10-18 | 820 | 820H-91744-03 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10607 | 820.10 | 820-10-18 | 820 | 820H-91744-03 | Flange connection(XV-9173C) rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10608 | 820.10 | 820-10-18 | 820 | 820H-91745-01 | Grating kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10609 | 820.10 | 820-10-18 | 820 | 820H-91745-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10610 | 820.10 | 820-10-18 | 820 | 820H-91745-02 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10611 | 820.10 | 820-10-18 | 820 | 820H-91745-02 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10612 | 820.10 | 820-10-18 | 820 | 820H-91745-03 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10613 | 820.10 | 820-10-18 | 820 | 820H-91745-03 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10614 | 820.10 | 820-10-18 | 820 | 820HS-91554-01 | 820-B0001-E02/N2 Connection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10615 | 820.10 | 820-10-18 | 820 | 820HS-91554-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10616 | 820.10 | 820-10-18 | 820 | 820HS-91554-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10617 | 820.10 | 820-10-18 | 820 | 820HS-91554-01 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10618 | 820.10 | 820-10-18 | 820 | 820MS-91570-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10619 | 820.10 | 820-10-18 | 820 | 820MS-91570-01 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10620 | 820.10 | 820-10-18 | 820 | 820MS-91570-01 | Plug missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10621 | 820.10 | 820-10-18 | 820 | 820MS-91570-01 | Fig-8 to be installed in operate open position | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10622 | 820.10 | 820-10-18 | 820 | 820MS-91570-01 | PT NO.10 Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10623 | 820.10 | 820-10-18 | 820 | 820MS-91570-02 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10624 | 820.10 | 820-10-18 | 820 | 820MS-91570-02 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10625 | 820.10 | 820-10-18 | 820 | 820MS-91570-02 | FE-9198 upstream direction to be correct | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10626 | 820.10 | 820-10-18 | 820 | 820MS-91570-02 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10627 | 820.10 | 820-10-18 | 820 | 820MS-91570-03 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10628 | 820.10 | 820-10-18 | 820 | 820MS-91570-03 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10629 | 820.10 | 820-10-18 | 820 | 820MS-91570-04 | PT NO.10 Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10630 | 820.10 | 820-10-18 | 820 | 820MS-91570-04 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10631 | 820.10 | 820-10-18 | 820 | 820MS-91570-04 | FV-9198 name plate not matching with Isometric | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10632 | 820.10 | 820-10-18 | 820 | 820MS-91570-05 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10633 | 820.10 | 820-10-18 | 820 | 820MS-91570-05 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10634 | 820.10 | 820-10-18 | 820 | 820MS-91570-05 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10635 | 820.10 | 820-10-18 | 820 | 820MS-91570-06 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10636 | 820.10 | 820-10-18 | 820 | 820MS-91570-06 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10637 | 820.10 | 820-10-18 | 820 | 820MS-91570-07 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10638 | 820.10 | 820-10-18 | 820 | 820MS-91570-07 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10639 | 820.10 | 820-10-18 | 820 | 820MS-91570-08 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10640 | 820.10 | 820-10-18 | 820 | 820MS-91571-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10641 | 820.10 | 820-10-18 | 820 | 820MS-91571-01 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10642 | 820.10 | 820-10-18 | 820 | 820MS-91571-02 | Kick plate to be provided around pipes to safe operations | A | ME | HEC ME Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10643 | 820.10 | 820-10-18 | 820 | 820MS-91571-02 | Damaged cladding to be rectify near S5 | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10644 | 820.10 | 820-10-18 | 820 | 820MS-91571-03 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10645 | 820.10 | 820-10-18 | 820 | 820MS-91571-03 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10646 | 820.10 | 820-10-18 | 820 | 820MS-91572-01 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10647 | 820.10 | 820-10-18 | 820 | 820MS-91572-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10648 | 820.10 | 820-10-18 | 820 | 820MS-91572-01 | Pipe line clashing with grating to be rectify | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10649 | 820.10 | 820-10-18 | 820 | 820MS-91572-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10650 | 820.10 | 820-10-18 | 820 | 820MS-91572-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10651 | 820.10 | 820-10-18 | 820 | 820MS-91572-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10652 | 820.10 | 820-10-18 | 820 | 820MS-91573-01 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10653 | 820.10 | 820-10-18 | 820 | 820MS-91573-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10654 | 820.10 | 820-10-18 | 820 | 820MS-91573-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10655 | 820.10 | 820-10-18 | 820 | 820MS-91573-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10656 | 820.10 | 820-10-18 | 820 | 820MS-91573-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10657 | 820.10 | 820-10-18 | 820 | 820MS-91573-01 | Rusted plug painting to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10658 | 820.10 | 820-10-18 | 820 | 820MS-91573-02 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10659 | 820.10 | 820-10-18 | 820 | 820MS-91573-02 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10660 | 820.10 | 820-10-18 | 820 | 820NY-91656-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10661 | 820.10 | 820-10-18 | 820 | 820NY-91656-01 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10662 | 820.10 | 820-10-18 | 820 | 820NY-91662-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10663 | 820.10 | 820-10-18 | 820 | 820NY-91658-01 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10664 | 820.10 | 820-10-18 | 820 | 820NY-91658-01 | PT NO.10 Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10665 | 820.10 | 820-10-18 | 820 | 820NY-91658-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10666 | 820.10 | 820-10-18 | 820 | 820NY-91658-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10667 | 820.10 | 820-10-18 | 820 | 820NY-91667-01 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10668 | 820.10 | 820-10-18 | 820 | 820SC-91608-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10669 | 820.10 | 820-10-18 | 820 | 820SC-91608-01 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10670 | 820.10 | 820-10-18 | 820 | 820SC-91609-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10671 | 820.10 | 820-10-18 | 820 | 820SC-91609-01 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10672 | 820.10 | 820-10-18 | 820 | 820SOL-91761-01 | Flange connections (TE) rusted bolts to be clean and apply molykote | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-05 | Walkdown |  |  | 2022-12-02 |  | V |  |  |  | RFC/RFSU
. | 10673 | 820.10 | 820-10-18 | 820 | 820TR-LG9150-01 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10674 | 820.10 | 820-10-18 | 820 | 820TR-LG9150-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10675 | 820.10 | 820-10-18 | 820 | 820TR-LG9150-01 | Masking tape to be remove from valve stem | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10676 | 820.10 | 820-10-18 | 820 | 820TR-LG9150-02 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10677 | 820.10 | 820-10-18 | 820 | 820TR-LG9150-02 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10678 | 820.10 | 820-10-18 | 820 | 820TR-LG9150-02 | Masking tape to be remove from valve stem | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10679 | 820.10 | 820-10-18 | 820 | 820TR-LT9150A-01 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10680 | 820.10 | 820-10-18 | 820 | 820TR-LT9150A-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10681 | 820.10 | 820-10-18 | 820 | 820TR-LT9150A-01 | Masking tape to be remove from valve stem | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10682 | 820.10 | 820-10-18 | 820 | 820TR-LT9150A-02 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10683 | 820.10 | 820-10-18 | 820 | 820TR-LT9150A-02 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10684 | 820.10 | 820-10-18 | 820 | 820TR-LT9150A-02 | Masking tape to be remove from valve stem | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10685 | 820.10 | 820-10-18 | 820 | 820TR-LT9150B-01 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10686 | 820.10 | 820-10-18 | 820 | 820TR-LT9150B-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10687 | 820.10 | 820-10-18 | 820 | 820TR-LT9150B-01 | Masking tape to be remove from valve stem | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10688 | 820.10 | 820-10-18 | 820 | 820TR-LT9150B-02 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10689 | 820.10 | 820-10-18 | 820 | 820TR-LT9150B-02 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10690 | 820.10 | 820-10-18 | 820 | 820TR-LT9150B-02 | Masking tape to be remove from valve stem | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10691 | 820.10 | 820-10-18 | 820 | 820TR-LT9150C-01 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10692 | 820.10 | 820-10-18 | 820 | 820TR-LT9150C-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10693 | 820.10 | 820-10-18 | 820 | 820TR-LT9150C-01 | Masking tape to be remove from valve stem | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10694 | 820.10 | 820-10-18 | 820 | 820TR-LT9150C-02 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10695 | 820.10 | 820-10-18 | 820 | 820TR-LT9150C-02 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10696 | 820.10 | 820-10-18 | 820 | 820TR-LT9150C-02 | Masking tape to be remove from valve stem | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10697 | 820.10 | 820-10-18 | 820 | 820TR-LT9151A-01 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10698 | 820.10 | 820-10-18 | 820 | 820TR-LT9151A-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10699 | 820.10 | 820-10-18 | 820 | 820TR-LT9151A-01 | Masking tape to be remove from valve stem | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10700 | 820.10 | 820-10-18 | 820 | 820TR-LT9151A-02 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10701 | 820.10 | 820-10-18 | 820 | 820TR-LT9151A-02 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10702 | 820.10 | 820-10-18 | 820 | 820TR-LT9151A-02 | Masking tape to be remove from valve stem | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10703 | 820.10 | 820-10-18 | 820 | 820TR-LT9151B-01 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10704 | 820.10 | 820-10-18 | 820 | 820TR-LT9151B-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10705 | 820.10 | 820-10-18 | 820 | 820TR-LT9151B-01 | Masking tape to be remove from valve stem | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10706 | 820.10 | 820-10-18 | 820 | 820TR-LT9151B-02 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10707 | 820.10 | 820-10-18 | 820 | 820TR-LT9151B-02 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10708 | 820.10 | 820-10-18 | 820 | 820TR-LT9151B-02 | Masking tape to be remove from valve stem | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10709 | 820.10 | 820-10-18 | 820 | 820TR-PG9152-01 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10710 | 820.10 | 820-10-18 | 820 | 820TR-PG9152-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10711 | 820.10 | 820-10-18 | 820 | 820TR-PG9152-01 | Piping Insulation missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10712 | 820.10 | 820-10-18 | 820 | 820TR-PT9151-01 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10713 | 820.10 | 820-10-18 | 820 | 820TR-PT9151-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10714 | 820.10 | 820-10-18 | 820 | 820TR-PT9151-01 | Piping Insulation missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10715 | 820.10 | 820-10-18 | 820 | 820VG-91701-01 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10716 | 820.10 | 820-10-18 | 820 | 820VG-91701-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10717 | 820.10 | 820-10-18 | 820 | 820VG-91701-01 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10718 | 820.10 | 820-10-18 | 820 | 820VG-91701-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10719 | 820.10 | 820-10-18 | 820 | 820VG-91701-01 | U-Bolt to be tightened properly | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10720 | 820.10 | 820-10-18 | 820 | 820VG-91701-01 | Insulation symbol not mentioned in ISO | C | EM | HEC MS Design | Mr. Maciej Smalira | 2022-10-20 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10721 | 820.10 | 820-10-18 | 820 | 820VG-91701-02 | Pipe line not resting | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10722 | 820.10 | 820-10-18 | 820 | 820VG-91701-02 | Insulation symbol not mentioned in ISO | C | EM | HEC MS Design | Mr. Maciej Smalira | 2022-10-20 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10723 | 820.10 | 820-10-18 | 820 | 820VG-91701-02 | Pipe line final painting to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10724 | 820.10 | 820-10-18 | 820 | 820VG-91701-02 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10725 | 820.10 | 820-10-18 | 820 | 820VG-91701-03 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10726 | 820.10 | 820-10-18 | 820 | 820VG-91701-03 | Valve visor missing | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2023-04-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10727 | 820.10 | 820-10-18 | 820 | 820VG-91701-03 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10728 | 820.10 | 820-10-18 | 820 | 820VG-91701-03 | Spool tag and masking tape to be remove | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10729 | 820.10 | 820-10-18 | 820 | 820VG-91701-03 | U-Bolt insulator damaged to be replace | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10730 | 820.10 | 820-10-18 | 820 | 820A-91902-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10731 | 820.10 | 820-10-18 | 820 | 820A-91903-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10732 | 820.10 | 820-10-18 | 820 | 820A-91903-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10733 | 820.10 | 820-10-18 | 820 | 820A-91904-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10734 | 820.10 | 820-10-18 | 820 | 820A-91904-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10735 | 820.10 | 820-10-18 | 820 | 820A-91904-01 | Nearby boiler nozzle blind flange missing | B | ME | HEC ME Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10736 | 820.10 | 820-10-18 | 820 | 820A-91905-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10737 | 820.10 | 820-10-18 | 820 | 820A-91908-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10738 | 820.10 | 820-10-18 | 820 | 820A-91908-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10739 | 820.10 | 820-10-18 | 820 | 820A-91909-01 | Whole valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10740 | 820.10 | 820-10-18 | 820 | 820A-91910-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10741 | 820.10 | 820-10-18 | 820 | 820A-91910-01 | U-Bolt insulator damaged to be replace | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10742 | 820.10 | 820-10-18 | 820 | 820A-91910-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10743 | 820.10 | 820-10-18 | 820 | 820A-91911-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10744 | 820.10 | 820-10-18 | 820 | 820A-91911-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10745 | 820.10 | 820-10-18 | 820 | 820A-91911-01 | PT no.-4&5 paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10746 | 820.10 | 820-10-18 | 820 | 820AV-91632-01 | Pipe line shaking to be fixed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10747 | 820.10 | 820-10-18 | 820 | 820AV-91634-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10748 | 820.10 | 820-10-18 | 820 | 820AV-91639-01 | valve and elbow paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10749 | 820.10 | 820-10-18 | 820 | 820AV-91641-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10750 | 820.10 | 820-10-18 | 820 | 820AV-91642-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10751 | 820.10 | 820-10-18 | 820 | 820AV-91643-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10752 | 820.10 | 820-10-18 | 820 | 820CWR-91951-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10753 | 820.10 | 820-10-18 | 820 | 820CWR-91951-01 | Valve visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10754 | 820.10 | 820-10-18 | 820 | 820CWR-91951-01 | Fig-8 Plastic to be remove | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10755 | 820.10 | 820-10-18 | 820 | 820CWR-91952-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10756 | 820.10 | 820-10-18 | 820 | 820CWR-91952-01 | 820-B0001-X02/TP-5 Connection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10757 | 820.10 | 820-10-18 | 820 | 820CWR-91953-01 | 820-B0001-W01/CWR-1/2 Connection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10758 | 820.10 | 820-10-18 | 820 | 820CWR-91953-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10759 | 820.10 | 820-10-18 | 820 | 820CWR-91954-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10760 | 820.10 | 820-10-18 | 820 | 820CWR-91954-01 | S11 support foundation grouting to be done | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10761 | 820.10 | 820-10-18 | 820 | 820CWR-91954-01 | 820-B0001-MW02/CWR 1 Connection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10762 | 820.10 | 820-10-18 | 820 | 820CWR-91954-01 | PT no -4 round plug to be install | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10763 | 820.10 | 820-10-18 | 820 | 820CWS-91931-01 | PT no -10 round plug to be install | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10764 | 820.10 | 820-10-18 | 820 | 820CWS-91931-01 | Fig-8 Plastic to be remove | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10765 | 820.10 | 820-10-18 | 820 | 820CWS-91932-01 | 820-B0001-X02/TP-6 Connection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2023-01-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10766 | 820.10 | 820-10-18 | 820 | 820CWS-91932-01 | PT no -10 round plug to be install | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10767 | 820.10 | 820-10-18 | 820 | 820CWS-91932-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10768 | 820.10 | 820-10-18 | 820 | 820CWS-91933-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10769 | 820.10 | 820-10-18 | 820 | 820CWS-91933-01 | 820-B0001-X02/TP-6 Connection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10770 | 820.10 | 820-10-18 | 820 | 820CWS-91933-01 | 820-B0001-W01/CWS 2 Connection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10771 | 820.10 | 820-10-18 | 820 | 820CWS-91933-01 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10772 | 820.10 | 820-10-18 | 820 | 820CWS-91934-01 | 820-B0001-MW02/CWS 1/2 Connection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10773 | 820.10 | 820-10-18 | 820 | 820CWS-91934-01 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10774 | 820.10 | 820-10-18 | 820 | 820CWS-91934-01 | PT no -4 round plug to be install | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10775 | 820.10 | 820-10-18 | 820 | 820CWS-91934-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10776 | 820.10 | 820-10-18 | 820 | 820FG-91726-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10777 | 820.10 | 820-10-18 | 820 | 820FG-91726-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10778 | 820.10 | 820-10-18 | 820 | 820FG-91727-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10779 | 820.10 | 820-10-18 | 820 | 820FG-91727-01 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10780 | 820.10 | 820-10-18 | 820 | 820FG-91727-01 | PG & PT tube connection to be verify asper the drawing | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 10781 | 820.10 | 820-10-18 | 820 | 820FG-91727-02 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10782 | 820.10 | 820-10-18 | 820 | 820FG-91727-02 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10783 | 820.10 | 820-10-18 | 820 | 820FG-91728-01 | PG-9180 flange touch up paint to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10784 | 820.10 | 820-10-18 | 820 | 820FG-91728-01 | PG-9180 valve handle clashing with insulation to be rectify | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10785 | 820.10 | 820-10-18 | 820 | 820FG-91728-01 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10786 | 820.10 | 820-10-18 | 820 | 820FG-91728-01 | Piping insulation cladding loose to be tightened | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10787 | 820.10 | 820-10-18 | 820 | 820FG-91729-01 | PG-9185 valve handle clashing with insulation to be rectify | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10788 | 820.10 | 820-10-18 | 820 | 820FG-91729-01 | PG-9180 flange touch up paint to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10789 | 820.10 | 820-10-18 | 820 | 820FG-91729-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10790 | 820.10 | 820-10-18 | 820 | 820FG-91729-01 | Piping insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10791 | 820.10 | 820-10-18 | 820 | 820FG-91729-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10792 | 820.10 | 820-10-18 | 820 | 820IA-91801-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10793 | 820.10 | 820-10-18 | 820 | 820IA-91801-01 | Plug painting to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10794 | 820.10 | 820-10-18 | 820 | 820IA-91801-02 | Additional flange connection to be updated in ISO | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10795 | 820.10 | 820-10-18 | 820 | 820IA-91802-01 | Near by S9 support additional holes to be sealed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10796 | 820.10 | 820-10-18 | 820 | 820IA-91802-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10797 | 820.10 | 820-10-18 | 820 | 820IA-91802-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10798 | 820.10 | 820-10-18 | 820 | 820IA-91802-01 | Additonal coupling connection to be updated in ISO | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10799 | 820.10 | 820-10-18 | 820 | 820IA-91803-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10800 | 820.10 | 820-10-18 | 820 | 820IA-91806-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10801 | 820.10 | 820-10-18 | 820 | 820IA-91807-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10802 | 820.10 | 820-10-18 | 820 | 820IA-91808-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10803 | 820.10 | 820-10-18 | 820 | 820IA-91808-01 | Valve visor bolt paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10804 | 820.10 | 820-10-18 | 820 | 820IA-91809-01 | Additional U-bolt support to be updated in ISO | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10805 | 820.10 | 820-10-18 | 820 | 820IA-91810-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10806 | 820.10 | 820-10-18 | 820 | 820IA-91810-01 | Plug missing( 2 locations) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10807 | 820.10 | 820-10-18 | 820 | 820IA-91810-01 | Additional flange connection to be updated in ISO | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10808 | 820.10 | 820-10-18 | 820 | 820IA-91811-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10809 | 820.10 | 820-10-18 | 820 | 820IA-91812-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10810 | 820.10 | 820-10-18 | 820 | 820IA-91813-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10811 | 820.10 | 820-10-18 | 820 | 820IA-91814-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10812 | 820.10 | 820-10-18 | 820 | 820IA-91815-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10813 | 820.10 | 820-10-18 | 820 | 820IA-91815-01 | Pipe line shaking to be fixed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10814 | 820.10 | 820-10-18 | 820 | 820IA-91816-01 | U-Bolt to be tightened properly | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10815 | 820.10 | 820-10-18 | 820 | 820IA-91816-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10816 | 820.10 | 820-10-18 | 820 | 820IA-91816-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10817 | 820.10 | 820-10-18 | 820 | 820IA-91817-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10818 | 820.10 | 820-10-18 | 820 | 820IA-91817-01 | XV-9176C tube connection to be verify as per the drawing | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 10819 | 820.10 | 820-10-18 | 820 | 820IA-91818-01 | XV-9172C tube connection to be verify as per the drawing | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 10820 | 820.10 | 820-10-18 | 820 | 820IA-91818-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10821 | 820.10 | 820-10-18 | 820 | 820IA-91819-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10822 | 820.10 | 820-10-18 | 820 | 820IA-91820-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10823 | 820.10 | 820-10-18 | 820 | 820IA-91821-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10824 | 820.10 | 820-10-18 | 820 | 820IA-91822-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10825 | 820.10 | 820-10-18 | 820 | 820IA-91823-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10826 | 820.10 | 820-10-18 | 820 | 820IA-91824-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10827 | 820.10 | 820-10-18 | 820 | 820IA-91825-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10828 | 820.10 | 820-10-18 | 820 | 820IA-91825-01 | XV-9178B tube connection to be verify as per the drawing | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 10829 | 820.10 | 820-10-18 | 820 | 820IA-91826-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10830 | 820.10 | 820-10-18 | 820 | 820IA-91826-01 | valve visor side glass to be clean | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10831 | 820.10 | 820-10-18 | 820 | 820IA-91826-01 | XV-9177C tube connection to be verify as per the drawing | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 10832 | 820.10 | 820-10-18 | 820 | 820IA-91827-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10833 | 820.10 | 820-10-18 | 820 | 820IA-91828-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10834 | 820.10 | 820-10-18 | 820 | 820IA-91829-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10835 | 820.10 | 820-10-18 | 820 | 820IA-91829-01 | XV-9174C tube connection to be verify as per the drawing | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 10836 | 820.10 | 820-10-18 | 820 | 820IA-91830-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10837 | 820.10 | 820-10-18 | 820 | 820IA-91830-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10838 | 820.10 | 820-10-18 | 820 | 820IA-91831-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10839 | 820.10 | 820-10-18 | 820 | 820IA-91831-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10840 | 820.10 | 820-10-18 | 820 | 820IA-91832-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10841 | 820.10 | 820-10-18 | 820 | 820IA-91832-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10842 | 820.10 | 820-10-18 | 820 | 820IA-91832-01 | Valve visor bolts missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10843 | 820.10 | 820-10-18 | 820 | 820IA-91833-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10844 | 820.10 | 820-10-18 | 820 | 820IA-91834-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10845 | 820.10 | 820-10-18 | 820 | 820IA-91834-01 | XV-9175C tube connection to be verify as per the drawing | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 10846 | 820.10 | 820-10-18 | 820 | 820IA-91835-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10847 | 820.10 | 820-10-18 | 820 | 820IA-91835-01 | Valve visor bolts missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10848 | 820.10 | 820-10-18 | 820 | 820IA-91836-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10849 | 820.10 | 820-10-18 | 820 | 820IA-91837-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10850 | 820.10 | 820-10-18 | 820 | 820IA-91836-01 | XV-9170C tube connection to be verify as per the drawing | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 10851 | 820.10 | 820-10-18 | 820 | 820IA-91838-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10852 | 820.10 | 820-10-18 | 820 | 820IA-91838-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10853 | 820.10 | 820-10-18 | 820 | 820IA-91839-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10854 | 820.10 | 820-10-18 | 820 | 820IA-91840-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10855 | 820.10 | 820-10-18 | 820 | 820IA-91841-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10856 | 820.10 | 820-10-18 | 820 | 820IA-91841-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10857 | 820.10 | 820-10-18 | 820 | 820IA-91842-01 | XV-9178C tube connection to be verify as per the drawing | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 10858 | 820.10 | 820-10-18 | 820 | 820IA-91842-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10859 | 820.10 | 820-10-18 | 820 | 820IA-91842-01 | Valve visor bolts missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10860 | 820.10 | 820-10-18 | 820 | 820IA-91843-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10861 | 820.10 | 820-10-18 | 820 | 820IA-91843-01 | Tube connection point(XV-9173A) to be updated in ISO | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10862 | 820.10 | 820-10-18 | 820 | 820IA-91844-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10863 | 820.10 | 820-10-18 | 820 | 820IA-91845-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10864 | 820.10 | 820-10-18 | 820 | 820IA-91845-01 | XV-9174C tube connection to be verify as per the drawing | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 10865 | 820.10 | 820-10-18 | 820 | 820IA-91846-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10866 | 820.10 | 820-10-18 | 820 | 820IA-91847-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10867 | 820.10 | 820-10-18 | 820 | 820IA-91851-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10868 | 820.10 | 820-10-18 | 820 | 820IA-91852-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10869 | 820.10 | 820-10-18 | 820 | 820IA-91853-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10870 | 820.10 | 820-10-18 | 820 | 820IA-91853-01 | Valve visor bolts missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10871 | 820.10 | 820-10-18 | 820 | 820IA-91884-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10872 | 820.10 | 820-10-18 | 820 | 820IA-91884-01 | Support missing(S5&6) | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10873 | 820.10 | 820-10-18 | 820 | 820IA-91885-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10874 | 820.10 | 820-10-18 | 820 | 820IA-91885-01 | Tube connection touching with another line to be rectify | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10875 | 820.10 | 820-10-18 | 820 | 820IA-91885-01 | Pipe line touching with grating to be rectify | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10876 | 820.10 | 820-10-18 | 820 | 820IA-91886-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10877 | 820.10 | 820-10-18 | 820 | 820IA-91886-01 | Tube connection touching with another line to be rectify | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10878 | 820.10 | 820-10-18 | 820 | 820IA-91887-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10879 | 820.10 | 820-10-18 | 820 | 820IA-91887-01 | Tube connection not yet done | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10880 | 820.10 | 820-10-18 | 820 | 820IA-91887-01 | Line shaking to be fixed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10881 | 820.10 | 820-10-18 | 820 | 820IA-91888-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10882 | 820.10 | 820-10-18 | 820 | 820MS-91574-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10883 | 820.10 | 820-10-18 | 820 | 820MS-91574-01 | Wrong steam trap installed to be replace | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-10-20 |  | Walkdown | [8 empty] | RFC/RFSU
. | 10884 | 820.10 | 820-10-18 | 820 | 820MS-91574-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10885 | 820.10 | 820-10-18 | 820 | 820MS-91575-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10886 | 820.10 | 820-10-18 | 820 | 820MS-91575-01 | Wrong steam trap installed to be replace | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-10-20 |  | Walkdown | [8 empty] | RFC/RFSU
. | 10887 | 820.10 | 820-10-18 | 820 | 820MS-91575-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10888 | 820.10 | 820-10-18 | 820 | 820N-91531-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10889 | 820.10 | 820-10-18 | 820 | 820N-91531-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10890 | 820.10 | 820-10-18 | 820 | 820NY-91654-01 | Valve stem damaged to be replace | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10891 | 820.10 | 820-10-18 | 820 | 820NY-91654-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10892 | 820.10 | 820-10-18 | 820 | 820NY-91654-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10893 | 820.10 | 820-10-18 | 820 | 820NY-91655-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10894 | 820.10 | 820-10-18 | 820 | 820NY-91659-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10895 | 820.10 | 820-10-18 | 820 | 820NY-91660-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10896 | 820.10 | 820-10-18 | 820 | 820NY-91669-01 | ET&Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10897 | 820.10 | 820-10-18 | 820 | 820NY-91669-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10898 | 820.10 | 820-10-18 | 820 | 820NY-91671-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10899 | 820.10 | 820-10-18 | 820 | 820NY-91671-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10900 | 820.10 | 820-10-18 | 820 | 820NY-91672-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10901 | 820.10 | 820-10-18 | 820 | 820SOL-91761-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10902 | 820.10 | 820-10-18 | 820 | 820SOL-91761-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10903 | 820.10 | 820-10-18 | 820 | 820SOL-91761-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10904 | 820.10 | 820-10-18 | 820 | 820SOL-91761-01 | U-Bolt damage to be replace | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10905 | 820.10 | 820-10-18 | 820 | 820SOL-91761-03 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10906 | 820.10 | 820-10-18 | 820 | 820SOL-91761-03 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10907 | 820.10 | 820-10-18 | 820 | 820SOL-91761-03 | FT-9172 Flow direction wrong to bre rectify | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10908 | 820.10 | 820-10-18 | 820 | 820SOL-91761-04 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10909 | 820.10 | 820-10-18 | 820 | 820SOL-91761-04 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10910 | 820.10 | 820-10-18 | 820 | 820SOL-91761-04 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10911 | 820.10 | 820-10-18 | 820 | 820SOL-91762-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10912 | 820.10 | 820-10-18 | 820 | 820SOL-91762-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10913 | 820.10 | 820-10-18 | 820 | 820SOL-91762-02 | Line shaking to be fixed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10914 | 820.10 | 820-10-18 | 820 | 820SOL-91763-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10915 | 820.10 | 820-10-18 | 820 | 820SOL-91763-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10916 | 820.10 | 820-10-18 | 820 | 820SOL-91763-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10917 | 820.10 | 820-10-18 | 820 | 820SOL-91763-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10918 | 820.10 | 820-10-18 | 820 | 820SOL-91764-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10919 | 820.10 | 820-10-18 | 820 | 820SOL-91764-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10920 | 820.10 | 820-10-18 | 820 | 820SOL-91764-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10921 | 820.10 | 820-10-18 | 820 | 820VG-91702-01 | Touch up paint to be done near by nipple | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10922 | 820.10 | 820-10-18 | 820 | 820VG-91703-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10923 | 820.10 | 820-10-18 | 820 | 820HS-91552-08 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10924 | 820.10 | 820-10-18 | 820 | 820HS-91552-09 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10925 | 820.10 | 820-10-18 | 820 | 820HS-91552-06 | Piping insulation missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10926 | 820.10 | 820-10-18 | 820 | 820HS-91552-06 | PSV to be installed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10927 | 820.10 | 820-10-18 | 820 | 820BW-91501-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10928 | 820.10 | 820-10-18 | 820 | 820BW-91501-01 | Valve paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10929 | 820.10 | 820-10-18 | 820 | 820BW-91501-01 | Fig-8 Plastic to be remove | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10930 | 820.10 | 820-10-18 | 820 | 820BW-91505-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10931 | 820.10 | 820-10-18 | 820 | 820BW-91505-01 | Secondary support C-channel end to be closed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10932 | 820.10 | 820-10-18 | 820 | 820BW-91505-01 | Temporary support to be remove | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10933 | 820.10 | 820-10-18 | 820 | 820BW-91501-02 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10934 | 820.10 | 820-10-18 | 820 | 820BW-91501-03 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10935 | 820.10 | 820-10-18 | 820 | 820BW-91501-03 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10936 | 820.10 | 820-10-18 | 820 | 820BW-91501-03 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10937 | 820.10 | 820-10-18 | 820 | 820BW-91501-04 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10938 | 820.10 | 820-10-18 | 820 | 820BW-91501-04 | PT No.12 Valve hand wheel pin missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10939 | 820.10 | 820-10-18 | 820 | 820BW-91501-04 | Valve body paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10940 | 820.10 | 820-10-18 | 820 | 820BW-91501-05 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10941 | 820.10 | 820-10-18 | 820 | 820BW-91501-05 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10942 | 820.10 | 820-10-18 | 820 | 820BW-91501-05 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10943 | 820.10 | 820-10-18 | 820 | 820BW-91501-05 | Valve visor missing | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2023-04-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10944 | 820.10 | 820-10-18 | 820 | 820BW-91501-06 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10945 | 820.10 | 820-10-18 | 820 | 820BW-91501-06 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10946 | 820.10 | 820-10-18 | 820 | 820BW-91502-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10947 | 820.10 | 820-10-18 | 820 | 820BW-91503-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10948 | 820.10 | 820-10-18 | 820 | 820BW-91503-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10949 | 820.10 | 820-10-18 | 820 | 820BW-91503-02 | Valve hand wheel tightening nut missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10950 | 820.10 | 820-10-18 | 820 | 820BW-91503-02 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10951 | 820.10 | 820-10-18 | 820 | 820BW-91504-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10952 | 820.10 | 820-10-18 | 820 | 820BW-91504-02 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10953 | 820.10 | 820-10-18 | 820 | 820BW-91504-02 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10954 | 820.10 | 820-10-18 | 820 | 820BW-91506-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10955 | 820.10 | 820-10-18 | 820 | 820BW-91506-01 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10956 | 820.10 | 820-10-18 | 820 | 820BW-91506-02 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10957 | 820.10 | 820-10-18 | 820 | 820BW-91506-02 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10958 | 820.10 | 820-10-18 | 820 | 820BW-91506-03 | Valve body paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10959 | 820.10 | 820-10-18 | 820 | 820BW-91506-03 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10960 | 820.10 | 820-10-18 | 820 | 820BW-91506-03 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10961 | 820.10 | 820-10-18 | 820 | 820BW-91506-04 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10962 | 820.10 | 820-10-18 | 820 | 820BW-91506-04 | Valve hand wheel and visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10963 | 820.10 | 820-10-18 | 820 | 820BW-91511-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10964 | 820.10 | 820-10-18 | 820 | 820BW-91512-01 | Valve visor paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10965 | 820.10 | 820-10-18 | 820 | 820BW-91510-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10966 | 820.10 | 820-10-18 | 820 | 820BW-91507-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10967 | 820.10 | 820-10-18 | 820 | 820BW-91507-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10968 | 820.10 | 820-10-18 | 820 | 820BW-91508-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10969 | 820.10 | 820-10-18 | 820 | 820BW-91509-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10970 | 820.10 | 820-10-18 | 820 | 820BW-91509-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10971 | 820.10 | 820-10-18 | 820 | 820SC-91605-02 | Valve stem guard missing | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2023-04-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10972 | 820.10 | 820-10-18 | 820 | 820SC-91605-02 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10973 | 820.10 | 820-10-18 | 820 | 820SC-91605-01 | Valve visor missing | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2023-04-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10974 | 820.10 | 820-10-18 | 820 | 820SC-91605-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10975 | 820.10 | 820-10-18 | 820 | 820SC-91607-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10976 | 820.10 | 820-10-18 | 820 | 820SC-91607-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10977 | 820.10 | 820-10-18 | 820 | 820SC-91606-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10978 | 820.10 | 820-10-18 | 820 | 820SC-91606-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10979 | 820.10 | 820-10-18 | 820 | 820NY-91657-01 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10980 | 820.10 | 820-10-18 | 820 | 820NY-91657-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10981 | 820.10 | 820-10-18 | 820 | 820NY-91657-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10982 | 820.10 | 820-10-18 | 820 | 820NY-91658-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10983 | 820.10 | 820-10-18 | 820 | 820NY-91658-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10984 | 820.10 | 820-10-18 | 820 | 820NY-91658-01 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10985 | 820.10 | 820-10-18 | 820 | 820CH-91541-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10986 | 820.10 | 820-10-18 | 820 | 820CH-91541-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10987 | 820.10 | 820-10-18 | 820 | 820CH-91541-01 | Fig-8 Plastic to be remove | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10988 | 820.10 | 820-10-18 | 820 | 820CH-91541-01 | Valve visor bolts to be clean | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10989 | 820.10 | 820-10-18 | 820 | 820CH-91541-01 | Piping insulation clashing with grating to be rectify | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10990 | 820.10 | 820-10-18 | 820 | 820CH-91541-02 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10991 | 820.10 | 820-10-18 | 820 | 820CH-91541-03 | Line touching with steel structure to be rectify | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10992 | 820.10 | 820-10-18 | 820 | 820CH-91541-03 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10993 | 820.10 | 820-10-18 | 820 | 820CH-91542-01 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10994 | 820.10 | 820-10-18 | 820 | 820CH-91542-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10995 | 820.10 | 820-10-18 | 820 | 820CH-91542-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10996 | 820.10 | 820-10-18 | 820 | 820AV-91623-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10997 | 820.10 | 820-10-18 | 820 | 820AV-91626-01 | Line not resting on beam to be rectify | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10998 | 820.10 | 820-10-18 | 820 | 820AV-91622-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 10999 | 820.10 | 820-10-18 | 820 | 820AV-91625-01 | Masking tape to be remove from bolts | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11000 | 820.10 | 820-10-18 | 820 | 820AV-91625-01 | Line not resting on beam to be rectify | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11001 | 820.10 | 820-10-18 | 820 | 820AV-91627-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11002 | 820.10 | 820-10-18 | 820 | 820AV-91627-01 | Line not resting on beam to be rectify | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11003 | 820.10 | 820-10-18 | 820 | 820AV-91624-01 | PSV valve handle missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11004 | 820.10 | 820-10-18 | 820 | 820AV-91624-01 | PSV drain not leaded in safe way | C | EM | HEC MS Design | Mr. Maciej Smalira | 2022-10-20 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11005 | 820.10 | 820-10-18 | 820 | 820AV-91624-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11006 | 820.10 | 820-10-18 | 820 | 820NY-91665-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11007 | 820.10 | 820-10-18 | 820 | 820AV-91621-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11008 | 820.10 | 820-10-18 | 820 | 820SC-91604-02 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11009 | 820.10 | 820-10-18 | 820 | 820SC-91604-02 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11010 | 820.10 | 820-10-18 | 820 | 820SC-91604-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11011 | 820.10 | 820-10-18 | 820 | 820SC-91604-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11012 | 820.10 | 820-10-18 | 820 | 820SC-91602-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11013 | 820.10 | 820-10-18 | 820 | 820SC-91602-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11014 | 820.10 | 820-10-18 | 820 | 820SC-91602-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11015 | 820.10 | 820-10-18 | 820 | 820SC-91603-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11016 | 820.10 | 820-10-18 | 820 | 820SC-91603-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11017 | 820.10 | 820-10-18 | 820 | 820SC-91602-02 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11018 | 820.10 | 820-10-18 | 820 | 820SC-91602-02 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11019 | 820.10 | 820-10-18 | 820 | 820SC-91602-02 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11020 | 820.10 | 820-10-18 | 820 | 820SC-91602-02 | Support not updated in ISO | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11021 | 820.10 | 820-10-18 | 820 | 820SC-91602-04 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11022 | 820.10 | 820-10-18 | 820 | 820SC-91602-04 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11023 | 820.10 | 820-10-18 | 820 | 820SC-91602-03 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11024 | 820.10 | 820-10-18 | 820 | 820SC-91602-03 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11025 | 820.10 | 820-10-18 | 820 | 820SC-91602-03 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11026 | 820.10 | 820-10-18 | 820 | 820SC-91602-03 | Valve visor bolts to be clean | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11027 | 820.10 | 820-10-18 | 820 | 820SC-91602-05 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11028 | 820.10 | 820-10-18 | 820 | 820SC-91601-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11029 | 820.10 | 820-10-18 | 820 | 820SC-91601-01 | Kick plate paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11030 | 820.10 | 820-10-18 | 820 | 820SC-91601-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11031 | 820.10 | 820-10-18 | 820 | 820SC-91601-01 | Valve visor missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11032 | 820.10 | 820-10-18 | 820 | 820SC-91601-01 | Slope on the pipe line to be verify | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11033 | 820.10 | 820-10-18 | 820 | 820NY-91673-01 | Bolts& nuts missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11034 | 820.10 | 820-10-18 | 820 | 820HS-91557-01 | Line contact with tubing to be rectify | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11035 | 820.10 | 820-10-18 | 820 | 820HS-91557-01 | Secondary support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11036 | 820.10 | 820-10-18 | 820 | 820HS-91557-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11037 | 820.10 | 820-10-18 | 820 | 820HS-91556-02 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11038 | 820.10 | 820-10-18 | 820 | 820HS-91556-02 | Cladding not overlapped to be rectify | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11039 | 820.10 | 820-10-18 | 820 | 820HS-91556-01 | Cladding damaged to be rectify | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11040 | 820.10 | 820-10-18 | 820 | 820HS-91556-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11041 | 820.10 | 820-10-18 | 820 | 820HS-91552-01 | Boiler connection to be boxed up | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11042 | 820.10 | 820-10-18 | 820 | 820HS-91552-02 | Is the paint applied on support is high temperature resist | A | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11043 | 820.10 | 820-10-18 | 820 | 820HS-91552-02 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11044 | 820.10 | 820-10-18 | 820 | 820HS-91552-02 | Guide support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11045 | 820.10 | 820-10-18 | 820 | 820HS-91552-11 | Valve paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11046 | 820.10 | 820-10-18 | 820 | 820HS-91552-11 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11047 | 820.10 | 820-10-18 | 820 | 820HS-91552-12 | Valve paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11048 | 820.10 | 820-10-18 | 820 | 820HS-91552-12 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11049 | 820.10 | 820-10-18 | 820 | 820HS-91552-13 | Valve paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11050 | 820.10 | 820-10-18 | 820 | 820HS-91552-13 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11051 | 820.10 | 820-10-18 | 820 | 820HS-91552-14 | Valve paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11052 | 820.10 | 820-10-18 | 820 | 820HS-91552-14 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11053 | 820.10 | 820-10-18 | 820 | 820HS-91552-15 | Valve visor bolts to be clean | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11054 | 820.10 | 820-10-18 | 820 | 820HS-91552-15 | Valve paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11055 | 820.10 | 820-10-18 | 820 | 820HS-91552-15 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11056 | 820.10 | 820-10-18 | 820 | 820HS-91552-03 | Valve visor bolts to be clean | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11057 | 820.10 | 820-10-18 | 820 | 820HS-91552-03 | Valve paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11058 | 820.10 | 820-10-18 | 820 | 820HS-91552-03 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11059 | 820.10 | 820-10-18 | 820 | 820HS-91552-04 | Support paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11060 | 820.10 | 820-10-18 | 820 | 820HS-91552-04 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11061 | 820.10 | 820-10-18 | 820 | 820HS-91558-01 | Piping insulation missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11062 | 820.10 | 820-10-18 | 820 | 820HS-91552-05 | Valve visor bolts to be clean | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11063 | 820.10 | 820-10-18 | 820 | 820HS-91552-05 | Valve paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11064 | 820.10 | 820-10-18 | 820 | 820HS-91552-05 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11065 | 820.10 | 820-10-18 | 820 | 820HS-91552-05 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11066 | 820.10 | 820-10-18 | 820 | 820HS-91552-05 | Masking tape to be remove from valve stem | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11067 | 820.10 | 820-10-18 | 820 | 820HS-91552-05 | Globe valve installed instead of check valve to be clarify | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11068 | 820.10 | 820-10-18 | 820 | 820HS-91552-07 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11069 | 820.10 | 820-10-18 | 820 | 820HS-91552-07 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11070 | 820.10 | 820-10-18 | 820 | 820HS-91551-01 | Piping insulation missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11071 | 820.10 | 820-10-18 | 820 | 820HS-91551-01 | Flange connections rusted bolts to be clean and apply molykote | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11072 | 820.10 | 820-10-18 | 820 | 820HS-91553-01 | Boiler connection to be boxed up | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11073 | 820.10 | 820-10-18 | 820 | 820HS-91553-01 | There is no cut-off valve in the instrument connection. Specify how to restore the device if it fails. | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11074 | 820.10 | 820-10-18 | 820 | 820HS-91553-01 | Piping insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11075 | 820.10 | 820-10-18 | 820 | 820HS-91553-02 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11076 | 820.10 | 820-10-18 | 820 | 820HS-91553-02 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11077 | 820.10 | 820-10-18 | 820 | 820HS-91559-01 | Valve hand wheel paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11078 | 820.10 | 820-10-18 | 820 | 820HS-91559-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11079 | 820.10 | 820-10-18 | 820 | 820HS-91559-01 | Steam trap with acceptance to feed/bedd to be confirm | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-10-20 |  | Walkdown | [8 empty] | RFC/RFSU
. | 11080 | 820.10 | 820-10-18 | 820 | 820NY-91661-01 | Guide support installed to be updated in ISO | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-10-20 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 11081 | 820.10 | 820-10-18 | 820 | 820-US-011 | Limited walkway on the platform 1 (around 35 cm between the utility station and piping/equipment) | C | EM | HEC PI Design | Mr. Piotr Słowik | 2022-10-20 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 13575 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | General | Provide grommet for the edge of cable tray | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 13576 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | General | The warning labels shall be bilingual (Polish labels shall be added). | B | CI | HEC CI Construction | Owner Maintenance team | 2022-11-04 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 13577 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | General | Atex Marking of all instrument should be verified and the correct ATEX marking selected on device. | B | CI | HEC CI Construction | Owner Maintenance team | 2022-11-04 | 2023-01-11 | Walkdown |  |  | 2023-01-09 |  | V |  |  |  | RFC/RFSU
. | 13578 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-PT-1001A, 820-PT-1001B, 820-PT-1002, 820-PT-1003, 820-PT-1004A, 820-PT-1004B | Replace the blind plug of instrument with Atex specification | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-12-01 | Walkdown |  |  | 2022-11-30 |  | V |  |  |  | RFC/RFSU
. | 13579 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-LT-1001, 820-LT-1002A | Internal inspection label shall be supplemented. | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-12-05 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 13580 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-AR-001, 820-AR-002 | Aluminium part of isolation was demaged in several places - it shall be repaired. | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-11-28 | Walkdown |  | 2022-11-28 | 2022-11-28 |  | V |  |  |  | RFC/RFSU
. | 13581 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-AR-001, 820-AR-002 | Sample outlet shall be provided slope | B | CI | HEC CI Construction | Owner Maintenance team | 2022-11-04 | 2022-12-12 | Walkdown |  | Rejected.. Phot need for outlet sampling point.. Should provide the Slope | 2022-12-02 |  | V |  |  |  | RFC/RFSU
. | 13582 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-AR-001 | Flowmeter mounting brackets should be tightened | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-11-28 | Walkdown |  | 2022-11-28 | 2022-11-28 |  | V |  |  |  | RFC/RFSU
. | 13583 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-AR-002 | JB Power cable gland quantity shall be verified | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-12-01 | Walkdown |  | 2022-11-30 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 13584 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-AR-002 | Power cable installation shall be improved | B | EL | HEC EL Construction | Owner Maintenance team | 2022-11-04 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 13585 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-SN-0111, 820-SN-0211 | 820-SN-0111 and 820-SN-0211 are manual sampling units, but on site cooler have these TAG NOs. It shall be verified and corrected. | B | CI | HEC CI Construction | Owner Maintenance team | 2022-11-04 | 2023-01-13 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 13586 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-FO-9022A, 820-FO-9022B | The orificies shall be installed. | B | PI | HEC PI Construction | Owner Maintenance team | 2022-11-04 | 2023-01-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 13587 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-PT-1004B | Radiator inside cabinet shall be tightened | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-26 |  | V |  |  |  | RFC/RFSU
. | 13588 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-PT-1002, 820-PT-1003 | Glanding shall be tightened | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-11-30 | Walkdown |  | 2022-11-29 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 13589 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-FO-8021B | Improper Tag NO - it shall be A instead of B | B | PI | HEC PI Construction | Owner Maintenance team | 2022-11-04 | 2023-01-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 13590 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-PRV-0001A, 820-PRV-0001B | Mounted in reverse - B is mounted first down the line, it shall be exchanged A with B | B | PI | HEC PI Construction | Owner Maintenance team | 2022-11-04 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 13591 | 820.10 | 820-10-24 | Deaerator and BFW Distribution System | 820-PG-1001 | Electrical tracing shalll be done | B | EL | HEC EL Construction | Owner Maintenance team | 2022-11-04 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14908 | 820.10 | 820-10-18 | General | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2022-12-16 | Walkdown |  |  | 2022-12-16 |  | V |  |  |  | RFC/RFSU
. | 14909 | 820.10 | 820-10-20 | General | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 14910 | 820.10 | 820-10-24 | General | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2022-12-01 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 14911 | 820.10 | 820-10-26 | General | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2022-12-02 | Walkdown |  |  | 2022-12-02 |  | V |  |  |  | RFC/RFSU
. | 15271 | 820.10 | 820-10-12 | 200PR1-HS-0003 | HP Steam Distribution System | Reinstatement | A | PI | HEC PI Construction | J.W.JEONG | 2022-11-29 | 2022-12-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15272 | 820.10 | 820-10-12 | 810PR-HS-1001 | HP Steam Distribution System | Reinstatement | A | PI | HEC PI Construction | Ms. Alicja Sulżyc | 2022-11-29 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15273 | 820.10 | 820-10-12 | 700-X0002 | HP Steam Distribution System | Final Appeareance Inspection | C | IN | HEC IN Construction | J.W.JEONG | 2022-11-29 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15274 | 820.10 | 820-10-12 | 810PR-LS-1004 | HP Steam Distribution System | Final Appeareance Inspection | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-11-29 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15275 | 820.10 | 820-10-12 | 300PR-HS-2002 | HP Steam Distribution System | Final Appeareance Inspection | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-11-29 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15276 | 820.10 | 820-10-12 | 820-X0008 | 820-X0008 | Rust to be removed | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-29 | 2023-04-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15277 | 820.10 | 820-10-12 | 820-X0008 | 820-X0008 | Damage support to be repaired | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-29 | 2023-02-10 | Walkdown |  |  |  | DA | V |  |  |  | RFC/RFSU
. | 15278 | 820.10 | 820-10-12 | 820-X0008 | 820-X0008 | Rust on flange connection between pipe and silencer to be cleaned and protected | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-29 | 2023-04-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15279 | 820.10 | 820-10-12 | 700-X0002 | 700-X0002 | No accesss to operate the valve | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-29 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15280 | 820.10 | 820-10-12 | 700-X0002 | 700-X0002 | Insulation of piping at the bottom part to be completed | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-11-29 | 2023-02-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15281 | 820.10 | 820-10-12 | HP Steam Distribution System | 700-PV-1111 | Filter regulator position shall be corrected. | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2022-12-12 | Walkdown |  |  | 2022-12-06 |  | V |  |  |  | RFC/RFSU
. | 15282 | 820.10 | 820-10-12 | HP Steam Distribution System | 700-TT-1111 | Proper Atex markig shall be selected on devices | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2022-12-12 | Walkdown |  |  | 2022-12-06 |  | V |  |  |  | RFC/RFSU
. | 15283 | 820.10 | 820-10-12 | HP Steam Distribution System | 700-PT-1112 | Proper Atex markig shall be selected on devices. Drain tubing shall be connected. Electrical tracing shalll be done | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2022-12-12 | Walkdown |  |  | 2022-12-06 |  | V |  |  |  | RFC/RFSU
. | 15284 | 820.10 | 820-10-12 | HP Steam Distribution System | 700-PT-1112 | Electrical tracing shalll be done | A | EL | HEC EL Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-29 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15285 | 820.10 | 820-10-12 | HP Steam Distribution System | 700-JS-101 | Missing junction boxes grounding | A | EL | HEC EL Construction | Owner Maintenance team | 2022-11-29 | 2023-01-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15286 | 820.10 | 820-10-12 | HP Steam Distribution System | 700-PT-1111 | Proper Atex markig shall be selected on devices. Drain tubing shall be connected. Electrical tracing shalll be done | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15287 | 820.10 | 820-10-12 | HP Steam Distribution System | 700-PT-1111 | Electrical tracing shalll be done | A | EL | HEC EL Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-29 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15288 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PT-721 | Proper Atex markig shall be selected on devices. Electrical tracing shalll be done | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15289 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PT-721 | Electrical tracing shalll be done | A | EL | HEC EL Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-29 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15290 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-TT-721 | Proper Atex markig shall be selected on devices. Hanging Tag missing | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15291 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-SN-0721 | 820-SN-0721 is manual sampling units, but on site cooler have these TAG NO. It shall be verified and corrected. Manual sampling unit plate missing. | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15292 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PT-731 | Proper Atex markig shall be selected on devices. Electrical tracing shalll be done. Blind plug shall be replaced (shall be ATEX plug). | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15293 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PT-731 | Electrical tracing shalll be done | A | EL | HEC EL Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-29 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15294 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-TT-731 | Proper Atex markig shall be selected on devices. Hanging Tag missing | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15295 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-SN-0731 | 820-SN-0731 is manual sampling units, but on site cooler have these TAG NO. It shall be verified and corrected. Manual sampling unit plate missing. | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15296 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-TT-1022 | Proper Atex markig shall be selected on devices | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15297 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-FT-1013 | Electrical tracing shall be done | A | EL | HEC EL Construction | Owner Maintenance team | 2022-11-29 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15298 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PT-1007A | Proper Atex markig shall be selected on devices. Electrical tracing shalll be done. Problem with opening protection box (space collision) shall be solved. | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15299 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PT-1007A | Electrical tracing shalll be done | A | EL | HEC EL Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-29 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15300 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PT-1007B | Proper Atex markig shall be selected on devices. Electrical tracing shalll be done | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15301 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PT-1007B | Electrical tracing shalll be done | A | EL | HEC EL Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-29 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15302 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PT-1007C | Proper Atex markig shall be selected on devices. Electrical tracing shalll be done | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15303 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PT-1007C | Electrical tracing shalll be done | A | EL | HEC EL Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-29 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15304 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-FT-1011, 820-TT-1014, 820-LT-1007, 820-PG-1007 | No acces to devices. Walk down for these devices shall be repeated. | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2023-01-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15305 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PT-1009 | Proper Atex markig shall be selected on devices. Electrical tracing shalll be done | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15306 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PT-1009 | Electrical tracing shalll be done | A | EL | HEC EL Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-29 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15307 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-HV-1004 | Tubbing shall be connected | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-29 | 2023-01-11 | Walkdown |  |  | 2022-12-16 |  | V |  |  |  | RFC/RFSU
. | 15308 | 820.10 | 820-10-12 | HP Steam Distribution System | 700-PRO-PID-00111 | No access to handwheel near valve PV 1111 | C | EM | HEC PI Design | Ms. Alicja Sulżyc | 2022-11-29 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15309 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PRO-PID-00073 | Insulation not completed | B | IN | HEC IN Construction | Ms. Alicja Sulżyc | 2022-11-29 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15310 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PRO-PID-00073 | Wrong hanging tag on TE0731 | B | CI | HEC CI Construction | Ms. Alicja Sulżyc | 2022-11-29 | 2022-12-16 | Walkdown |  |  | 2022-12-16 |  | V |  |  |  | RFC/RFSU
. | 15311 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PRO-PID-00091 | Check valve installed in wrong direction | A | PI | HEC PI Construction | Mr. Jarosław Krzysztofowicz | 2022-11-29 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15312 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PRO-PID-00091 | Drain valve missing on P&ID | B | EM | HEC PR Design | Mr. Jarosław Krzysztofowicz | 2022-11-29 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15313 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PRO-PID-00091 | PG-1007 not installed | A | CI | HEC CI Construction | Mr. Jarosław Krzysztofowicz | 2022-11-29 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15314 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PRO-PID-00091 | No access (only temporary platform) to check LG-M 1003 and LT 1007 | C | EM | HEC PI Design | Ms. Alicja Sulżyc | 2022-11-29 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15315 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PRO-PID-00091 | No access to operate isolation valves on HP steam line no. 00105 | C | EM | HEC PI Design | Ms. Alicja Sulżyc | 2022-11-29 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15316 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PRO-PID-00121 | Missing valves according to PID | A | PI | HEC PI Construction | Mr. Jarosław Krzysztofowicz | 2022-11-29 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15317 | 820.10 | 820-10-12 | HP Steam Distribution System | 820-PRO-PID-00111 | Drain line to be relocated before MP Steam tie in from GAP | A | PI | HEC PI Construction | Ms. Alicja Sulżyc | 2022-11-29 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15318 | 820.10 | 820-10-12 | HP Steam Distribution System | n/a | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PI Construction | Ms. Paulina Bajer | 2022-11-29 | 2023-04-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 15319 | 820.10 | 820-10-12 | HP Steam Distribution System | n/a | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-29 |  | Walkdown | [8 empty] | RFC/RFSU
. | 16473 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00081 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16474 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00081 | Touch-up paint to be done on valve and handwheels | C | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16475 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00072 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16476 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00072 | Damaged insulation to be fixed and mastic to be applied on openings such as support, ET thermostat, etc. | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16477 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00072 | Touch-up paint to be done on valve and handwheels | C | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16478 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00073 / 820-4-HS-00110-MS-13-H | Grating opening to modified and fixed to avoid clashing with pipeline | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-12-09 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16479 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00073 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16480 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00073 | Damaged insulation to be fixed and mastic to be applied on openings such as support, ET thermostat, etc. | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16481 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00073 | Touch-up paint to be done on valve and handwheels | C | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16482 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00073 | Touch-up paint to be done on pipe supports | C | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16483 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / 810WT-820HS00106-01 | Bolt tightening to be done on flange connection (820-B0004) | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16484 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / 810WT-820HS00106-01 | Rusted bolts and nuts on flange connection (820-B0004) | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16485 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / 810WT-820HS00106-01 | Grating opening to modified and fixed to avoid clashing with pipeline | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-12-09 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16486 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 | Rusted bolts and nuts on flange connection (near LG-M-1003) | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16487 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / 810PR-820HS09101 | Missing valve handwheels (vertical line going to silencer 820-X0008) | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-12-09 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16488 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / 810PR-820HS09101 | Scaffolding clashing with pipe and valves to be removed | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-12-09 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16489 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / 810PR-820HS09101 | Toe plate to be installed | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-12-09 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16490 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / 810PR-820HS09101 | Rusted bolts on 3/4'' valve | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16491 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / HS-00105 | Piping Insulation to be completed | C | IN | HEC FP Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16492 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / HS-00106 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16493 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / HS-09103 | Piping Insulation missing | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16494 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / HS-09101 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16495 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / HS-00105 | Touch-up paint to be done on valve and handwheels | C | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16496 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / HS-09103 | Touch-up paint to be done on valve and handwheels | C | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16497 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / HS-09101 | Touch-up paint to be done on valve and handwheels | C | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16498 | 820.10 | 820-10-12 |  | EGAT-HEC-820-PRO-PID-00091 / 820-10-HS00106 | Touch-up paint to be done on strainer (TSTR-003) | C | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16499 | 820.10 | 820-10-12 |  | EGAT-HEC-700-PRO-PID-00111 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16500 | 820.10 | 820-10-12 |  | EGAT-HEC-700-PRO-PID-00111 | Touch-up paint to be done on valve and handwheels. | C | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16501 | 820.10 | 820-10-12 |  | EGAT-HEC-700-PRO-PID-00121 | Piping Insulation to be completed | C | IN | HEC PA Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16502 | 820.10 | 820-10-12 |  | EGAT-HEC-700-PRO-PID-00121 | Touch-up paint to be done on valve and handwheels. | C | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16503 | 820.10 | 820-10-12 |  | GENERAL | INSULATION NOT DONE PROPERLY: NO DISTANCE FOR BOLTS, NOT CLOSED WITH CAPS OR PROTECTED NEAR FLANGES, NOT PROPERLY COVERED SUPPORTS ETC. | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-12-09 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16504 | 820.10 | 820-10-12 |  | GENERAL | TOE GURAD TO BE INSTALLED | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2021-12-09 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17499 | 820.10 | 820-10-14 | 820-X0010 | 820-X0010 | Rust to be removed on the desuperheater | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-09 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17500 | 820.10 | 820-10-14 | 820-X0010 | 820-X0010 | Rust on handle to be cleaned and protected | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-09 | 2023-01-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17501 | 820.10 | 820-10-14 | 820-X0010 | 820-X0010 | Touch up painting to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-09 | 2023-03-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17502 | 820.10 | 820-10-14 | 820-X0003 | 820-X0003 | Rust to be removed on the desuperheater | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-09 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17503 | 820.10 | 820-10-14 | 820-X0003 | 820-X0003 | Rust on handle to be cleaned and protected | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-09 | 2023-01-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17504 | 820.10 | 820-10-14 | 820-X0003 | 820-X0003 | Touch up painting to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-09 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17505 | 820.10 | 820-10-14 | 820-X0011A | 820-X0011A | Rust to be removed on the desuperheater | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-09 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17506 | 820.10 | 820-10-14 | 820-X0011A | 820-X0011A | Rust on handle to be cleaned and protected | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-09 | 2023-01-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17507 | 820.10 | 820-10-14 | 820-X0011A | 820-X0011A | Touch up painting to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-09 | 2023-03-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17508 | 820.10 | 820-10-14 | 820-X0011B | 820-X0011B | Rust to be removed on the desuperheater | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-09 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17509 | 820.10 | 820-10-14 | 820-X0011B | 820-X0011B | Rust on handle to be cleaned and protected | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-09 | 2023-01-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17510 | 820.10 | 820-10-14 | 820-X0011B | 820-X0011B | Touch up painting to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-09 | 2023-03-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17511 | 820.10 | 820-10-14 |  | 820-PRO-PID-00071 | No access to all manual valves upstream of TV-1008 | C | EM | HEC PI Design | Mr. Piotr Słowik | 2022-12-09 |  | Walkdown | [8 empty] | RFC/RFSU
. | 17512 | 820.10 | 820-10-14 |  | 820-PRO-PID-00071 | Rusted bolts | B | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-09 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17513 | 820.10 | 820-10-14 |  | 820-PRO-PID-00071 | Rusted coil (SN-0711) | A | PI | HEC PI Construction | Mr. Piotr Słowik | 2022-12-09 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17514 | 820.10 | 820-10-14 |  | 820-PRO-PID-00072 | No acces to the valves on main steam line | C | EM | HEC PI Design | Ms. Paulina Bajer | 2022-12-09 |  | Walkdown | [8 empty] | RFC/RFSU
. | 17515 | 820.10 | 820-10-14 |  | 820-PRO-PID-00072 | Electrical tracing to be provided | B | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-12-09 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17516 | 820.10 | 820-10-14 |  | 820-PRO-PID-00072 | Drain valve missing in P&ID upstream of STRP-002 | B | EM | HEC PR Design | Ms. Paulina Bajer | 2022-12-09 | 2023-01-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17517 | 820.10 | 820-10-14 |  | 820-PRO-PID-00073 | Drain valve missing in P&ID upstream of STRP-003 | B | EM | HEC PR Design | Ms. Paulina Bajer | 2022-12-09 | 2023-01-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17518 | 820.10 | 820-10-14 |  | 820-PRO-PID-00073 | CSO valve on line no. BW-00113-MS-13-ET unable to operate | B | PI | HEC PI Construction | Mr. Piotr Słowik | 2022-12-09 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17519 | 820.10 | 820-10-14 |  | 820-PRO-PID-00073 | Support touch-up painting | B | PA | HEC PA Construction | Ms. Alicja Sulżyc | 2022-12-09 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17520 | 820.10 | 820-10-14 |  | 820-PRO-PID-00071 | Grating on the platform incomplete (large holes) | B | SS | HEC SS Construction | Ms. Alicja Sulżyc | 2022-12-09 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17521 | 820.10 | 820-10-14 |  | 900-PRO-PID-05012 | Reference to the typical for steam traps to be specified in notes in P&ID. | B | EM | HEC PR Design | Mr. Piotr Słowik | 2022-12-09 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17522 | 820.10 | 820-10-14 |  | 900-PRO-PID-05012 | rusted handwheels | B | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-09 | 2023-01-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17523 | 820.10 | 820-10-14 |  | 970-PRO-PID-00041 | no acces to the manual valve next to FT-1001A/B | C | EM | HEC PI Design | Ms. Paulina Bajer | 2022-12-09 |  | Walkdown | [8 empty] | RFC/RFSU
. | 17524 | 820.10 | 820-10-14 |  | 970-PRO-PID-00041 | FT-1001A/B - to be connected | A | CI | HEC CI Construction | Mr. Piotr Słowik | 2022-12-09 | 2022-12-28 | Walkdown |  |  | 2022-12-23 |  | V |  |  |  | RFC/RFSU
. | 17525 | 820.10 | 820-10-14 |  | All Pipelines | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-09 | 2023-04-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17669 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092A | PG-9403 not installed | A | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-03 | Walkdown |  |  | 2023-01-03 |  | V |  |  |  | RFC/RFSU
. | 17670 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092A | Pipeline 820-1"-LO-94010-LC53-ET not installed | A | ME | HEC ME Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17671 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092A | Pipeline 820-2"-LO-94011-LC53-N not installed | A | ME | HEC ME Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17672 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092A | Pipeline 820-3"-LO-94012-LC53-N not installed | A | ME | HEC ME Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17673 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092A | Lack of ID TAG PLATE for: PG-9401, PG9402, SG-9401, SG-9402 | C | ME | HEC ME Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-06-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17674 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092A | Heat tracing for: PG-9401, and PG-9402 not installed | A | EL | HEC EL Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17675 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092A | Wrong tag of TE-9405 | C | ME | HEC ME Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-06-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17676 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092A | Lack of ID TAG PLATE for: PG-9404 | C | ME | HEC ME Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-06-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17677 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092A | Wrong positions of spectacle blinds | B | ME | HEC ME Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17678 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092C | PG-9407, PG-9408 not installed | A | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-20 | Walkdown |  |  | 2023-01-20 |  | V |  |  |  | RFC/RFSU
. | 17679 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092C | Insulation for pipelines not installed: 820-2"-LS-09201-MS-11-H 820-4"-LS-09207-E1A1-H | C | IN | HEC IN Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17680 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092C | Lack of access to sight glass SG-9408. It will not be possible to check the flow during the operational phase | A | EM | HEC MR Design | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17681 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092C | Heat tracing for lube oil skid to be verified (eg. Heat tracing is installed for 820-1"-LO-94127-LC53-N) | C | EM | HEC MR Design | Mr. Damian Maciejaszek | 2022-12-08 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17682 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092C | Flow orfices FO-9406 and FO-9407 not installed | A | ME | HEC ME Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17683 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092 | TG-0923 not installed | A | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-25 | Walkdown |  |  | 2023-01-25 |  | V |  |  |  | RFC/RFSU
. | 17684 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092 | TG-0922 and PG-0922 not installed | A | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-25 | Walkdown |  |  | 2023-01-25 |  | V |  |  |  | RFC/RFSU
. | 17685 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092 | TG-0921 and PG-0921 not installed | A | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-25 | Walkdown |  |  | 2023-01-25 |  | V |  |  |  | RFC/RFSU
. | 17686 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092 | Heat tracing for: 820-B0004-ST01 not installed | A | EL | HEC EL Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17687 | 820.10 | 820-10-10 | Steam Turbine Power Generator Package | 820-PRO-PID-00092 | Heat tracing for line 820-2"-LO-09206-LC53-ET not installed | A | EL | HEC EL Construction | Mr. Damian Maciejaszek | 2022-12-08 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17688 | 820.10 | 820-10-10 | 820-B0004-ST02 | General | loose U-bolt to be tightend | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2022-12-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17689 | 820.10 | 820-10-10 | 820-B0004-ST02 | 820-B0004-ST02 | Rusted instrument cover on the skid to be clean | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2022-12-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17690 | 820.10 | 820-10-10 | 820-B0004-ST02 | 820-B0004-ST02 | Rust on the tank to be remove | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2022-12-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17691 | 820.10 | 820-10-10 | 820-B0004-ST02 | 820-B0004-ST02 | Broken drain line to be replaced and tested | A | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-31 | Walkdown |  |  |  | PI | V |  |  |  | RFC/RFSU
. | 17692 | 820.10 | 820-10-10 | 820-B0004-ST02 | General | Rusted valve wheel to be painted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17693 | 820.10 | 820-10-10 | 820-B0004-ST02 | 820-B0004-ST02 | Housekeeping to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17694 | 820.10 | 820-10-10 | 820-B0004-ST02 | 820-B0004-ST02 | Touch -up painting for the skid to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17695 | 820.10 | 820-10-10 | 820-B0004-ST02 | 820-B0004-ST02 | Motor to be clean | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2022-12-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17696 | 820.10 | 820-10-10 | 820-B0004-ST02 | 820-B0004-ST02 | Grating clips to be tightened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2022-12-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17697 | 820.10 | 820-10-10 | 820-B0004-ST02 | 820-B0004-ST02 | 810-WT-820 ( 820-SG-9405) flange bolt connection to be rectified stainless to teflon | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 |  | Walkdown |  |  |  | EM | V |  |  |  | RFC/RFSU
. | 17698 | 820.10 | 820-10-10 | 820-B0004-ST02 | 820-B0004-ST02 | Oil mist separator motor to be cleaned | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2022-12-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17699 | 820.10 | 820-10-10 | 820-B0004-ST02 | 820-B0004-ST02 | Stainless flange to carbon steel bolt and nuts to be verefied | C | EM | HEC MR Design | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-03-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17700 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004 | loose U-bolt to be tightend | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17701 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004 | Final inspection | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17702 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004 | Final alignment | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17703 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004 | Housekeeping to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17704 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004 | Touch up painting to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17705 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004 | Rusted bolts and nuts to be cleaned and protected | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17706 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004 | Couplings not installed | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17707 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004 | Temporary tarpaulin cover to be removed (after shelter roof completion) to allow reinspection, top of the turbine and generator not verified due to limited access (temporary cover) | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17708 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004 | Wet and Damage insulation cover to be replaced | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 |  | Walkdown |  | Changed from Category B |  | IN |  |  |  | 2023-03-10 | RFC/RFSU
. | 17709 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004 | Temporary blinds to be replace | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17710 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004-ST01 | Housekeeping to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17711 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004-ST01 | Painting of structure to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17712 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004-ST01 | Lighting lamp to be rectified ( very near to the ladder ) | B | EL | HEC EL Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17713 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004-ST01 | Rust on the tank to be removed | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17714 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004-ST01 | Gratings to be completed | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17715 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004-ST01 | Grating clips to be tigthened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17716 | 820.10 | 820-10-10 | 820-B0004 | 820-B0004-ST01 | Insulation on rundown tank is missing | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17717 | 820.10 | 820-10-10 |  | 820-B0004 | Limited Space for maintenance (collission with cable tray) | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-08 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17718 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092 | Grating to be fixed on the Rundown Tank platform | B | ME | HEC ME Construction | Mr. Piotr Słowik | 2022-12-08 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17719 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092 | Touch-up painting of supports to be provided | C | PA | HEC PA Construction | Mr. Piotr Słowik | 2022-12-08 | 2023-05-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17720 | 820.10 | 820-10-10 |  | general | Insulation incomplete - Walkdown to be repeated | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17721 | 820.10 | 820-10-10 |  | general | Electrical tracing to be provided | B | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17722 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092 | Electrical tracing to be specified in P&ID in drain line. | B | EM | HEC PR Design | Ms. Paulina Bajer | 2022-12-08 | 2022-12-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17723 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092 | missing plugs on drain valves on CWS/CWR lines | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-01-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17724 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092 | drain valve on CWR line to be spcified in P&ID upstream of the isolation valve | B | EM | HEC PR Design | Ms. Paulina Bajer | 2022-12-08 | 2022-12-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17725 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092 | PG-0923 to be installed | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-01-16 | Walkdown |  |  | 2023-01-14 |  | V |  |  |  | RFC/RFSU
. | 17726 | 820.10 | 820-10-10 |  | general | Rusted bolts | B | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17727 | 820.10 | 820-10-10 |  | general | rusted flanges | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-05-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17728 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092 | NY to be provided for drains | C | AR | HEC AR Construction | Ms. Małgorzata Juszczyk | 2022-12-08 | 2023-02-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17729 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092 | ditch to be cleaned | C | CV | HEC CV Construction | Ms. Małgorzata Juszczyk | 2022-12-08 | 2023-01-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17730 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092C | bleed to be provided | A | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2022-12-08 | 2023-02-03 | Walkdown |  |  |  | (DA) 해당 Valve 설치 부탁 드립니다. Vendor supply | V |  |  |  | RFC/RFSU
. | 17731 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092C | rusted valve upstream of YSTR-9401 and rusted strainer | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-05-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17732 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092H | rusted handwheels | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-05-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17733 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092H | TE-9416 instead of TE-9406 installed at Site | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-01-03 | Walkdown |  |  | 2023-01-03 |  | V |  |  |  | RFC/RFSU
. | 17734 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092H | Wrong hanging tag on cable to LT-9402 | B | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-01-03 | Walkdown |  |  | 2023-01-03 |  | V |  |  |  | RFC/RFSU
. | 17735 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092H | SG-9408/9409 - not visible to the operator | B | ME | HEC ME Construction | Mr. Piotr Słowik | 2022-12-08 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17736 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092H | YSTR-9402 - not enough space to replace the spacer | B | ME | HEC ME Construction | Mr. Piotr Słowik | 2022-12-08 | 2023-01-31 | Walkdown |  |  |  | Element 빼는 것이 불가하면 45도 돌려서 조치 부탁 드립니다. FE Comment | V |  |  |  | RFC/RFSU
. | 17737 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092H | Configuration in P&ID in the blower area is not in line with Site conditions | C | ME | HEC ME Construction | Mr. Piotr Słowik | 2022-12-08 |  | Walkdown | [8 empty] | RFC/RFSU
. | 17738 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092H | PG-9415 to be installed | B | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17739 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092H | ET for CW lines to be specified in P&ID (line nos. To be corrected) | B | EM | HEC PR Design | Ms. Paulina Bajer | 2022-12-08 | 2022-12-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17740 | 820.10 | 820-10-10 |  | EGAT-HEC-820-PRO-PID-00092H | U-Bolt to be tightened | B | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2022-12-08 | 2023-01-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17741 | 820.10 | 820-10-10 |  | general | Locking device missing | C | COMM | HEC COMM | Ms. Małgorzata Juszczyk | 2022-12-08 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17742 | 820.10 | 820-10-10 |  |  | Drain missing on TCV-9401 bypass line in P&ID | B | EM | HEC PR Design | Ms. Małgorzata Juszczyk | 2022-12-08 | 2022-12-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17743 | 820.10 | 820-10-10 | Steam Turbine Power Generator package | EGAT-HEC-820-PRO-PID-00092G | Cable trench cleaning and sealing to be provided | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-08 |  | Walkdown | [8 empty] | RFC/RFSU
. | 17744 | 820.10 | 820-10-10 | Steam Turbine Power Generator package | EGAT-HEC-820-PRO-PID-00092G | NER cleaning to done | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-08 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17745 | 820.10 | 820-10-10 | Steam Turbine Power Generator package | EGAT-HEC-820-PRO-PID-00092G | Stub-up Conduit duct sealing to be provided | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-08 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17746 | 820.10 | 820-10-10 | Steam Turbine Power Generator package | EGAT-HEC-820-PRO-PID-00092G | MV cable termination and cable testing inspection to be carried out | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-08 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17747 | 820.10 | 820-10-10 | Steam Turbine Power Generator package | EGAT-HEC-820-PRO-PID-00092G | Deleted cables to be kept inside cable to be kept inside cble tray. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-08 | 2023-01-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17748 | 820.10 | 820-10-10 | Steam Turbine Power Generator package | EGAT-HEC-820-PRO-PID-00092H | Tagno:- 820-B0004-MW01A & B Demisstor Auxillary motor cable connections and earthing connections to be done. | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-08 | 2023-01-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17749 | 820.10 | 820-10-10 | Steam Turbine Power Generator package | EGAT-HEC-820-PRO-PID-00092C | Gland steam condensor skid earthing to be done | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-08 | 2023-01-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17750 | 820.10 | 820-10-10 | Steam Turbine Gland Steam Condenser |  | Rust on many fixing elements at Gland Steam Condenser nozzles | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-12-08 | 2023-01-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17751 | 820.10 | 820-10-10 |  |  | Rusted valves and fixing elements | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-12-08 | 2023-01-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17752 | 820.10 | 820-10-10 |  |  | Temporary blind flanges | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-12-08 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17753 | 820.10 | 820-10-10 |  |  | Not installed measuring devices | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-12-08 | 2023-01-30 | Walkdown |  |  |  | Will close | V |  |  |  | RFC/RFSU
. | 17754 | 820.10 | 820-10-10 |  |  | Not installed grounding | A | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2022-12-08 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17755 | 820.10 | 820-10-10 |  |  | Not finished heat tracing | A | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2022-12-08 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17756 | 820.10 | 820-10-10 |  |  | Stainless steel installation of IA for 820-TCV-9401 connected by rusted carbon steel bolts | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-12-08 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17757 | 820.10 | 820-10-10 |  |  | Not finished construction works at ST Generator - cables not properly fixed and switchgear not bolted | A | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2022-12-08 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17758 | 820.10 | 820-10-10 |  |  | Rust in many places on installations at ST area | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-12-08 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17759 | 820.10 | 820-10-10 |  |  | Rust on supporting structures at ST area | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-12-08 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17760 | 820.10 | 820-10-10 |  |  | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-04-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 17761 | 820.10 | 820-10-10 |  |  | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-08 |  | Walkdown | [8 empty] | RFC/RFSU
. | 18543 | 820.10 | 820-10-16 | 820-X0002A/B | 820-X0002A/B | Touch-up painting of handwheel | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-14 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18544 | 820.10 | 820-10-16 | 820-X0002A/B | 820-X0002A/B | Touch-up painting of body | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-14 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18545 | 820.10 | 820-10-16 | 820-X0003 | 820-X0003 | Touch-up painting of handwheel | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-14 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18546 | 820.10 | 820-10-16 | 820-X0003 | 820-X0003 | Touch-up painting of body | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-14 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18547 | 820.10 | 820-10-16 | 820-X0012 | 820-X0012 | Touch-up painting of handwheel | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-14 | 2023-03-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18548 | 820.10 | 820-10-16 | 820-X0012 | 820-X0012 | Touch-up painting of body | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-14 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18549 | 820.10 | 820-10-16 | 820-X0009 | 820-X0009 | Touch up painting of the silencer | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-14 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18550 | 820.10 | 820-10-16 | 820-X0009 | 820-X0009 | Rusted bolt and nuts to be cleaned and protected | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-14 | 2023-01-30 | Walkdown |  |  |  | DA | V |  |  |  | RFC/RFSU
. | 18551 | 820.10 | 820-10-16 | 820-X0009 | 820-X0009 | Rusted wire to be remove | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-14 | 2023-01-30 | Walkdown |  |  |  | DA | V |  |  |  | RFC/RFSU
. | 18552 | 820.10 | 820-10-16 | 820-X0009 | 820-X0009 | temporary tape on the lifting lug to be removed | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-14 | 2023-03-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18553 | 820.10 | 820-10-16 | 820-X0005 | 820-X0005 | Touch up painting of the silencer | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-14 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18554 | 820.10 | 820-10-16 | 820-X0005 | 820-X0005 | Rusted bolt and nuts to be cleaned and protected | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-14 | 2023-01-30 | Walkdown |  |  |  | DA | V |  |  |  | RFC/RFSU
. | 18555 | 820.10 | 820-10-16 | AUX | 200FS3-LS-1004 | Reinstatement to be done | A | PI | HEC PI Construction | J.W.JEONG | 2022-12-14 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18556 | 820.10 | 820-10-16 | AUX | 200PR1-LS-0002 | Reinstatement to be done | A | PI | HEC PI Construction | J.W.JEONG | 2022-12-14 | 2022-12-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18557 | 820.10 | 820-10-16 | AUX | General | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-05-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18558 | 820.10 | 820-10-16 | AUX | General | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-14 |  | Walkdown | [8 empty] | RFC/RFSU
. | 18559 | 820.10 | 820-10-16 | AUX | 840-TV-1003 | Missing Atex name plate of the valve | C | CI | HEC CI Construction | Owner Maintenance team | 2022-12-14 | 2023-03-15 | Walkdown |  |  | 2023-03-03 |  | V |  |  |  | RFC/RFSU
. | 18560 | 820.10 | 820-10-16 | AUX | 870-FV-4511/FV-4501 | The cable glanding should be tightened properly | C | CI | HEC CI Construction | Owner Maintenance team | 2022-12-14 | 2023-01-05 | Walkdown |  |  | 2022-12-29 |  | V |  |  |  | RFC/RFSU
. | 18561 | 820.10 | 820-10-16 | AUX | 870-FT-4511/810-PT-1033 | The cover of transmitter should be tightened properly | C | CI | HEC CI Construction | Owner Maintenance team | 2022-12-14 | 2023-01-05 | Walkdown |  |  | 2022-12-29 |  | V |  |  |  | RFC/RFSU
. | 18562 | 820.10 | 820-10-16 | AUX | 810-PT-1009 | Thermmostat inside enclosure box to be fix & the cover of transmitter have scratch must be apply touch up paint | C | CI | HEC CI Construction | Owner Maintenance team | 2022-12-14 | 2023-01-16 | Walkdown |  |  | 2023-01-07 |  | V |  |  |  | RFC/RFSU
. | 18563 | 820.10 | 820-10-16 | AUX | 810-TV-1005 | Replace the plug on the valve positioner by ATEX blind plug | C | CI | HEC CI Construction | Owner Maintenance team | 2022-12-14 | 2023-01-05 | Walkdown |  |  | 2022-12-30 |  | V |  |  |  | RFC/RFSU
. | 18564 | 820.10 | 820-10-16 | AUX | 820-PT-1006A/B/C & 870-FT-4501 | On the seal pot drain side insulation plaster should be cut in order to removed or installed the blind plug | C | CI | HEC CI Construction | Owner Maintenance team | 2022-12-14 | 2023-01-05 | Walkdown |  |  | 2023-01-02 |  | V |  |  |  | RFC/RFSU
. | 18565 | 820.10 | 820-10-16 | AUX | 820-TT-1010/TT-1008/TT-1013/TT-1011 | Mounting installaton of transmitter should be tightened properly | C | CI | HEC CI Construction | Owner Maintenance team | 2022-12-14 | 2023-02-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18566 | 820.10 | 820-10-16 | AUX | 820-TV-1008/PV-1007B | Tubing to be connect | B | CI | HEC CI Construction | Owner Maintenance team | 2022-12-14 | 2023-01-05 | Walkdown |  |  | 2022-12-29 |  | V |  |  |  | RFC/RFSU
. | 18567 | 820.10 | 820-10-16 | AUX | 820-PT-1008A/B/C | Replace the plug on the transmitter by Atex blind plug | C | CI | HEC CI Construction | Owner Maintenance team | 2022-12-14 | 2023-01-05 | Walkdown |  |  | 2022-12-30 |  | V |  |  |  | RFC/RFSU
. | 18568 | 820.10 | 820-10-16 | AUX | 820-HV-1003 | The air regulator should be rotate in proper postion | B | CI | HEC CI Construction | Owner Maintenance team | 2022-12-14 | 2023-01-17 | Walkdown |  |  | 2023-01-14 |  | V |  |  |  | RFC/RFSU
. | 18569 | 820.10 | 820-10-16 | AUX | 820-TV-1019 | The positioner of valve must be in accessable location & air regulator gauge of valve is broken | B | CI | HEC CI Construction | Owner Maintenance team | 2022-12-14 | 2023-01-24 | Walkdown |  |  | 2023-01-21 | Rejected.... Positioner need to move other Side... for access.. | V |  |  |  | RFC/RFSU
. | 18570 | 820.10 | 820-10-16 | AUX | utility stations | Pipeline shaking, additional support to be provoded for the most of US | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18571 | 820.10 | 820-10-16 | AUX | utility stations | Insulation incomplete | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18572 | 820.10 | 820-10-16 | AUX | EGAT-HEC-600-PRO-PID-00041 | Spectacle blind to be relocated in P&ID downstream of the valve | B | EM | HEC PR Design | Ms. Paulina Bajer | 2022-12-14 | 2022-12-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18573 | 820.10 | 820-10-16 | AUX | EGAT-HEC-600-PRO-PID-00041 | Rusted spectacle blind | B | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18574 | 820.10 | 820-10-16 | AUX | EGAT-HEC-700-PRO-PID-00021 | LS line to 700-E0001: support to be fixed | B | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-01-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18575 | 820.10 | 820-10-16 | AUX | EGAT-HEC-700-PRO-PID-00021 | bolting incomplete on flange connections | A | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2022-12-14 | 2023-01-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18576 | 820.10 | 820-10-16 | AUX | EGAT-HEC-810-PRO-PID-00101/161 | Electrical tracing to be provided | B | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18577 | 820.10 | 820-10-16 | AUX | common | Electrical tracing to be provided | B | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-01-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18578 | 820.10 | 820-10-16 | AUX | EGAT-HEC-820-PRO-PID-00011 | No acces to the valve upstream of the deaerator | C | EM | HEC PI Design | Ms. Paulina Bajer | 2022-12-14 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18579 | 820.10 | 820-10-16 | AUX | EGAT-HEC-820-PRO-PID-00011 | rusted valves | B | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-01-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18580 | 820.10 | 820-10-16 | AUX | EGAT-HEC-820-PRO-PID-00071 | PSV-0004A/B: touch-up paint to be done | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18581 | 820.10 | 820-10-16 | AUX | EGAT-HEC-820-PRO-PID-00081 | IA not connected with TVs | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-12-14 | 2022-12-30 | Walkdown |  |  | 2022-12-30 |  | V |  |  |  | RFC/RFSU
. | 18582 | 820.10 | 820-10-16 | AUX | EGAT-HEC-820-PRO-PID-00081 | No access to the valves | C | EM | HEC PI Design | Ms. Paulina Bajer | 2022-12-14 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18583 | 820.10 | 820-10-16 | AUX | 820-PRO-PID-00082 | No access to the valves | C | EM | HEC PI Design | Ms. Paulina Bajer | 2022-12-14 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18584 | 820.10 | 820-10-16 | AUX | 820-PRO-PID-00091 | TT-1018 and tt-1019 to be exchanged in P&ID | B | EM | HEC PR Design | Ms. Paulina Bajer | 2022-12-14 | 2023-01-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18585 | 820.10 | 820-10-16 | AUX | 820-PRO-PID-00091 | no access to LO valves | C | EM | HEC PI Design | Ms. Paulina Bajer | 2022-12-14 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18586 | 820.10 | 820-10-16 | AUX | 820-PRO-PID-00092 | LP steam line not connected with the turbine | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-14 | 2022-12-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18587 | 820.10 | 820-10-16 | AUX | 820-PRO-PID-00092c | rusted valve and strainer | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-12-14 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18588 | 820.10 | 820-10-16 | AUX | 850-PRO-PID-00021 | Piping sealing to be completed | B | CV | HEC CV Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18589 | 820.10 | 820-10-16 | AUX | 870-PRO-PID-00011 | no access the manual valve upstream of 870-E0001 | C | EM | HEC PI Design | Ms. Paulina Bajer | 2022-12-14 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18590 | 820.10 | 820-10-16 | AUX | 900-PRO-PID-00041 | plug on drain missing | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18591 | 820.10 | 820-10-16 | AUX | common | Insulation incomplete | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18592 | 820.10 | 820-10-16 | AUX | US on demi water tank | Touch-up painting (US on demi water tank) | B | PA | HEC PA Construction | Mr. Damian Maciejaszek | 2022-12-14 | 2023-01-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18593 | 820.10 | 820-10-16 | AUX | US-09 | Valve unable to operate (US-09) | B | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2022-12-14 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18594 | 820.10 | 820-10-16 | AUX |  | manual valves unable or hard to operate | B | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2022-12-14 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18595 | 820.10 | 820-10-16 | AUX |  | Drain valve to be specified in P&ID upstream of STRP bypass | B | EM | HEC PR Design | Ms. Paulina Bajer | 2022-12-14 | 2023-01-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18596 | 820.10 | 820-10-16 | AUX | Common | Rusted handwheels | B | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 18597 | 820.10 | 820-10-16 | AUX | Common | Visor bolts to be replaced to SS | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-14 | 2023-02-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23526 | 820.10 | 820-10-16 | 200FS2 | 200FS2-700LS00101-01 | Shoe support doesn't stick to the secondary support | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23527 | 820.10 | 820-10-16 | 200FS2 | 200FS2-700LS00101-01 | Visors to be cleaned | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23528 | 820.10 | 820-10-16 | 200FS2 | 200FS2-700LS00101-01 | Visor bolts rusted, to be replaced (ss) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23529 | 820.10 | 820-10-16 | 200FS2 | 200FS2-700LS00101-01 | Secondary touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23530 | 820.10 | 820-10-16 | 200FS2 | 200FS2-700LS00101-02 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23531 | 820.10 | 820-10-16 | 200FS2 | 200FS2-700LS00101-02 | Visor bolts rusted, to be replaced (ss) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23532 | 820.10 | 820-10-16 | 200FS2 | 200FS2-700LS00101-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23533 | 820.10 | 820-10-16 | 850WT | 850WT-850LS00101-02 | Insulation to be completed | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23534 | 820.10 | 820-10-16 | 850WT | 850WT-850LS00101-03 | No access (I can't perform inspection there) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23535 | 820.10 | 820-10-16 | 850WT | 850WT-850LS00106-01 | Valve's nut rusted | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23536 | 820.10 | 820-10-16 | 850WT | 850WT-850LS00106-01 | Visors to be cleaned | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23537 | 820.10 | 820-10-16 | 850WT | 850WT-850LS00106-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23538 | 820.10 | 820-10-16 | 850WT | 850WT-850LS00106-01 | Visor bolts rusted, to be replaced (ss) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23539 | 820.10 | 820-10-16 | 850WT | 850WT-850LS60002-01 | Insulation missing (the pipeline in clash with scaffolding) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23540 | 820.10 | 820-10-16 | 850WT | 850WT-850LS60003-01 | Painting tape to be removed from insulation | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23541 | 820.10 | 820-10-16 | 850WT | 850WT-850LS60004-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23542 | 820.10 | 820-10-16 | 850WT | 850WT-850LS60004-02 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23543 | 820.10 | 820-10-16 | 850WT | 850WT-850LS60004-02 | Masking tape to be removed from tag plate | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23544 | 820.10 | 820-10-16 | 850WT | 850WT-850LS60004-03 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23545 | 820.10 | 820-10-16 | 850WT | 850WT-850LS60004-03 | Wheel touch up paiting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23546 | 820.10 | 820-10-16 | 850WT | 850WT-850LS61002-01 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23547 | 820.10 | 820-10-16 | 850WT | 850WT-850LS61002-01 | Valve to be cleaned | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23548 | 820.10 | 820-10-16 | 850WT | 850WT-850LS61002-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23549 | 820.10 | 820-10-16 | 850WT | 850WT-850LS61003-01 | Valve body paiting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23550 | 820.10 | 820-10-16 | 850WT | 850WT-850LS61003-01 | Handle touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23551 | 820.10 | 820-10-16 | 850WT | 850WT-850LS61003-01 | Insulation missing (near flange) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23552 | 820.10 | 820-10-16 | 850WT | 850WT-850LS61003-01 | Insulation to be completed (the cap) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23553 | 820.10 | 820-10-16 | 200PR2 | 200PR2-200LS61009-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23554 | 820.10 | 820-10-16 | 200PR2 | 200PR2-200LS61009-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23555 | 820.10 | 820-10-16 | 200PR2 | 200PR2-200LS61009-01 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23556 | 820.10 | 820-10-16 | 200RS3 | 200RS3-700LS00102-01 | Insulation missing (the pipeline in clash with scaffolding) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23557 | 820.10 | 820-10-16 | 200RS3 | 200RS3-700LS00102-01 | Ending of the fastening insulation strip to be cut off | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23558 | 820.10 | 820-10-16 | 200RS3 | 200RS3-700LS00103-01 | Visor glass missing | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23559 | 820.10 | 820-10-16 | 200RS3 | 200RS3-700LS00103-01 | Visor bolts rusted, to be replaced (ss) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23560 | 820.10 | 820-10-16 | 200RS3 | 200RS3-700LS00103-01 | Visor to be cleaned | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23561 | 820.10 | 820-10-16 | 200RS3 | 200RS3-700LS61502-01 | Insulation to be repaired (masking tape) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23562 | 820.10 | 820-10-16 | 200RS3 | 200RS3-700LS61502-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23563 | 820.10 | 820-10-16 | 200RS3 | 200RS3-700LS61502-01 | The pipeline needs to be stabilized (it's shaking) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23564 | 820.10 | 820-10-16 | 200RS3 | 200RS3-700LS61502-01 | Whell touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23565 | 820.10 | 820-10-16 | 700FS | 700FS-700LS60001-02 | Insulation fastening strip to be removed | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23566 | 820.10 | 820-10-16 | 700FS | 700FS-700LS60001-02 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23567 | 820.10 | 820-10-16 | 700FS | 700FS-700LS60001-02 | Masking tape to be removed from tag plate | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23568 | 820.10 | 820-10-16 | 700FS | 700FS-700LS60001-02 | Valve's nut to be tightened | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23569 | 820.10 | 820-10-16 | 700FS | 700FS-700LS60001-03 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23570 | 820.10 | 820-10-16 | 700FS | 700FS-700LS60001-03 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23571 | 820.10 | 820-10-16 | 700FS | 700FS-700LS61001-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23572 | 820.10 | 820-10-16 | 700FS | 700FS-700LS61001-02 | Masking tape to be removed | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23573 | 820.10 | 820-10-16 | 700FS | 700FS-700LS61001-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23574 | 820.10 | 820-10-16 | 700FS | 700FS-700LS61001-02 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23575 | 820.10 | 820-10-16 | 700FS | 700FS-900LS01104-01 | Insulation fastening strip to be repaired | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23576 | 820.10 | 820-10-16 | 700FS | 700FS-900LS01104-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23577 | 820.10 | 820-10-16 | 700FS | 700FS-900LS01104-01 | Valve body paiting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23578 | 820.10 | 820-10-16 | 200PR2 | 200PR2-900LS00103-01 | Earthing (grounding) wire has been cut out. To be verify, | C | EL | HEC EL Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-05-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23579 | 820.10 | 820-10-16 | 200PR2 | 200PR2-900LS00103-01 | Insulation missing (the pipeline in clash with scaffolding) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23580 | 820.10 | 820-10-16 | 200PR2 | 200PR2-900LS00103-01 | Support (secondary) rusted | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23581 | 820.10 | 820-10-16 | PDH | 200PR2-900LS00103-01 | Parts of foil to be removed from the pipeline | C | FP | HEC FP Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23582 | 820.10 | 820-10-16 | 200PR2 | 200PR2-900LS00103-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23583 | 820.10 | 820-10-16 | 200PR2 | 200PR2-900LS00103-02 | The support doesn't stick to secondary | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23584 | 820.10 | 820-10-16 | 200PR2 | 200PR2-900LS00103-02 | Support (secondary) touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23585 | 820.10 | 820-10-16 | 200PR2 | 200PR2-900LS00103-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23586 | 820.10 | 820-10-16 | 200PR2 | 200PR2-900LS00103-02 | Masking tape to be removed | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23587 | 820.10 | 820-10-16 | 200PR2 | 200PR2-700LS00105-01 | Visor bolts to be replaced (ss) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23588 | 820.10 | 820-10-16 | 200PR2 | 200PR2-700LS00105-01 | Visors to be cleaned | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23589 | 820.10 | 820-10-16 | 200PR2 | 200PR2-700LS00105-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23590 | 820.10 | 820-10-16 | 300PR | 300PR-300LC00509-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23591 | 820.10 | 820-10-16 | 300PR | 300PR-300LS00509-01 | Wheel touch up painting | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23592 | 820.10 | 820-10-16 | 300PR | 300PR-300LS00509-01 | Secondary touch up painting | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23593 | 820.10 | 820-10-16 | 300PR | 300PR-300LS00509-01 | Masking tape to be removed from tag plate | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23594 | 820.10 | 820-10-16 | 300PR | 300PR-300LS90102-01 | Additional protective cover (on the ground) to be welded | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 |  | Walkdown | [8 empty] | RFC/RFSU
. | 23595 | 820.10 | 820-10-16 | 300PR | 300PR-300LS90102-01 | Wheel touch up painting | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23596 | 820.10 | 820-10-16 | 300PR | 300PR-300LS90102-01 | Masking tape to be removed from tag plate | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23597 | 820.10 | 820-10-16 | 300PR | 300PR-300LS90102-01 | 8-figure tail closed (please check the drawing) | C | COMM | HEC COMM | Mr. Damian Sejnowski | 2022-12-29 |  | Walkdown | [8 empty] | RFC/RFSU
. | 23598 | 820.10 | 820-10-16 | 300PR | 300PR-300LS90102-01 | 8-figure tail rusted | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23599 | 820.10 | 820-10-16 | 300PR | 300PR-300LS90102-01 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23600 | 820.10 | 820-10-16 | 300PR | 300PR-300LS90102-02 | Valve body touch up painting | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23601 | 820.10 | 820-10-16 | 300PR | 300PR-300LS90102-03 | Heating wite connection missing | C | EL | HEC EL Construction | Mr. Damian Sejnowski | 2022-12-29 |  | Walkdown | [8 empty] | RFC/RFSU
. | 23602 | 820.10 | 820-10-16 | 300PR | 300PR-300MC00510-01 | Wheel touch up painting | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23603 | 820.10 | 820-10-16 | 300PR | 300PR-300MC00510-01 | Masking tape to be removed | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23604 | 820.10 | 820-10-16 | 300PR | 300PR-300MC00510-01 | Insulation missing (near flange) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23605 | 820.10 | 820-10-16 | 300PR | 300PR-300MC00510-01 | Insulation fastening strip to be shortened (cut out) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23606 | 820.10 | 820-10-16 | 300PR | 300PR-900LS01201-01 | Wheel touch up painting | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23607 | 820.10 | 820-10-16 | 300PR | 300PR-900LS01201-01 | Masking tape to be removed | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23608 | 820.10 | 820-10-16 | 300PR | 300PR-900LS01201-01 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-03-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23610 | 820.10 | 820-10-16 | 200PR1 | 200PR1-200MC61001-01 | Support touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23611 | 820.10 | 820-10-16 | 200FS3 | 200FS3-200LS60099-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23612 | 820.10 | 820-10-16 | 200FS3 | 200FS3-200LS60099-02 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23613 | 820.10 | 820-10-16 | 200FS3 | 200FS3-200LS60099-03 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23614 | 820.10 | 820-10-16 | 200FS3 | 200FS3-200LS60099-04 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23615 | 820.10 | 820-10-16 | 200FS3 | 200FS3-200LS60099-04 | Part of the pipie rusted, to eb painted | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-02-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23616 | 820.10 | 820-10-16 | 200FS3 | 200FS3-200LS60099-05 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23617 | 820.10 | 820-10-16 | 200FS3 | 200FS3-200LS60100-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23618 | 820.10 | 820-10-16 | 200FS3 | 200FS3-200LS60100-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23619 | 820.10 | 820-10-16 | 200FS3 | 200FS3-200LS60102-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-29 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23620 | 820.10 | 820-10-16 | 200PR1 | 200PR1-200LS61005-01 | Support doesn't stick to secondary | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-30 | 2023-02-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23621 | 820.10 | 820-10-16 | 200PR1 | 200PR1-200LS61005-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-30 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23622 | 820.10 | 820-10-16 | 200PR1 | 200PR1-200LS61005-01 | Wheel touch up painting | C | PI | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-30 | 2023-02-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23623 | 820.10 | 820-10-16 | 200PR1 | 200PR1-200LS61006-01 | Wheel touch up painting | C | PI | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-30 | 2023-02-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23624 | 820.10 | 820-10-16 | 200PR1 | 200PR1-200LS61012-01 | Masking tape to be removed (valve) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-30 | 2023-02-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23625 | 820.10 | 820-10-16 | 200PR1 | 200PR1-200LS61012-01 | Wheel touch up painting | C | PI | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-30 | 2023-02-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23626 | 820.10 | 820-10-16 | 200PR1 | 200PR1-200LS61012-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23627 | 820.10 | 820-10-16 | 200PR1 | 200PR1-200LS61013-01 | Support with the part of pipeline corroded (lack of paint after grinding) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-02-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23628 | 820.10 | 820-10-16 | 200PR1 | 200PR1-200LS61013-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23629 | 820.10 | 820-10-16 | 200PR1 | 200PR1-200LS61013-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23630 | 820.10 | 820-10-16 | 200PR1 | 200PR1-200LS61013-01 | Shoe support rusted | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-02-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23631 | 820.10 | 820-10-16 | 200PR1 | 200PR1-200LS61013-01 | An elbow corroded | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-02-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23632 | 820.10 | 820-10-16 | 200PR1 | 200PR1-900LS00103-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23633 | 820.10 | 820-10-16 | 200PR1 | 200PR1-900LS00103-02 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23634 | 820.10 | 820-10-16 | 200PR1 | 200PR1-900LS00103-02 | Masking tape to be removed | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23635 | 820.10 | 820-10-16 | 200PR1 | 200PR1-900LS00103-13 | Masking tape to be removed | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23636 | 820.10 | 820-10-16 | 200PR1 | 200PR1-900LS00104-01 | Wheel touch up painting | C | PI | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-02-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23637 | 820.10 | 820-10-16 | 200PR1 | 200PR1-900LS00104-01 | Masking tape to be removed | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-02-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23638 | 820.10 | 820-10-16 | 200PR1 | 200PR1-900LS00104-01 | Valve body touch up painting | C | PI | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-02-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23639 | 820.10 | 820-10-16 | 200PR1 | 200PR1-900LS01201-01 | Foil to be removed | C | FP | HEC FP Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-02-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23640 | 820.10 | 820-10-16 | 200PR3 | 200PR3-200LS61014-01 | Pipeline touch up painting | C | PI | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-02-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23641 | 820.10 | 820-10-16 | 200PR3 | 200PR3-200LS61014-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23642 | 820.10 | 820-10-16 | 200PR3 | 200PR3-200LS61014-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23643 | 820.10 | 820-10-16 | 200PR3 | 200PR3-900LS00104-01 | Part of insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23644 | 820.10 | 820-10-16 | 600PS | 600PS-600LS00101-01 | Visors to be cleaned | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2022-12-31 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23645 | 820.10 | 820-10-16 | 600PS | 600PS-600LS00101-01 | Visor bolts rusted, to be replaced (ss) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23646 | 820.10 | 820-10-16 | 600PS | 600PS-600LS00101-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23647 | 820.10 | 820-10-16 | 600PS | 600PS-600LS00101-01 | 8-figure tail rusted | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23648 | 820.10 | 820-10-16 | 600PS | 600PS-600LS00102-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23649 | 820.10 | 820-10-16 | 600PS | 600PS-600LS00102-02 | Visor bolts rusted, to be replaced (ss) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23650 | 820.10 | 820-10-16 | 600PS | 600PS-600LS00102-02 | Whell touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23651 | 820.10 | 820-10-16 | 600PS | 600PS-600LS00102-03 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23652 | 820.10 | 820-10-16 | 600PS | 600PS-600LS00102-03 | Visor bolts rusted, to be replaced (ss) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23653 | 820.10 | 820-10-16 | 600PS | 600PS-600LS00102-03 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23654 | 820.10 | 820-10-16 | 600PS | 600PS-600LS00102-03 | Masking tape to be removed from tag plate | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23655 | 820.10 | 820-10-16 | 600PS | 600PS-600LS00102-04 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23656 | 820.10 | 820-10-16 | 600PS | 600PS-600LS00102-04 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23657 | 820.10 | 820-10-16 | 600PS | 600PS-600LS60002-02 | Ending of the insulation strip to be shortened (cut out) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23658 | 820.10 | 820-10-16 | 600PS | 600PS-600LS60002-02 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23659 | 820.10 | 820-10-16 | 600PS | 600PS-600LS60002-03 | Ending of the insulation strip to be shortened (cut out) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23660 | 820.10 | 820-10-16 | 600PS | 600PS-600LS60002-03 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23661 | 820.10 | 820-10-16 | 600PS | 600PS-600LS60006-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23662 | 820.10 | 820-10-16 | 600PS | 600PS-600LS60006-02 | Support touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23663 | 820.10 | 820-10-16 | 600PS | 600PS-600LS60008-02 | Wrong flow direction of the line drain trap (orientation to be verified) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-02-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23664 | 820.10 | 820-10-16 | 600PS | 600PS-600LS60008-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23665 | 820.10 | 820-10-16 | 600PS | 600PS-600LS60011-02 | Valve body touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23666 | 820.10 | 820-10-16 | 600PS | 600PS-600LS60011-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23667 | 820.10 | 820-10-16 | 600PS | 600PS-600LS60011-03 | Masking tape to be removed | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23668 | 820.10 | 820-10-16 | 600PS | 600PS-600LS60011-03 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23669 | 820.10 | 820-10-16 | 600PS | 600PS-600LS60011-03 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23670 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61001-02 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23671 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61001-02 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23672 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61001-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23673 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61002-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23674 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61002-02 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23675 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61004-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23676 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61004-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23677 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61004-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23678 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61004-02 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23679 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61005-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23680 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61005-02 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23681 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61006-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23682 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61006-02 | Masking tape to be removed | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23683 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61007-01 | Support not indicated in drawing | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-02-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23684 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61008-01 | Support not indicated in drawing | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-02-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23685 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61008-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23686 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61009-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23687 | 820.10 | 820-10-16 | 600PS | 600PS-600LS61009-01 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23688 | 820.10 | 820-10-16 | 600PS | 600PS-900LS00104-01 | Pipeline goes three times upwards. Drawing to be verified. | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-02-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23689 | 820.10 | 820-10-16 | 600PS | 600PS-900LS00104-03 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23690 | 820.10 | 820-10-16 | 600PS | 600PS-900LS00104-03 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23691 | 820.10 | 820-10-16 | 600PS | 600PS-900LS00104-04 | Pipeline goes three times upwards. Drawing to be verified. | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-02-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23692 | 820.10 | 820-10-16 | 600PS | 600PS-900LS00104-05 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23693 | 820.10 | 820-10-16 | 600PS | 600PS-900LS00104-05 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23694 | 820.10 | 820-10-16 | 600PS | 600PR-900LS00104-01 | Visor bolts rusted, to be replaced (ss) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-02-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23695 | 820.10 | 820-10-16 | 600PR | 600PR-900LS00104-01 | Valve's wheel broken, to be replaced | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23696 | 820.10 | 820-10-16 | 600PR | 600PR-900LS00104-01 | Wrong SHT number. Component's 21 connection should be indicated as SHT: 01 | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-02-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23697 | 820.10 | 820-10-16 | 600PR | 600PR-900LS00104-02 | Masking tape to be removed | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23698 | 820.10 | 820-10-16 | 600PR | 600PR-900LS00104-04 | Masking tape to be removed | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-02 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23699 | 820.10 | 820-10-16 | 600PS | 600PS-610LS00104-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23700 | 820.10 | 820-10-16 | 600PS | 600PS-610LS60001-01 | Painting tape to be removed from insulation | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-01-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23701 | 820.10 | 820-10-16 | 600PS | 600PS-610LS60001-01 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23702 | 820.10 | 820-10-16 | 600PS | 600PS-610LS60001-01 | Masking tape to be moved from tag plate | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23703 | 820.10 | 820-10-16 | 600PS | 600PS-610LS60001-02 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23704 | 820.10 | 820-10-16 | 600PS | 600PS-610LS60001-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23705 | 820.10 | 820-10-16 | 600PS | 600PS-610LS60002-02 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23706 | 820.10 | 820-10-16 | 600PS | 600PS-610LS60002-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23707 | 820.10 | 820-10-16 | 600PS | 600PS-610LS61001-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23708 | 820.10 | 820-10-16 | 600PS | 600PS-610LS61001-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23709 | 820.10 | 820-10-16 | 600PS | 600PS-610LS61001-02 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23710 | 820.10 | 820-10-16 | 600PS | 600PS-610LS61002-01 | Painting tape to be removed from insulation | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23711 | 820.10 | 820-10-16 | 600PS | 600PS-610LS61002-02 | Painting tape to be removed from insulation | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23712 | 820.10 | 820-10-16 | 600PS | 600PS-610LS61002-02 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-02-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23713 | 820.10 | 820-10-16 | 600PS | 600PS-610LS61002-02 | Masking tape to be removed | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23714 | 820.10 | 820-10-16 | 830AS | 830AS-900LS00104-01 | Insulation fastening strip to be fasted or removed | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23715 | 820.10 | 820-10-16 | 830AS | 830AS-900LS00104-01 | Foil to be removed from the pipeline | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-02-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23716 | 820.10 | 820-10-16 | 830AS | 830AS-830LS60001-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23717 | 820.10 | 820-10-16 | 830AS | 830AS-830LS60001-02 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23718 | 820.10 | 820-10-16 | 830AS | 830AS-830LS60001-03 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23719 | 820.10 | 820-10-16 | 820BF | 820BF-900LS00103-01 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-03 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23720 | 820.10 | 820-10-16 | 820BF | 820BF-820LS60005-01 | Handle touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23721 | 820.10 | 820-10-16 | 820BF | 820BF-820LS60005-01 | Incomplete insulation | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23722 | 820.10 | 820-10-16 | 820BF | 820BF-820LS60005-02 | Incomplete insulation | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23723 | 820.10 | 820-10-16 | 820BF | 820BF-820LS60005-02 | Pipeline to be stabilized (it's shaking) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23724 | 820.10 | 820-10-16 | 820BF | 820BF-820LS60011-01 | Drawing to be verified and updated (the pipeline doesn't go down at a particular place on the drawing | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23725 | 820.10 | 820-10-16 | 820BF | 820BF-820LS60011-01 | Insulation plug to be installed (near flange) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23726 | 820.10 | 820-10-16 | 820BF | 820BF-820LS60012-01 | Insulation missing | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23727 | 820.10 | 820-10-16 | 820BF | 820BF-820LS60012-01 | Insulation fastening strip to be shortened (cut out) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23728 | 820.10 | 820-10-16 | 820BF | 820BF-820LS60012-01 | Support not indicated in drawing | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23729 | 820.10 | 820-10-16 | 860CT | 860CT-860LS60001-03 | Incomplete insulation (plugs near flanges) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23730 | 820.10 | 820-10-16 | 860CT | 860CT-860LS60002-01 | Handle touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23731 | 820.10 | 820-10-16 | 860CT | 860CT-860LS60002-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23732 | 820.10 | 820-10-16 | 860CT | 860CT-860LS60004-01 | Flange contaminated by rust | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23733 | 820.10 | 820-10-16 | 860CT | 860CT-860LS60004-01 | Handle touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23734 | 820.10 | 820-10-16 | 860CT | 860CT-860LS60004-02 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23735 | 820.10 | 820-10-16 | 860CT | 860CT-860LS60005-01 | Masking tape to be removed | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23736 | 820.10 | 820-10-16 | 860CT | 860CT-860LS61001-01 | Incomplete insulation | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23737 | 820.10 | 820-10-16 | 860CT | 860CT-860LS61001-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23738 | 820.10 | 820-10-16 | 810PR | 810PR-820AV01102-01 | Valve's nut rusted | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23739 | 820.10 | 820-10-16 | 810PR | 810PR-820AV01102-01 | Wheel touch up painting | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23740 | 820.10 | 820-10-16 | 810PR | 810PR-820AV07102-01 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23741 | 820.10 | 820-10-16 | 810PR | 810PR-820AV07102-01 | Rust contamination in general | C | PA | HEC PA Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23742 | 820.10 | 820-10-16 | 810PR | 810PR-810LS61001-01 | Insulation foil to be taped (near flange) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23743 | 820.10 | 820-10-16 | 810PR | 810PR-810LS61001-01 | Insulation plug missing (near flange) | C | IN | HEC IN Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23744 | 820.10 | 820-10-16 | 810PR | 810PR-810LS61002-01 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23745 | 820.10 | 820-10-16 | 810PR | 810PR-810LS61003-01 | Rusted bolts (flange) | C | PI | HEC PI Construction | Mr. Damian Sejnowski | 2023-01-04 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23870 | 820.10 | 820-10-18 | 820-B0001-W01 |  | Proximitor tag no. incompatible with documentation (V-KWB-M10-820-B0001-00002) | C | CI | HEC CI Construction | Mr. Adrian Antonowicz | 2023-01-04 |  | Walkdown |  |  | 2023-03-02 | Rejected... Wrong Tag Photos attached.. Correct Tags are below |  |  |  |  | RFC/RFSU
. | 23871 | 820.10 | 820-10-18 | 820-B0001-W01 |  | Missing bearing temperature sensors tag no. | C | CI | CW Construction | Mr. Adrian Antonowicz | 2023-01-04 | 2023-04-05 | Walkdown |  |  | 2023-01-21 | Wrong submission | V |  |  |  | RFC/RFSU
. | 23872 | 820.10 | 820-10-24 | 820-P0002A/B |  | Missing lubrication point cap. | C | ME | HEC ME Construction | Mr. Adrian Antonowicz | 2023-01-04 | 2023-04-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23873 | 820.10 | 820-10-24 | 820-P0002A/B |  | Plenty signs of rust. | C | ME | HEC ME Construction | Mr. Adrian Antonowicz | 2023-01-04 | 2023-04-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23874 | 820.10 | 820-10-24 | 820-P0002A/B |  | Piping isolation to be completed. | C | IN | HEC IN Construction | Mr. Adrian Antonowicz | 2023-01-04 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23875 | 820.10 | 820-10-24 | 820-P0002A/B |  | Unreadable tag no. of the proximitor. | C | CI | CW Construction | Mr. Adrian Antonowicz | 2023-01-04 | 2023-05-30 | Walkdown |  |  | 2023-03-20 | All hanging tags are wrong because P&ID it self wrong tags ... after update the P&ID tags need to replace | V |  |  |  | RFC/RFSU
. | 29628 | 820.10 | 820-10-16 | IN_Piping Insulation - 300 | 300PR-LS-2002 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29633 | 820.10 | 820-10-16 | IN_Piping Insulation - AUX | 200PR1-LC-0003 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29634 | 820.10 | 820-10-16 | IN_Piping Insulation - AUX | 200PR1-LS-1002 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29638 | 820.10 | 820-10-16 | IN_Piping Insulation - AUX | 600PR-LS-1001 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29644 | 820.10 | 820-10-14 | IN_Piping Insulation - AUX | 810PR-MS-1004 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29645 | 820.10 | 820-10-10 | IN_Piping Insulation - AUX | 810WT-LO-1005 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29646 | 820.10 | 820-10-10 | IN_Piping Insulation - AUX | 810WT-LO-1006 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29648 | 820.10 | 820-10-18 | IN_Piping Insulation - AUX | 820BFV-NY-1006 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30541 | 820.10 | 820-10-18 | Boiler Pckg | 820-TT-9152. PID 820-00031B | This transmitter is not working properly. | C | CI | HEC CI Construction | Mr. Andrzej Przechrzta | 2023-02-09 |  | PAC | [8 empty] | RFC/RFSU
. | 30542 | 820.10 | 820-10-24 | Boiler Pckg | AT-1002, AT-1003, AT-1001. PID 820-00011 | Ph Oxygen and conductivity measurements of BMW are not being calibrated. Conductivity measurement is not working. | C | CI | HEC CI Construction | Mr. Andrzej Przechrzta | 2023-02-10 | 2023-05-23 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31099 | 820.10 | 820-10-10 | 820-PR-001 | V-MHU-S01-820-PR1B1-00001-0 EGAT-820-PR-001-BLOCK-B-E0025 | Ladder is not bolted to foundation | C | SS | HEC SS Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-03-27 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31100 | 820.10 | 820-10-24 | 820-V0003 | 820-AI-1001 | measurement does not working properly | C | COMM | HEC COMM | Mr. Damian Maciejaszek | 2023-03-17 |  | PAC | [8 empty] | RFC/RFSU
. | 31101 | 820.10 | 820-10-16 | 820-X0002A | 820-TV-1012 | DCS not showing valve as open (it was open 20%) | C | COMM | HEC COMM | Mr. Damian Maciejaszek | 2023-03-17 |  | PAC | [8 empty] | RFC/RFSU
. | 31137 | 820.10 | 820-10-22 | Unit 820 | 820-PRO-PID-00031 | Leakage on phosphate dosing line | C | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2023-03-17 | 2023-05-16 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31299 | 820.10 | 820-10-20 | 820 | 820-B0004 | STTP-9150 is defective, letting a lot of steam go through. | C | ME | HEC ME Construction | Mr. Andrzej Przechrzta | 2023-04-06 |  | PAC | [8 empty] | RFC/RFSU
. | 31368 | 820.10 | 820-10-12 | AUX area top pipe rack Letdown Station | EGAT-HEC-820-PRO-PID-00081 | Leakage - probably from valve flange (hard to investigate under insulation). Valve on steam letdown station HS-LS 820-on PV-1007A | C | PI | HEC PI Construction | Mr. Kamil Wiśniewski | 2023-04-17 |  | PAC | [8 empty] | RFC/RFSU
. | 31369 | 820.10 | 820-10-12 | AUX area top pipe rack Letdown Station | EGAT-HEC-820-PRO-PID-00081 | Leakage from impulse line on letdown station 820-PT-1007B | C | PI | HEC PI Construction | Mr. Kamil Wiśniewski | 2023-04-17 |  | PAC | [8 empty] | RFC/RFSU
. | 31374 | 820.10 | 820-10-24 | BFW Pumps | EGAT-HEC-820-PRO-PID-00021 | 820-SN-0211 - sampling drain blocked | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-04-11 | 2023-05-02 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31376 | 820.10 | 820-10-18 |  | EGAT-HEC-820-PRO-PID-00031B | Stream trap (820-STTP-9150) downstream of desuperheater (820-B0001-X03) is damaged and it is not workin properly. A lot of steam with high velocity is coming out from the drain. The concrete under the outlet of the drain is also damaged (there is a hole in the concrete) | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-04-11 |  | PAC | [8 empty] | RFC/RFSU
. | 31377 | 820.10 | 820-10-26 | 820-X0007 | EGAT-HEC-820-PRO-PID-00041 | 820-X0007-P01A/B - pumps doesn't work (not pumping) | C | ME | HEC ME Construction | Mr. Damian Maciejaszek | 2023-04-14 | 2023-04-20 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31383 | 820.10 | 820-10-24 | BFW Pumps | EGAT-HEC-820-PRO-PID-00021 | 820-FT-1003/1004 is not working correctly | C | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2023-04-14 |  | PAC | [8 empty] | RFC/RFSU
. | 31750 | 820.10 | 820-10-18 | 820-B0001 |  | Boiler controllers (air and FG) are not properly tuned and it cause boiler trip during load increase (trip occurs when the load was changed from 65% to 66% | C | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2023-05-06 |  | PAC | [8 empty] | RFC/RFSU
. | 31751 | 820.10 | 820-10-18 | 820-B0001 | EGAT-HEC-820-PRO-PID-00031B | 820-FI-9153 has a high alarm (51000 kg/h) whereas there is no alarm in the instrument index. | C | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2023-05-06 | 2023-06-12 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31752 | 820.10 | 820-10-18 | 820-B0001 | EGAT-HEC-820-PRO-PID-00031B | The temperature transmitter (820-TT-9152) is not working (is showing NaN) | C | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2023-05-06 | 2023-06-02 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31753 | 820.10 | 820-10-18 | 820-B0001 | EGAT-HEC-820-PRO-PID-00031H | Lack of possibility taking HP steam sample (820-SN-0903). Even if the manual valve is fully opened, there is no flow. | C | COMM | HEC COMM | Mr. Damian Maciejaszek | 2023-05-06 |  | PAC | [8 empty] | RFC/RFSU
. | 31754 | 820.10 | 820-10-18 | 820-B0001 | EGAT-HEC-820-PRO-PID-00031C | FD fan motor winding temperature (820-TT-9183) is not working | C | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2023-05-06 |  | PAC | [8 empty] | RFC/RFSU
. | 31755 | 820.10 | 820-10-18 | 820-B0001 | EGAT-HEC-820-PRO-PID-00031 | Boiler load has been limited to 70% (820-PIC-1007) without any information | C | COMM | HEC COMM | Mr. Damian Maciejaszek | 2023-05-06 |  | PAC | [8 empty] | RFC/RFSU
. | 31756 | 820.10 | 820-10-26 | 820-B0001 | EGAT-HEC-820-PRO-PID-00041 | A lot of solid white substance in the oxygen scavenger injection tank cause plugging of pipes and dosing pumps | C | COMM | HEC COMM | Mr. Damian Maciejaszek | 2023-05-06 |  | PAC | [8 empty] | RFC/RFSU
. | 31784 | 820.10 | 820-10-16 | 820-X0002B | 820-X0002B | water leak | C | PI | HEC PI Construction | Mr. Jarosław Pykosz | 2023-05-07 |  | PAC | [8 empty] | RFC/RFSU
. | 31786 | 820.10 | 820-10-18 | 820-3/4"-NY-91654 | 820-3/4"-NY-91654 Boiler Economizer drain | Steam leak prapably valve is not fully closed | C | PI | HEC PI Construction | Mr. Jarosław Pykosz | 2023-05-07 |  | PAC | [8 empty] | RFC/RFSU
. | 31857 | 820.10 | 820-10-10 | unit 820 |  | Insulation on lube oil skid steam turbine to be provided | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2023-05-11 |  | PAC | [8 empty] | RFC/RFSU
. | 31881 | 820.10 | 820-10-12 | HS-MS letdown station | EGAT-HEC-820-PRO-PID-00072 | Demaged insulation before pipe size change from 10 inch to 6 inch - photo attached. | C | IN | HEC IN Construction | Ms. Anna Mazur | 2023-05-11 |  | PAC | [8 empty] | RFC/RFSU
. | 31882 | 820.10 | 820-10-18 | HP Boiler | EGAT-HEC-820-PRO-PID-00031B | Leak on HP Boiler economizer | C | PI | HEC PI Construction | Mr. Piotr Śliwa | 2023-05-11 |  | PAC | [8 empty] | RFC/RFSU
. | 31980 | 820.10 | 820-10-10 | AUX | 820-B0004 | Damaged internal cables (820-B0004 Steam Turbine Power Generator) in the neutral terminal box should be replaced with new ones and the structural edge should be secured to prevent further damage to the cables. Cables should be replaced by the manufacturer. You should also receive a document from the manufacturer about the receipt of the warranty after replacement. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-05-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32029 | 820.10 | 820-10-16 | LS line | TAG nr in Remark | Steam trap is broken. Steam is coming out from this trap | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-05-25 |  | PAC | [8 empty] | RFC/RFSU
. | 32038 | 820.10 | 820-10-18 | 820-B0001-E01 - Boiler's economizer | PID: 820-00031A Line No: 820-3/4"-NY-91654-MS-13-1-ET(40) | Hand valve on drain line is broken. It stuck in open position ane the high pressure, high temperature water is coming out all the time. Concrete under the drain pipe outlet is broken. | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-05-25 |  | PAC | [8 empty] | RFC/RFSU
. | 32039 | 820.10 | 820-10-26 | 820-X0007 - oxygen scavenger dosing skid | PID:820-00041 | Design issue. Range of actual PGs(820-PG-9307 & 820-PG-9308) is wrong. ? Now the unit of pressure gauge is MPa what cause that PGs will indicate almost 0 MPa all the time and we are not able to see changes (even if it hapening, eg. suction filter plugging)). Gauges need to be changed to one with a unit like bar or even kPa. | C | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2023-05-25 |  | PAC | [8 empty] | RFC/RFSU
. | 32040 | 820.10 | 820-10-28 | 820-X0006 - alkalinizing amine dosing skid | PID:820-00041 | Design issue. Range of actual PGs(820-PG-9207 & 820-PG-9208) is wrong. ? Now the unit of pressure gauge is MPa what cause that PGs will indicate almost 0 MPa all the time and we are not able to see changes (even if it hapening, eg. suction filter plugging)). Gauges need to be changed to one with a unit like bar or even kPa. | C | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2023-05-25 |  | PAC | [8 empty] | RFC/RFSU
. | 32041 | 820.10 | 820-10-22 | 820-X0001 - phosphate injection skid | PID: 820-00051 | Design issue. Range of actual PGs(820-PG-9107 & 820-PG-9108) is wrong. ? Now the unit of pressure gauge is MPa what cause that PGs will indicate almost 0 MPa all the time and we are not able to see changes (even if it hapening, eg. suction filter plugging)). Gauges need to be changed to one with a unit like bar or even kPa. | C | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2023-05-25 |  | PAC | [8 empty] | RFC/RFSU
. | 32045 | 820.10 | 820-10-26 | 820-X0006 - oxygen scavenger dosing skid | PID: 820-00041 | Oxygen scavenger dosing pumps (820-X0006-P01A/B) are not pumping the chemical | C | ME | HEC ME Construction | Mr. Damian Maciejaszek | 2023-05-25 |  | PAC | [8 empty] | RFC/RFSU
. | 32130 | 820.10 | 820-10-18 | unit 820 | 820-B0001 | Improper slope on drain line 820HS-91553-02 and broken / wet insulation | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-06-01 |  | PAC | [8 empty] | RFC/RFSU
. | 32309 | 820.10 | 820-10-18 | 820 | 820-10"-HS-91552 | Burned insulation on top of the boiler (pressure signal from high pressure steam to PT) | C | ME | HEC ME Construction | Mr. Andrzej Przechrzta | 2023-06-09 |  | PAC | [8 empty] | RFC/RFSU
. | 32310 | 820.10 | 820-10-18 | 820 | 820-3/4"-AV-91640 | Vents from superheaters leaking. | C | ME | HEC ME Construction | Mr. Andrzej Przechrzta | 2023-06-09 |  | PAC | [8 empty] | RFC/RFSU
. | 32311 | 820.10 | 820-10-18 | 830 | 830-3/4"-Y-TUBINGLINE | Automatic drain from compressor A leak | C | ME | HEC ME Construction | Mr. Andrzej Przechrzta | 2023-06-09 |  | PAC | [8 empty] | RFC/RFSU
. | 32312 | 820.10 | 820-10-18 | 820 | 820-6"-BW-91504-MS | Leak from outlet pipe from economizer | C | ME | HEC ME Construction | Mr. Andrzej Przechrzta | 2023-06-09 | 2023-06-26 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 32360 | 820.10 | 820-10-18 | 820-B0001 | PID: 820-00031C 820-PG-9161 | PG seens to be damaged. Lack of liquid inside pressure gauge | C | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2023-06-13 |  | PAC | [8 empty] | RFC/RFSU
. | 32361 | 820.10 | 820-10-18 | 820-B0001 | 80-PT-9151 | Leak from transmitter's impulse line. Insulation is wet and damaged | C | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2023-06-13 |  | PAC | [8 empty] | RFC/RFSU
. | EGAT-PMC-000-QAC-NCR-ME139.01 | 820.10 | 820-10-10 | 820-B0004 |  | The Contrator is requested to provide revised detail documentation for Steam Turbine Shelter 820-SHT-SH-300 including changes related to crane service platform dismantling. | C | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2023-05-25 | [10 empty] | Construction
. | EGAT-PMC-000-QAC-NCR-ME139.02 | 820.10 | 820-10-10 | 820-B0004 |  | The Contractor shall provide plan of handling and transportation for Steam Turbine Generator maintenance purposes (how the Generator will be removed from site, including all details of removable roof including dimensioning, which elements are intended for disassembly, type and capacity of crane required for such operation, positioning of the crane and truck, taking into account all space limitations, obstacles and current plot-plan. | C | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2023-05-25 | [10 empty] | Construction
. | EGAT-RFI-CI-CW-00340.01 | 820.10 | 820-10-18 | 820 Steam Boiler Area | Instrument Installation | Permanent Tag Missing | C | CI | HEC CI Construction | J.W.JEONG | 2021-10-21 | 2022-04-11 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-00340.02 | 820.10 | 820-10-18 | 820 Steam Boiler Area | Instrument Installation | Permanent Tag Missing | C | CI | HEC CI Construction | J.W.JEONG | 2021-10-21 | 2022-04-11 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-00367.01 | 820.10 | 820-10-18 | Steam Boiler | 820-PT-9182A/B/C | Additional Support | C | CI | HEC CI Construction | Ariel Lazaro | 2021-11-02 | 2021-11-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-00496.01 | 820.10 | 820-10-14 | 820 AUXILLARY AREA | 820-PV-0722, 820-PV-0732, 820-PV-0733, 820-PV-1006, 820-TV-0723820-TV-0731A, 820-TV-0731B | PUNCHING PLATE (RACEWAY TUBE)NEED TO BE CLEAN GOING TO EACH VALVE | B | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-12-15 | 2023-01-17 | Construction |  |  | 2023-01-16 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-00496.02 | 820.10 | 820-10-14 | 820 AUXILLARY AREA | 820-PV-1007A, 820-PV-1007B, 820-TV-1008, 820-TV-1011, 820-TV-1012 | PUNCHING PLATE (RACEWAY TUBE)NEED TO BE CLEAN GOING TO EACH VALVE | B | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-12-14 | 2023-01-17 | Construction |  |  | 2023-01-16 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-00830.01 | 820.10 | 820-10-18 | Steam Boiler | Impulse tubing | Pressure test to be perform | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-02-23 | 2022-12-08 | Construction |  |  | 2022-12-02 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01215.01 | 820.10 | 820-10-26 | Spent Caustic | Duct tray | Provide additional support for duct tray (810-TT-1018) portion | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-27 | 2022-07-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01299.01 | 820.10 | 820-10-16 | AUX. AREA | 810-TV-1002 | Missing hanging tag to be provided | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-17 | 2022-06-27 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01309.01 | 820.10 | 820-10-16 | AUX Area | Junction Panel | Touch up paint to be done in Local PDP | C | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-05-18 | 2022-11-25 | Construction |  |  | 2022-11-25 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01393.01 | 820.10 | 820-10-20 | Aux Area | Instrument Installation | Torquing to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-30 | 2022-09-16 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01401.01 | 820.10 | 820-10-14 | 820 PR-01 | EGAT-HEC-600-INC-DLP-00001_6 | Stud bolt torquing to be done | B | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-03 | 2022-07-29 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01402.01 | 820.10 | 820-10-14 | 820 PR-01 | EGAT-HEC-600-INC-DLP-00001_6 | Stud bolt torquing to be done | B | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-03 | 2022-07-29 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01442.01 | 820.10 | 820-10-16 | Steam Boiler | EGAT-HEC-870-PRO-PID-00021 | Torquing to be done | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-06 | 2022-10-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01483.01 | 820.10 | 820-10-18 | Steam boiler | Flow transmitter (4ea) | Sunshade to be installed | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-06 | 2022-11-22 | Construction | 2022-11-17 | 2022-11-22 | 2022-11-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01486.01 | 820.10 | 820-10-18 | Steam boiler | Instrument Installation | Torquing to be done | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-06 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01486.02 | 820.10 | 820-10-18 | Steam boiler | Temperature transmitter | Transmitter must be properly tighten | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-06 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01486.03 | 820.10 | 820-10-18 | Steam boiler | Stud Bolt | Bolt corroded must be clean | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-06 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01513.01 | 820.10 | 820-10-18 | AUX AREA | 9 EA | TORQUING TO BE DONE | C | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-06-09 | 2023-04-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01515.01 | 820.10 | 820-10-18 | Steam Boiler | AUX Area | Torquing to be done | C | CI | HEC CI Construction | Ariel Lazaro | 2022-06-09 | 2023-05-02 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01516.01 | 820.10 | 820-10-18 | Steam Boiler | AUX Area | Torquing to be done | C | CI | HEC CI Construction | Ariel Lazaro | 2022-06-09 | 2023-05-02 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01561.01 | 820.10 | 820-10-16 | Auxiliary | 840-TI-1003 | Local indicator to be verify | C | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-11-10 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01741.01 | 820.10 | 820-10-16 | 870 Fuel Gas | 870-FV-4501, 4511 | Site calibration to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-07-11 | 2022-08-18 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01741.02 | 820.10 | 820-10-16 | 870 Fuel Gas | 870-FV-4501, 4511 | Bolt should be completed | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-07-11 | 2022-09-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01832.01 | 820.10 | 820-10-18 | Steam boiler | Gauges | Torquing to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-07-18 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01878.01 | 820.10 | 820-10-18 | Steam Boiler | Instrument Installation | Torquing to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-07-21 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01878.02 | 820.10 | 820-10-18 | Steam Boiler | Instrument Installation | Calibration of FT need to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-07-21 | 2022-12-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01955.01 | 820.10 | 820-10-20 | AUX AREA | 820 V0002 | TORQUING TO BE DONE | C | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-07-27 | 2023-04-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01955.02 | 820.10 | 820-10-20 | Aux Area | 820-V0002 | Hook up Drawing to be Revised for Stud Bolt length | C | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-07-27 | 2023-05-01 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01955.03 | 820.10 | 820-10-20 | Aux Area | 820-LG-M-1002 | Missing hanging tag | C | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-07-27 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01997.01 | 820.10 | 820-10-16 | Auxiliary | 810-AS-001 | Actual elevation for sub-header not as per drawing | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-07-30 | 2022-12-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01997.02 | 820.10 | 820-10-16 | Auxiliary | 810-AS-001, 840-AS-001 | Provide identification tag for sub-header | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-07-30 | 2022-09-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02291.01 | 820.10 | 820-10-20 | 820 Piperack 1 | 870-JP-052 | Spare hole ATEX blind plug to be provide | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-25 | 2022-09-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02294.01 | 820.10 | 820-10-16 | 820 Auxiliary | 870-FT-4501, 4511 | 1/4 SS tube for drain to be provide | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-25 | 2022-11-10 | Construction |  |  | 2022-11-11 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02305.01 | 820.10 | 820-10-24 | 820 Auxiliary | 820-FT-1008, 1009 | 1/4 SS tube for drain to be provide | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-25 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02305.02 | 820.10 | 820-10-24 | 820 Auxiliary | 820-TT-1003, 1006 | Torquing to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-25 | 2022-09-17 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02306.01 | 820.10 | 820-10-24 | 820 Auxiliary | 820-FT-1003, 1004, 820-PT-1002, 1003, 1004A/B | 1/4 SS tube for drain to be provide | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-25 | 2022-11-14 | Construction |  |  | 2022-11-11 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02306.02 | 820.10 | 820-10-24 | 820 Auxiliary | 820-FT-1003, 1004, 820-PT-1002, 1003, 1004A/B | Earthing to be provide | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-25 | 2022-10-06 | Construction |  |  | 2022-11-10 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02420.01 | 820.10 | 820-10-26 | Boiler feed water | 820-FT-1002 | 1/4 SS tube for drain to be provide | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-05 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02421.01 | 820.10 | 820-10-16 | Raw water treatment | 810-PT-1033 | Enclosure box rubber to be properly fix | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-05 | 2022-09-13 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02463.01 | 820.10 | 820-10-14 | Auxiliary | Instrument Installation (5ea) | SS hanging tag to be provide | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-10-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02463.02 | 820.10 | 820-10-14 | Auxiliary | 900-FT-1010A/B, 900-FT-1011A/B, 900-PT-1008 | Thermostat should be properly fix | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-11-16 | Construction | 2022-11-10 |  | 2022-11-10 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02463.03 | 820.10 | 820-10-14 | Auxiliary | 900-FT-1011A,1011B,1010B | Enclosure lock damage need to be replace | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-09-17 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02482.01 | 820.10 | 820-10-18 | Steam Boiler | V-KWB-M10-820-B0001-00063_1 | SS HANGING TAG TO BE PROVIDED (GEN.) | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-08-31 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02482.02 | 820.10 | 820-10-18 | Steam Boiler | V-KWB-M10-820-B0001-00063_1 | THERMOSTAT PROPERLY FIXED (GEN.) | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-08-31 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02482.03 | 820.10 | 820-10-18 | Steam Boiler | V-KWB-M10-820-B0001-00063_1 | ENCLOSURE LOCK (DAMAGE) TO BE REPLACE (GEN.) | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-08-31 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02482.04 | 820.10 | 820-10-18 | Steam Boiler | V-KWB-M10-820-B0001-00063_1 | BLIND PLUG SHOULD BE ATEX (GEN.) | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-08-31 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02482.05 | 820.10 | 820-10-18 | Steam Boiler | V-KWB-M10-820-B0001-00063_1 | 1/4 SS TUBING TO BE INSTALLED (GEN.) | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-08-31 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02482.06 | 820.10 | 820-10-18 | Steam Boiler | V-KWB-M10-820-B0001-00063_1 | SS HANGING TAG TO BE PROVIDED (GEN.) | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-01 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02483.01 | 820.10 | 820-10-18 | Steam Boiler | 820-PT-9151, 9164, 9165A/B/C, 820-TT-9151 | SS hanging tag to be provide | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-11-10 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02483.02 | 820.10 | 820-10-18 | Steam Boiler | 820-PT-9151 | Thermostat should be properly fix | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-11-10 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02483.03 | 820.10 | 820-10-18 | Steam Boiler | 820-PT-9151 | Enclosure lock damage need to be replace | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-09-17 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02483.04 | 820.10 | 820-10-18 | Steam Boiler | 820-PT-9151, 9164, 9165A/B/C | Additional support to be provide | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-11-16 | Construction | 2022-11-12 |  | 2022-11-12 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02483.05 | 820.10 | 820-10-18 | Steam Boiler | 820-TT-9151 | Torquing to be done | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02484.01 | 820.10 | 820-10-18 | Steam Boiler | Instrument Installation (4ea) | SS hanging tag to be provide | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-10-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02484.02 | 820.10 | 820-10-18 | Steam Boiler | 820-LT-9150A,9151A,PDT-9160 | Thermostat should be properly fix | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02484.03 | 820.10 | 820-10-18 | Steam Boiler | 820-TT-9161 | Torquing to be done | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02485.01 | 820.10 | 820-10-18 | Steam Boiler | 820-FT-9152, 820-LT-9150B/C, 820-LT-9151B, 820-PT-9162A/B/C | SS hanging tag to be provide | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-11-10 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02485.02 | 820.10 | 820-10-18 | Steam Boiler | 820-FT-9152, 820-LT-9150B/C, 820-LT-9151B, 820-PT-9162A/B/C | Enclosure clamp damage | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-10-26 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02485.03 | 820.10 | 820-10-18 | Steam Boiler | 820-FT-9152, 820-LT-9150B/C, 820-LT-9151B, 820-PT-9162A/B/C | Thermostat loosed need to be fix | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-11-24 | Construction | 2022-11-18 | 2022-11-21 | 2022-11-18 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02486.01 | 820.10 | 820-10-18 | Steam Boiler | 820-TT-9162 | Torquing to be done | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-09-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02489.01 | 820.10 | 820-10-18 | Steam Boiler | V-KWB-M10-820-B0001-00066_Z0 | 820-JD-532(IS), 820-JD-533(IS), 820-JD-534(IS), TERMINAL STRIP NUMBER 50 TO 60 TO BE INSTALL | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-01 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02489.02 | 820.10 | 820-10-18 | Steam Boiler | V-KWB-M10-820-B0001-00066_Z0 | 820-JS-531, 820-JS-532, 820-JS533, 820-JS-534, TERMINAL STRIP NUMBER 39 TO 40 TO BE INSTALL | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-01 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02510.01 | 820.10 | 820-10-18 | Steam Boiler | On-off valve installation (34ea) | All on-off valve should be properly clean | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-09-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02510.02 | 820.10 | 820-10-18 | Steam Boiler | 820-XV-9173B | Missing sunshade to be provide | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-11-22 | Construction | 2022-11-18 | 2022-11-22 | 2022-11-18 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02546.01 | 820.10 | 820-10-18 | Steam Boiler | Temperature Gauge | 820-TG-9151-9153-9161-9162-9170, Tourquing to be done | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-07 | 2022-09-16 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02547.01 | 820.10 | 820-10-18 | Steam Boiler | Pressure Gauge | 820-PG-9186, 9171 Torquing to be done | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-07 | 2022-09-16 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02547.02 | 820.10 | 820-10-18 | Steam Boiler | Pressure Gauge | 820-PG-9163,9162 Missing hanging tag | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-07 | 2022-09-26 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02548.01 | 820.10 | 820-10-18 | Steam Boiler | 820-LG-9150 | Torquing to be done | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-07 | 2022-09-16 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02579.01 | 820.10 | 820-10-16 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | 1/4 SS Tubing to be isntalled (GEN.) | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02581.01 | 820.10 | 820-10-14 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | 1/4 SS Tubing to be isntalled (GEN.) | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02586.01 | 820.10 | 820-10-12 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | 1/4 SS Tubing to be isntalled (GEN.) | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02587.01 | 820.10 | 820-10-12 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | 1/4 SS Tubing to be isntalled (GEN.) | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02589.01 | 820.10 | 820-10-16 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | 1/4 SS Tubing to be isntalled (GEN.) | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02593.01 | 820.10 | 820-10-14 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | 1/4 SS Tubing to be isntalled (GEN.) | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02594.01 | 820.10 | 820-10-14 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | 1/4 SS Tubing to be isntalled (GEN.) | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02595.01 | 820.10 | 820-10-14 | Boiler feed water | 820-TT-0731A/B | SS Tag to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-10 | Construction |  | closed | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02595.02 | 820.10 | 820-10-14 | Boiler feed water | 820-TT-0731A/B | Bolt and Nut to be changed | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-12-15 | Construction | 2022-11-09 |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02597.01 | 820.10 | 820-10-24 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | 1/4 SS Tubing to be isntalled (GEN.) | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02602.01 | 820.10 | 820-10-14 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | Tapping point SS tag to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-09 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02603.01 | 820.10 | 820-10-14 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | Tapping point SS tag to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02604.01 | 820.10 | 820-10-16 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | Tapping point SS tag to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02604.02 | 820.10 | 820-10-16 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | Additional support to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-16 | Construction | 2022-11-11 |  | 2022-11-11 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02605.01 | 820.10 | 820-10-16 | Boiler feed water | 820-PT-1008A/B/C | Tapping point SS tag to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-10 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02606.01 | 820.10 | 820-10-24 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | Tapping point SS tag to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-22 | Construction | 2022-11-18 | 2022-11-22 | 2022-11-18 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02606.02 | 820.10 | 820-10-24 | Boiler feed water | EGAT-HEC-600-INC-DLP-00001_6 | Bolt Torquing to be done | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-22 | Construction | 2022-11-21 | 2022-11-21 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02607.01 | 820.10 | 820-10-24 | Boiler feed water | 820-PT-1006A/B/C | Tapping point SS tag to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-10 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02607.02 | 820.10 | 820-10-24 | Boiler feed water | 820-PT-1006A/B/C | Bolt Torquing to be done | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-17 | Construction | 2022-11-18 |  | 2022-11-18 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02608.01 | 820.10 | 820-10-14 | Boiler feed water | 820-PT-0713 | Tapping point SS tag to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-10 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02613.01 | 820.10 | 820-10-10 | 820 Pipe Rack 1 | EGAT-HEC-600-INC-DLP-00001_6 | Cable tray entry in platform kick plate to be provided (General) | B | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-08 | 2022-12-01 | Construction |  |  | 2022-12-01 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02646.01 | 820.10 | 820-10-10 | Boiler Feed Water | EGAT-HEC-600-INC-DLP-00001_6 | 1/4 SS Tubing to be isntalled (GEN.) | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-11-22 | Construction | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02655.01 | 820.10 | 820-10-12 | Boiler Feed Water | EGAT-HEC-600-INC-DLP-00001_6 | Tapping point SS tag to be provided | B | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02655.02 | 820.10 | 820-10-12 | Boiler Feed Water | EGAT-HEC-600-INC-DLP-00001_6 | Bolt Torquing to be done | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-06 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02670.01 | 820.10 | 820-10-12 | Boiler Feed Water | EGAT-HEC-600-INC-DLP-00001_6 | Tapping point SS tag to be provided | B | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02670.02 | 820.10 | 820-10-12 | Boiler Feed Water | EGAT-HEC-600-INC-DLP-00001_6 | Tubing for vent to be done | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02677.01 | 820.10 | 820-10-18 | Steam Boiler | 820-FV-9198 | Wrong body name plate tag and hanging tag should be replaced | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-13 | 2022-11-10 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02714.01 | 820.10 | 820-10-14 | 900 AUX AREA | 900-TT-1015 (TAG) | SS Hanging tag to be provided | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-13 | 2022-11-10 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02714.02 | 820.10 | 820-10-14 | 900 AUX AREA | 900-TT-1015 (TAG) | Transmitter hole for mounting bracket plug to be provided | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-13 | 2022-11-14 | Construction |  |  | 2022-11-11 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02735.01 | 820.10 | 820-10-24 | AUX Area | 820-V0003 | Torquing to be done for TG & PG | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-14 | 2022-10-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02735.02 | 820.10 | 820-10-24 | AUX Area | 820-V0003 | Hook up drawing to be revised for stud bolt length | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-14 | 2022-10-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02735.03 | 820.10 | 820-10-24 | AUX Area | 820-V0003 | 2 way valve manifold is missing for PG | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-14 | 2022-10-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02764.01 | 820.10 | 820-10-12 | AUX Area | EGAT-HEC-600-INC-DLP-00001_6 | Torquing to be done for TG & PG | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-14 | 2022-11-15 | Construction |  |  | 2022-11-11 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02764.02 | 820.10 | 820-10-12 | AUX Area | EGAT-HEC-600-INC-DLP-00001_6 | Hook up drawing to be revised for stud bolt length | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-14 | 2022-10-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02764.03 | 820.10 | 820-10-12 | AUX Area | EGAT-HEC-600-INC-DLP-00001_6 | Callibration to be done | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-14 | 2022-12-07 | Construction |  |  | 2022-12-05 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02764.04 | 820.10 | 820-10-12 | AUX Area | EGAT-HEC-600-INC-DLP-00001_6 | Missing hanging tag | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-14 | 2022-10-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02902.01 | 820.10 | 820-10-14 | Aux Area | 900-TG-1007 | Hook up Drawing to be revised for Stud Bolt Length | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-09-21 | 2023-05-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02936.01 | 820.10 | 820-10-16 | FUEL GAS HEATER AUX 870 | EGAT-HEC-600-INC-DLP-00001_6 | 850FT4501 GROUTING AND BASE PLATE TO BE CLEAN PROPERLY | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-09-22 | 2022-11-15 | Construction |  |  | 2022-11-12 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02936.02 | 820.10 | 820-10-16 | FUEL GAS HEATER AUX 870 | EGAT-HEC-600-INC-DLP-00001_6 | 850FT4511 ADDITIONAL SUPPORT TO BE PROVIDED | A | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-09-22 | 2022-11-15 | Construction |  |  | 2022-11-10 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02936.03 | 820.10 | 820-10-16 | FUEL GAS HEATER AUX 870 | 870-FT-4501, 870-FT-4511 | SS TAG FOR THE TAPPING POINT TO BE PROVIDED | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-09-22 | 2022-11-15 | Construction |  |  | 2022-11-13 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02954.01 | 820.10 | 820-10-20 | Aux Area | 820-TG-1020 | Hook up Drawing to be Revised for Stud Bolt Length | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-09-22 | 2023-05-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03240.01 | 820.10 | 820-10-12 | AUX.PR-01 | EGAT-HEC-600-INC-DLP-00001_6 | CALIBRATION TO BE DONE ( GEN.) | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-10-07 | 2022-12-27 |  |  |  | 2022-12-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03240.02 | 820.10 | 820-10-12 | AUX.PR-01 | EGAT-HEC-600-INC-DLP-00001_6 | 820-FT-0731 ATEX PLUG TO BE PROVIDED | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-10-07 | 2022-11-08 |  |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03242.01 | 820.10 | 820-10-12 | 820 PIPE RACK 1 | EGAT-HEC-600-INC-DWG-00006_4 | CABLE TRAY ENTRY IN PLATFORM KICK PLATE TO BE PROVIDED (GENERAL) | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-10-10 | 2022-11-23 |  | 2022-11-23 | 2022-11-23 | 2022-11-23 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03244.01 | 820.10 | 820-10-14 | AUX.PR-01 | EGAT-HEC-600-INC-DLP-00001_6 | CALIBRATION TO BE DONE | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-10-07 | 2023-01-10 |  |  |  | 2023-01-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03247.01 | 820.10 | 820-10-16 | AUX.PR-01 | EGAT-HEC-600-INC-DLP-00006_6 | BOLT LENGTH HOOK UP DRAWING TO BE REVISE | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-10-07 | 2022-11-21 |  | 2022-11-15 | 2022-11-21 | 2022-11-15 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03247.02 | 820.10 | 820-10-16 | AUX.PR-01 | 820-TT-1008 | TORQUING TO BE DONE | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-10-07 | 2022-11-15 |  |  |  | 2022-11-13 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03251.01 | 820.10 | 820-10-12 | AUX.PR-01 | 820-TT-1022 | BOLT LENGTH HOOK UP DRAWING TO BE REVISE | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-10-07 | 2022-11-21 |  | 2022-11-15 | 2022-11-21 | 2022-11-15 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03251.02 | 820.10 | 820-10-12 | AUX.PR-01 | 820-TT-1022 | TORQUING TO BE DONE | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-10-07 | 2022-11-15 |  |  |  | 2022-11-13 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03794.01 | 820.10 | 820-10-12 | AUX | EGAT-HEC-600-INC-DWG-00007_Z0 | AT INSTRUMENT TAG NUMBER 810-PT-1009-P CABLE TAG TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-27 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03803.01 | 820.10 | 820-10-24 | BOILER FEED WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | ENCLOSURE 1/4 DRAIN TUBE TO BE PROVIDED | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-10-26 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03807.01 | 820.10 | 820-10-20 | BOILER FEED WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | ENCLOSURE 1/4 DRAIN TUBE TO BE PROVIDED | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-10-26 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03808.01 | 820.10 | 820-10-12 | BOILER FEED WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | STANCHION ANCHOR BOLT LONG NEED TO CUT | B | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-10-26 | 2022-11-22 |  | 2022-11-17 | 2022-11-22 | 2022-11-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03808.02 | 820.10 | 820-10-12 | BOILER FEED WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | BETWEEN CONCRETE BLOCK AND BASE PLATE PROVIDE SEALANT | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-10-26 | 2022-11-23 |  | 2022-11-17 | 2022-11-22 | 2022-11-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03808.03 | 820.10 | 820-10-12 | BOILER FEED WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | CABLE ENTRY SELANT TO BE PROVIDED | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-10-26 | 2022-11-22 |  | 2022-11-17 | 2022-11-22 | 2022-11-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03808.04 | 820.10 | 820-10-12 | BOILER FEED WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | ENCLOSURE 1/4 DRAIN TUBE TO BE PROVIDED | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-10-26 | 2022-11-22 |  | 2022-11-17 | 2022-11-22 | 2022-11-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03815.01 | 820.10 | 820-10-12 | BOILER FEED WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | DISPLAY TO BE ROTATE | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-10-26 | 2022-11-22 |  | 2022-11-17 | 2022-11-22 | 2022-11-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03815.02 | 820.10 | 820-10-12 | BOILER FEED WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | HANGING TAG TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-10-26 | 2022-11-22 |  | 2022-11-17 | 2022-11-22 | 2022-11-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03860.01 | 820.10 | 820-10-20 | AUXILIARY | 820-FV-1009 | Damage tubing going to diaphragm need to replace | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-27 | 2022-11-23 |  | 2022-11-23 |  | 2022-11-23 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03862.01 | 820.10 | 820-10-16 | AUXILIARY | 820-PV-1001 | Touch up paint for valve body need to provide | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-27 | 2022-11-28 |  | 2022-11-28 |  | 2022-11-28 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03865.01 | 820.10 | 820-10-16 | Aux Area | 820-PV-1008B, 820-HV-1003 | On Valve Mentioned IIB Atex Marked But in Dtat sheet Showing IIC | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-27 | 2023-05-01 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03924.01 | 820.10 | 820-10-18 | BOILER FEED | EGAT-HEC-600-INC-DLP-00001_Z0 | GROUTING TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03924.02 | 820.10 | 820-10-18 | BOILER FEED | EGAT-HEC-600-INC-DLP-00001_Z0 | EARTING TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-24 |  | 2022-11-24 | 2022-11-24 | 2022-11-24 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04078.01 | 820.10 | 820-10-16 | AUX AREA | EGAT-HEC-600-INC DWG-00006_Z0 | CABLE TAGGING TO BE PROVIDE AT INSTRUMENT AND JB SIDE (820-TT-1018, 820-LT-9401 | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-29 | 2023-06-15 | Construction | [8 empty] | Construction
. | EGAT-RFI-CI-CW-04117.01 | 820.10 | 820-10-12 | BOILER FEED WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | TORQUING TO BE DONE | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-04 | 2022-11-30 |  |  | 2022-11-29 | 2022-11-29 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04117.02 | 820.10 | 820-10-12 | BOILER FEED WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | BOLT LENGTH HOOK UP DRAWING TO BE REVISE | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-04 | 2022-11-17 |  | 2022-11-15 | 2022-11-17 | 2022-11-15 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04117.03 | 820.10 | 820-10-12 | BOILER FEED WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | TG FLEXIBLE TUBE PROVIDE CABLE TRAY | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-04 | 2022-11-30 |  |  |  | 2022-11-30 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04117.04 | 820.10 | 820-10-12 | BOILER FEED WATER |  | NO ATEX MARK ON DEVICE | A | EM | HEC CI Design | Mr. Paweł Rogoziński | 2022-11-04 | 2022-11-30 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04117.05 | 820.10 | 820-10-12 | BOILER FEED WATER | 820-PG-1007, 820-TG-1015 | NO ATEX CERTIFICATE INCLUDED | A | EM | HEC CI Design | Mr. Paweł Rogoziński | 2022-11-04 | 2022-11-25 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04118.01 | 820.10 | 820-10-16 | LP Steam distribution system | 820-TG-1017 | No hanging tag | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04118.02 | 820.10 | 820-10-16 | LP STEAM DISTRIBUTION SYSTEM | 820-TG-1017 | TORQUING TO BE DONE | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2023-04-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04118.03 | 820.10 | 820-10-16 | LP Steam distribution system | 820-TG-1017 | bolt size to be revise | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-01 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04119.01 | 820.10 | 820-10-18 | STEAM BOILER | EGAT-HEC-600-INC-DLP-00001_Z0 | SS TAG PLATE TO BE FIXED | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-03 | 2022-11-28 |  |  | 2022-11-28 | 2022-11-26 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04119.02 | 820.10 | 820-10-18 | STEAM BOILER | EGAT-HEC-600-INC-DLP-00001_Z0 | LOW02,HIGH02 BOTTLE NOT INSTALLED | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-03 | 2022-12-23 |  |  |  | 2022-12-23 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04121.01 | 820.10 | 820-10-18 | STEAM BOILER | EGAT-HEC-600-INC-DLP-00001_Z0 | SS TAG ( TE ) TO BE PROVIDED | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-03 | 2022-11-24 |  | 2022-11-24 | 2022-11-24 | 2022-11-24 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04121.02 | 820.10 | 820-10-18 | STEAM BOILER | EGAT-HEC-600-INC-DLP-00001_Z0 | 820TE9155 ELEMENT TO BE FIXED PROPERLY | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-03 | 2022-11-25 |  |  |  | 2022-11-25 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04124.01 | 820.10 | 820-10-18 | 820 AUX | EGAT-HEC-600-INC-DLP-00001_Z0 | SS NAME PLATE TO BE PROVIDED | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-02 | 2022-11-23 |  | 2022-11-23 | 2022-11-23 | 2022-11-23 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04124.02 | 820.10 | 820-10-18 | 820 AUX | EGAT-HEC-600-INC-DLP-00001_Z0 | EARTING TO BE PROVIDED | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-02 | 2022-11-23 |  | 2022-11-23 | 2022-11-23 | 2022-11-23 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04134.01 | 820.10 | 820-10-18 | PP AREA | 820-MOV-9151 820-MOV-9152 820-MOV-9150 | Blind plug to be provide for each valve | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-11-21 |  |  | 2022-11-18 | 2022-11-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04134.02 | 820.10 | 820-10-18 | PP AREA | 820-MOV-9151 820-MOV-9152 820-MOV-9150 | No earthing connection for each power cable | A | EL | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-11-21 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04169.01 | 820.10 | 820-10-24 | NITROGEN AREA | EGAT-HEC-600-INC-DLP-00001_Z0 | SS HANGING TAG FOR TAPPING POINT TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-04 | 2022-11-30 |  |  | 2022-11-30 | 2022-11-29 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04169.02 | 820.10 | 820-10-24 | NITROGEN AREA | EGAT-HEC-600-INC-DLP-00001_Z0 | PLASTIC CABLE TIE TO BE CHANGE IN SS CABLE TIE | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-04 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04559.01 | 820.10 | 820-10-10 | 820 Aux Area | 820-TG-9404,820-tg-9403,820-TG-9405,820-TG-9402 | No Atex mark on device | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-25 | 2023-04-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04561.01 | 820.10 | 820-10-16 | 870 Aux Area | 870-PV-4511b,8780-PV-4503,870-PV-4511A | Drawing need to be update actual tubing installed not as per drawing | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-25 | 2023-04-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04564.01 | 820.10 | 820-10-16 | 820 AUX AREA | EGAT-HEC-600-INC-DWG-00005_Z0 | Drawing need to be updated actual tubing installed not as per drawing | A | CI | HEC CI Construction | Mr. Michal Rewera | 2022-11-25 | 2023-01-13 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04566.01 | 820.10 | 820-10-20 | CLARIFIER | EGAT-HEC-600-INC-DLP-00001_Z0 | TAPPING POINT SS TAG TO BE PROVIDED | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-28 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04604.01 | 820.10 | 820-10-16 | 870 AUX AREA | 870-FV-4511, 870-FV-4501 | Drawing need to be updated actual tubing installed not as per drawing | A | CI | HEC CI Construction | Mr. Michal Rewera | 2022-11-28 | 2023-01-13 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04627.01 | 820.10 | 820-10-18 | 820 AUX AREA | For all tag names in description | 820-VXE-9185, 820-VXE-9183, 820-VXE-9182, 820-VXE-9180, 820-VXE-9184, 820-VXE-9181, 820-VXE-9186 Sensor model & Tag name must be provided | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-29 | 2022-12-15 |  |  |  | 2022-12-13 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04627.02 | 820.10 | 820-10-18 | 820 AUX AREA | For all tag names in description | 820-VXE-9185, 820-VXE-9183, 820-VXE-9182, 820-VXE-9180, 820-VXE-9184, 820-VXE-9181, 820-VXE-9186 Cable tag number should be provided (Transducer side) | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-29 | 2022-12-15 |  |  |  | 2022-12-13 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04627.03 | 820.10 | 820-10-18 | 820 AUX AREA | 820-VXE-9185, 820-VXE-9182 | Tag number not as per drawing actual tag installation (820-VE-9182, 820-VYE-9185) | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-29 | 2022-12-15 |  |  |  | 2022-12-13 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04628.01 | 820.10 | 820-10-18 | 820 AUX AREA | 820-BE-9171B, 820-BE-9171A, 820-BE-9180A, 820-BE-9180B | Provide cable tray for flexible hose to secure cable scanner | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-29 | 2022-12-12 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04628.02 | 820.10 | 820-10-18 | 820 AUX AREA | 820-BE-9171B, 820-BE-9171A, 820-BE-9180A, 820-BE-9180B | Flexible connector need ATEX mark | A | EM | HEC MS Design | Mr. Paweł Rogoziński | 2022-11-29 | 2023-01-17 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04650.01 | 820.10 | 820-10-20 | 820 STEAM TURBINE AUX AREA | 820-PRV-0923,820-PRV-0921,820-PRV-0922 | RUSTED NUT AND BOLT NEED TO BE CLEAN | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-12-01 | 2022-12-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04679.01 | 820.10 | 820-10-10 | 820 STEAM TURBINE AUX AREA | 820-LG-9402 | HANGING TAG NEED TO PROVIDE | B | CI | HEC CI Construction | Ms. Agnieszka Gawrońska | 2022-12-01 | 2022-12-13 | Construction |  |  | 2022-12-12 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04832.01 | 820.10 | 820-10-16 | AUX AREA | 820-TT-1018 | Permanent Hanging tag to be provided | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-12-08 | 2022-12-29 |  |  |  | 2022-12-30 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04832.02 | 820.10 | 820-10-16 | AUX AREA | 820-TT-1018 | Permanent nameplate device to be provided | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-12-08 | 2022-12-30 |  |  |  | 2022-12-30 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04832.03 | 820.10 | 820-10-16 | AUX AREA | 820-TT-1018 | Atex mark for instrument to be verified | A | CI | HEC CI Design | Ms. Agnieszka Szyndler-Jurszo | 2022-12-08 | 2022-12-30 |  |  |  | 2022-12-30 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04836.01 | 820.10 | 820-10-16 | AUX AREA | 820-TE-1018 | Permanent Hanging tag to be provided | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-12-09 | 2022-12-29 |  |  |  | 2022-12-30 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04836.02 | 820.10 | 820-10-16 | AUX AREA | 820-TE-1018 | Bolt torque to be done | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-12-09 | 2022-12-30 |  |  |  | 2022-12-30 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04961.01 | 820.10 | 820-10-14 | 820 Auxiliary Area | 8EA | (820-PV-0722,820-PV-0732,820-PV-0733,820-PV-1006,820-TV-0723,820-TV-0731A,820-TV-0731B) Punching plate (raceway tube)need to be clean going to each valve | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-12-15 | 2023-05-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04961.02 | 820.10 | 820-10-14 | 820 Auxiliary Area | 5EA | 820-PV-1007A,820-PV-1007B,820-TV-1008,820-TV-1011,820-TV-1012) Punching plate (raceway tube) need to be clean going to each valve | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-12-15 | 2022-05-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-05019.01 | 800.00 | 820-00-00 | 600 AUX AREA | 600-FV-1001, 600-XV-1019, 600-FV-1004 | Drawing to be update for manifold,Tubing installation sequence not as per drawing | C | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-12-19 | 2023-04-29 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01815.01 | 820.10 | 820-10-18 | Unit-810, 820, 860 | EGAT-HEC-900-ELE-DLP-01004, 01005, 01006 | Earthing connection to be provided at 820-B0001-MW01 | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-09 | 2022-10-10 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01815.02 | 820.10 | 820-10-18 | Unit-810, 820, 860 | EGAT-HEC-900-ELE-DLP-01004, 01005, 01006 | (General for All) LCS grounding to be done | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-03-09 | 2022-10-10 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03624.01 | 820.10 | 820-10-10 | AuX area | EGAT-HEC-900-ELE-SCH-00001_1 | MV Cable outer sheet should rectify in the cable pit (MP2.02-SWG-2-1B/1A) | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-05 | 2023-01-17 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03624.02 | 820.10 | 820-10-10 | AUX area | EGAT-HEC-900-ELE-SCH-00001_1 | SS cable tag should be provide inside the cable pit | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-05 | 2023-05-02 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02207 | 820.10 | 820-10-20 | 820 | 820-E0001 | Ends of insulation cludding to completely sealed | C | IN | HEC IN Construction | Mr. Uladzimir Belavus | 2022-08-17 | 2022-12-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02224 | 820.10 | 820-10-20 | 820 | 820-P0001B | Constant level oiler to be filled before commisioning | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-18 | 2022-11-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02287.1 | 820.10 | 820-10-22 | PDH | 820-X0001 | Stud bolts to be protected with molecote | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2022-10-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02287.2 | 820.10 | 820-10-22 | PDH | 820-X0001 | Rusted stud bolts on top nozzle flanges needs to be protected with anyi sieze | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2022-10-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02287.3 | 820.10 | 820-10-22 | PDH | 820-X0001 | Touch up paint required in modified handrail | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2022-10-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02288.1 | 820.10 | 820-10-28 | PDH | 820-X0006 | Stud bolts to be protected with molecote | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2022-10-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02288.2 | 820.10 | 820-10-28 | PDH | 820-X0006 | Grounding/earthing to be installed on tanks and ladders | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2023-01-11 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02289.01 | 820.10 | 820-10-26 | PDH | 820-X0007 | Stud bolts to be protected with molecote | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2022-10-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02289.02 | 820.10 | 820-10-26 | PDH | 820-X0007 | Grounding/earthing to be installed on tanks and ladders | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2023-01-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02381.1 | 820.10 | 820-10-24 | PDH | 820-P0002A | Heat tracing to be modified | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-09-15 | 2023-01-16 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02381.2 | 820.10 | 820-10-24 | PDH | 820-P0002A | Electrical cable on motor junction box to be protected (Electrical) | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-09-15 | 2023-01-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02383.1 | 820.10 | 820-10-24 | PDH | 820-P0002B | Heat tracing to be modified | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-09-15 | 2023-01-16 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02383.2 | 820.10 | 820-10-24 | PDH | 820-P0002B | Electrical cable on motor junction box to be protected (Electrical) | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-09-15 | 2023-01-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02410 | 820.10 | 820-10-16 | 820 | 820-X0005 | Remove temporary supports | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-19 | 2022-11-15 | Construction | [8 empty] | Construction
. | EGAT-RFI-ME-DA-02411 | 820.10 | 820-10-12 | 820 | 820-X0008 | Remove temporary supports | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-19 | 2022-11-15 | Construction | [8 empty] | Construction
. | EGAT-RFI-ME-DA-02412 | 820.10 | 820-10-16 | 820 | 820-X0009 | Remove temporary supports | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-19 | 2022-11-15 | Construction | [8 empty] | Construction
. | EGAT-RFI-ME-DA-02463.1 | 820.10 | 820-10-10 | 820 | 820-B0004-E01 | Touch up paint | C | ME | HEC ME Construction | Mr. Tomasz Trakul | 2022-09-26 | 2022-11-15 | Construction | [8 empty] | Construction
. | EGAT-RFI-ME-DA-02463.2 | 820.10 | 820-10-10 | 820 | 820-B0004-E01 | Provide nameplate polish translation | C | ME | HEC ME Construction | Mr. Tomasz Trakul | 2022-09-26 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-ME-DA-02488.01 | 820.10 | 820-10-20 | PDH | 820-V0002 | Touch up on damage paint | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-11-17 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02488.02 | 820.10 | 820-10-20 | PDH | 820-V0002 | Cutted gratings on piping supports to be enclosed by toe plate | B | PI | HEC PI Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-12-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02488.03 | 820.10 | 820-10-20 | PDH | 820-V0002 | Stand up pipe on vessel bolts not complete (Piping) | B | PI | HEC PI Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2023-01-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02488.04 | 820.10 | 820-10-20 | PDH | 820-V0002 | Electrical connection to be completed (Elec) | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2023-01-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02488.05 | 820.10 | 820-10-20 | PDH | 820-V0002 | Cutted gratings on instruments supports to be enclosed by toe plate | B | CI | HEC CI Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-11-30 | Construction |  | 2022-11-28 | 2022-11-26 |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02488.06 | 820.10 | 820-10-20 | PDH | 820-V0002 | Instrument connection to be completed (Inst) | B | CI | HEC CI Construction | Mr. Uladzimir Belavus | 2022-10-04 | 2022-12-02 | Construction |  |  | 2022-12-05 |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02492.1 | 820.10 | 820-10-24 | 820 | 820-V0003 | Touch up paint on platform and welded gratings | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-10-06 | 2022-11-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02492.2 | 820.10 | 820-10-24 | 820 | 820-V0003 | Ground cable to connect on ladder (Elect.) | C | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-10-06 | 2023-01-11 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02492.3 | 820.10 | 820-10-24 | 820 | 820-V0003 | Provide toeplate cutted gratings from piping (Piping) | B | PI | HEC PI Construction | Mr. Uladzimir Belavus | 2022-10-06 | 2023-01-10 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02492.4 | 820.10 | 820-10-24 | 820 | 820-V0003 | Electrical cable connection to be completed (Elect.) | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-10-06 | 2023-01-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02492.5 | 820.10 | 820-10-24 | 820 | 820-V0003 | Provide toeplate cutted gratings from inst. support. (Inst.) | B | CI | HEC CI Construction | Mr. Uladzimir Belavus | 2022-10-06 | 2022-11-30 | Construction |  | 2022-11-28 | 2022-11-26 |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02496.1 | 820.10 | 820-10-18 | 820 | 820-B0001 | Concrete stair landing on the ground not done | B | CV | HEC CV Construction | Mr. Uladzimir Belavus | 2022-10-04 | 2022-11-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02496.2 | 820.10 | 820-10-18 | 820 | 820-B0001 | Touch up on damage paint | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-10-04 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02496.3 | 820.10 | 820-10-18 | 820 | 820-B0001 | Provide toeplate on cutted gratings from piping | B | PI | HEC PI Construction | Mr. Uladzimir Belavus | 2022-10-04 | 2022-11-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02496.4 | 820.10 | 820-10-18 | 820 | 820-B0001 | Provide toeplate on cutted gratings from instrument | B | CI | HEC CI Construction | Mr. Uladzimir Belavus | 2022-10-04 | 2022-12-06 | Construction |  |  | 2022-12-05 |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02496.5 | 820.10 | 820-10-18 | 820 | 820-B0001 | Housekeeping on the platform | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-10-04 | 2023-01-11 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02497 | 820.10 | 820-10-18 | 820 | 820-B0001-X01 | Remove tarpulin cover on top opening of the stack before commisioning | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-10-07 | 2022-11-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02560.1 | 820.10 | 820-10-18 | 820 | 820-B0001-W02 | Sight glass to be clean (PIP) | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-10-26 | 2022-11-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02560.2 | 820.10 | 820-10-18 | 820 | 820-B0001-W02 | Cover electrical cable tray (ELEC) | C | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-10-26 | 2023-05-02 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02560.3 | 820.10 | 820-10-18 | 820 | 820-B0001-W02 | Pipes need more support (PIP) | B | PI | HEC PI Construction | Mr. Uladzimir Belavus | 2022-10-26 | 2022-11-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02560.4 | 820.10 | 820-10-18 | 820 | 820-B0001-W02 | Touch-up paint on pneumatic actuator | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-10-26 | 2022-11-29 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02650 | 820.10 | 820-10-16 | 820 | 820-X0002A | Touch up damage paint | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-12-23 | 2023-03-10 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02651 | 820.10 | 820-10-16 | 820 | 820-X0002B | Touch up damage paint | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2023-01-23 | 2023-01-31 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02652 | 820.10 | 820-10-16 | 820 | 820-X0003 | Touch up damage paint | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2023-01-23 | 2023-01-31 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02653 | 820.10 | 820-10-14 | 820 | 820-X0010 | Touch up damage paint | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2023-01-23 | 2023-01-31 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02654 | 820.10 | 820-10-14 | 820 | 820-X0011A | Touch up damage paint | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2023-01-23 | 2023-01-31 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02655 | 820.10 | 820-10-14 | 820 | 820-X0011B | Touch up damage paint | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2023-01-23 | 2023-01-31 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02681.1 | 820.10 | 820-10-10 | 820 | 820-B0004 | TOP PLATE FOR ELECTRICAL CABLES MISSING | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2023-01-09 | 2023-01-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02681.2 | 820.10 | 820-10-10 | 820 | 820-B0004 | ELECTRICAL GROUNDING NEED TO BE FINISHED | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2023-01-09 | 2023-01-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02681.3 | 820.10 | 820-10-10 | 820 | 820-B0004 | COUPLING COVER NEED TO BE INSTALL | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2023-01-09 | 2023-06-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02681.4 | 820.10 | 820-10-10 | 820 | 820-B0004 | IMPULSE LINE 820-PT-9402 NEED TO BE ISOLATED | C | IN | HEC IN Construction | Mr. Uladzimir Belavus | 2023-01-09 | 2023-04-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02684.1 | 820.10 | 820-10-10 | 820 | RUNDOWN TANK | ISOLATION NEED TO BE FINISHED | C | IN | HEC IN Construction | Mr. Uladzimir Belavus | 2023-01-12 | 2023-04-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | NCR-ME016.01 | 820.10 | 820-10-18 | HP Boiler | General | Apply sealant on every gap of insulatin jacket and reverse overlaping (Attached Pics') | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2021-11-16 |  | Construction |  | Changed from Category B |  | IN | V |  |  | 2023-03-10 | RFC/RFSU
. | NCR-ME016.02 | 820.10 | 820-10-18 | HP Boiler | General | Remove rust&stain on Insulation Jacket and protection (Attached Pics') | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2021-11-16 |  | Construction |  |  |  |  | V |  |  |  | RFC/RFSU
. | NCR-ME016.03 | 820.10 | 820-10-18 | HP Boiler | General | Screws for fixing insulation jacket got rust, need to be replaced with SS (attached Pic.) | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2021-11-16 |  | Construction |  |  |  |  | V |  |  |  | RFC/RFSU
. | NCR-ME074.01 | 820.10 | 820-10-18 | HP Boiler | General | General House keeping on insulation (Attached Pics') | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2021-11-16 |  | Construction |  |  |  |  | V |  |  |  | RFC/RFSU
. | NCR-ME074.02 | 820.10 | 820-10-18 | HP Boiler | General | (General) Check-plates need to be cleaned(free from rust) and painted | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2021-11-16 |  | Construction |  |  |  |  | V |  |  |  | RFC/RFSU
. | NCR-ME074.04 | 820.10 | 820-10-18 | HP Boiler | General | Name Plate of expansion joint has wrong translation | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2021-11-16 |  | Construction |  |  |  |  | V |  |  |  | RFC/RFSU
. | NCR-ME074-03 | 820.10 | 820-10-18 | HP Boiler | General | (General) Plat-form structures need to be free from rust and touched up | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2021-11-16 |  | Construction |  |  |  |  | V |  |  |  | RFC/RFSU
. | NCR-ME139 | 820.10 | 820-10-10 | PDH | 820-B0004 | The Contractor still should submit plan of handling and transportation for Generator maintenance purposes (how the Generator will be removed from site, including all details of removable roof including dimmensioning, which elements are intended for disassembly, type and capacity of crane required for such operation, positioning of the crane and truck, taking into account all space limitations, obstacles and current plot-plan. | C | EM | HEC MR Design | Mr. Krzysztof Nolbert | 2023-05-25 |  | Construction | [8 empty] | RFC/RFSU
. | PICS.300PR-MS-2002.01 | 820.10 | 820-10-14 |  |  | Padloc on valve missing | C | COMM | HEC COMM | Mr. Tomasz Trakul | 2022-10-19 |  | Construction | [8 empty] | RFC/RFSU
. | PICS.300PR-MS-2002.02 | 820.10 | 820-10-14 |  |  | Insulation not finished, ends not protected | C | IN | HEC IN Construction | Mr. Tomasz Trakul | 2022-10-19 | 2023-04-06 | Construction |  |  |  |  | V |  |  |  | RFC/RFSU
. | PICS.820BFV-BW-1003.01 | 820.10 | 820-10-18 |  |  | Insulation damage to be rectify | C | IN | HEC IN Construction | Mr. Tomasz Trakul | 2022-06-07 | 2023-03-31 | Construction |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14377 | 840.10 | 840-10-10 | unit 840 | 200PR1-NA-0002 | Reinstatement | A | PI | HEC PI Construction | J.W.JEONG | 2022-11-22 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14378 | 840.10 | 840-10-10 | unit 840 | 840-PG-1001A | Inspection for Installation | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14379 | 840.10 | 840-10-10 | unit 840 | 840-PG-1001B | Inspection for Installation | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14380 | 840.10 | 840-10-10 | unit 840 | 840-TE-1001 | Inspection for Installation | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14381 | 840.10 | 840-10-10 | unit 840 | 840-TE-1002 | Inspection for Installation 11 | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14382 | 840.10 | 840-10-10 | unit 840 | 840-TE-1003 | Inspection for Installation | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14383 | 840.10 | 840-10-10 | unit 840 | 810WS-TRE-1001 | Final Appeareance Inspection | C | IN | HEC IN Construction | J.W.JEONG | 2022-11-22 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14384 | 840.10 | 840-10-10 | unit 840 | 810WS-NA-1002_R | Final Appeareance Inspection | B | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14385 | 840.10 | 840-10-10 | unit 840 | 840-M0001 | Final Appeareance Inspection | B | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14386 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Housekeeping to be done | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-11-22 | 2023-01-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14387 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Steel cover to be provided for the pit | C | CV | HEC CV Construction | Ms. Alicja Sulżyc | 2022-11-22 |  | Walkdown | Gusan |  |  |  | V |  |  |  | RFC/RFSU
. | 14388 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Pit to be dewatered and cleaned | B | CV | HEC CV Construction | Ms. Alicja Sulżyc | 2022-11-22 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14389 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Piping sealing to be provided for pipelines crossing the dike walls | B | CV | HEC CV Construction | Ms. Paulina Bajer | 2022-11-22 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14390 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Rusted nuts on vent to atmosphere | B | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14391 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Touch-up paiting of railings to be provided | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-11-22 | 2023-01-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14392 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Handwheel of manual valve on pump suction line to be tightnened | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14393 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Manual valve on pump suction line downstream of spectacle blind to be relocated in P&ID as per Site conditions | B | EM | HEC PI Design | Ms. Paulina Bajer | 2022-11-22 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14394 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Sampling point no. 8401 - unable to collect the sample (to be shortened). | A | PI | HEC PI Construction | Ms. Alicja Sulżyc | 2022-11-22 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14395 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | PG-1001A/B- wrong hanging tags | B | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-11-30 | Walkdown |  | 2022-11-29 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 14396 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Oil indicator to be tightened (pump A) | A | ME | HEC ME Construction | Ms. Alicja Sulżyc | 2022-11-22 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14397 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Pump sealing to be completed (pump A/B) | A | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14398 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | FV-1004: grounding to be connected | A | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-12-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14399 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Drain downstream of the mixer to be relocated in P&ID downstream of TT-1001 | B | EM | HEC PI Design | Ms. Paulina Bajer | 2022-11-22 | 2022-12-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14400 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | End blinds to be provided in P&ID upustream and downstream of the cooler | B | EM | HEC PI Design | Ms. Alicja Sulżyc | 2022-11-22 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14401 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Anti-caustic coating to be provided | B | CV | HEC Marin Const. | Ms. Paulina Bajer | 2022-11-22 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14402 | 840.10 | 840-10-10 | unit 810 | EGAT-HEC-810-1''-SW-00112-B1A2-C-N | Support to be tightened | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14403 | 840.10 | 840-10-10 | PDH area | EGAT-HEC-200-PRO-PID-10361 | Electrical tracing to be provided | B | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-11-22 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14404 | 840.10 | 840-10-10 | PDH area | EGAT-HEC-200-PRO-PID-10361 | Insulation to be provided | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-22 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14405 | 840.10 | 840-10-10 | PDH area | EGAT-HEC-200-PRO-PID-30061 | Electrical tracing to be provided | B | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-11-22 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14406 | 840.10 | 840-10-10 | PDH area | EGAT-HEC-200-PRO-PID-30061 | Insulation to be provided | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-22 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14407 | 840.10 | 840-10-10 |  | n/a | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-11-22 | 2023-05-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14408 | 840.10 | 840-10-10 |  | n/a | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-22 |  | Walkdown | [8 empty] | RFC/RFSU
. | 14409 | 840.10 | 840-10-10 |  | common | Rusted bolts | B | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14410 | 840.10 | 840-10-10 |  | common | Rusted handhweels | B | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-12-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14411 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Electrical tracing on bypass of TV, FV, steam trap to be terminated | B | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-11-22 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14412 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Rusted spectacle blinds | B | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-22 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14413 | 840.10 | 840-10-10 | unit 840 | EGAT-HEC-PRO-PID-00041 | Insulation on TSTR-002 not completed and wool not secured | B | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-22 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14414 | 840.10 | 840-10-10 | Caustic Storage and Distribution System | 840-PG-1001A, 840-PG-1001B | Wrong tag | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-22 | 2022-11-30 | Walkdown |  | 2022-11-29 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 14415 | 840.10 | 840-10-10 | Caustic Storage and Distribution System | 840-FV-1004 | Electrical tracing to be done | A | EL | HEC EL Construction | Owner Maintenance team | 2022-11-22 | 2022-12-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14416 | 840.10 | 840-10-10 | Caustic Storage and Distribution System | 840-FV-1004 | Loose cover | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-22 | 2022-11-28 | Walkdown |  | 2022-11-28 | 2022-11-28 |  | V |  |  |  | RFC/RFSU
. | 14417 | 840.10 | 840-10-10 | Caustic Storage and Distribution System | 840-FV-1004 | Missing grounding | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-22 | 2022-11-30 | Walkdown |  | 2022-11-29 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 14418 | 840.10 | 840-10-10 | Caustic Storage and Distribution System | 840-LI-1001B | Loose grounding | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-22 | 2022-11-28 | Walkdown |  | 2022-11-28 | 2022-11-28 |  | V |  |  |  | RFC/RFSU
. | 14419 | 840.10 | 840-10-10 | Caustic Storage and Distribution System | 840-LT-1002 | Bolts to be tightened | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-22 | 2022-12-02 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 14420 | 840.10 | 840-10-10 | Caustic Storage and Distribution System | 840-TT-1003 | Missing hanging and cable tag | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-22 | 2022-11-30 | Walkdown |  | 2022-11-29 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 14421 | 840.10 | 840-10-10 | Caustic Storage & Distribution System | EGAT-HEC-840-PRO-PID-00011 | Motor Cable glands to be tightned for (Tag no:-840-MP0001A/JB & MP0001B) | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-22 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14422 | 840.10 | 840-10-10 | Caustic Storage & Distribution System | EGAT-HEC-840-PRO-PID-00011 | Main earthing to be connected to motor body not to terminal box (Tag no:-840-MP0001A/JB & MP0001B) | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-22 | 2022-12-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14423 | 840.10 | 840-10-10 | Caustic Storage & Distribution System | EGAT-HEC-840-PRO-PID-00011 | Eye bolts to be provided for Motors (Tag no:-840-MP0001A/JB & MP0001B) | B | ME | HEC ME Construction | Mr. Arkadiusz Tryniszewski | 2022-11-22 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14424 | 840.10 | 840-10-10 | Caustic Storage & Distribution System | EGAT-HEC-840-PRO-PID-00011 | Motor touch-up paint to be done (Tag no:-840-MP0001A/JB & MP0001B) | B | ME | HEC ME Construction | Mr. Arkadiusz Tryniszewski | 2022-11-22 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14425 | 840.10 | 840-10-10 | 840-M0001A/B | 840-M0001A/B | Missing insulation at pump side | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2022-02-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14426 | 840.10 | 840-10-10 | 840-M0001A/B | 840-M0001A/B | Housekeeping to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14427 | 840.10 | 840-10-10 | 840-M0001A/B | 840-M0001A/B | Rust on pump to be remove | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14428 | 840.10 | 840-10-10 | 840-MP0001A | 840-MP0001A | Missing stainless steel eyebolt | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14429 | 840.10 | 840-10-10 | 840-MP0001A | 840-MP0001A | Loose oil leveler to be tightened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14430 | 840.10 | 840-10-10 | 840-MP0001A | 840-MP0001A | Rusted bolt and nuts at drain line to be cleaned and protected | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14431 | 840.10 | 840-10-10 | 840-E0001 | 840-E0001 | insulation not yet completed | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14432 | 840.10 | 840-10-10 | 840-E0001 | 840-E0001 | Rusted bolt and nuts to be cleaned and protected near VC1C10CH | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2022-12-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14433 | 840.10 | 840-10-10 | 840-ST0001 | 840-ST0001 | Annular to concrete foundation to be sealed ( due to water accumulation) | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 |  | Walkdown |  |  |  | DA | V |  |  |  | RFC/RFSU
. | 14434 | 840.10 | 840-10-10 | 840-ST0001 | 840-ST0001 | Rusted bolts and nuts to be cleaned and protected at VG1C11CH | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2023-03-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14435 | 840.10 | 840-10-10 | 840-ST0001 | 840-ST0001 | Housekeeping around the tank to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2023-03-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14436 | 840.10 | 840-10-10 | 840-ST0001 | 840-ST0001 | Concrete spill wall capacity to be verefied ( Due to piping connection directly connected to the concrete wall ) | B | EM | HEC SE Design | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14437 | 840.10 | 840-10-10 | 840-ST0001 | 840-ST0001 | Loose grating clips to be tigthened | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14438 | 840.10 | 840-10-10 | 840-ST0001 | 840-ST0001 | Touch-up painting of handrail roof platform and stair | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14439 | 840.10 | 840-10-10 | 840-ST0001 | 840-ST0001 | Loose bolt on the stair step to be tigthened ( 2nd platform landing 3rd stair step) | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14440 | 840.10 | 840-10-10 | 840-ST0001 | 840-ST0001 | Gauge hatch to be touch up painted | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-22 | 2023-03-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14915 | 840.10 | 840-10-10 | General | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16236 | 840.10 | 840-10-12 | Caustic Section Sanitary Lift Station | 840-PRO-PID-00021 | HSCN 001 to be provided | B | PI | HEC PI Construction | Ms. Alicja Sulżyc | 2022-12-06 | 2022-12-12 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16237 | 840.10 | 840-10-12 | Caustic Section Sanitary Lift Station | 840-PRO-PID-00021 | Insulation incomplete | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-12-06 | 2023-02-28 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16238 | 840.10 | 840-10-12 | Caustic Section Sanitary Lift Station | 900-PRO-PID05101 | Rusted bolts on check valve | C | PI | HEC PI Construction | Ms. Alicja Sulżyc | 2022-12-06 | 2023-02-17 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16239 | 840.10 | 840-10-12 | Caustic Section Sanitary Lift Station | general | Housekeeping to be done | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-12-06 | 2022-12-15 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16240 | 840.10 | 840-10-12 | Caustic Section Sanitary Lift Station | 900-PRO-PID05101 | Cleaning inside the pit | B | CV | HEC CV Construction | Ms. Paulina Bajer | 2022-12-06 | 2023-01-13 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16241 | 840.10 | 840-10-12 | Caustic Section Sanitary Lift Station | 900-PRO-PID05101 | Touch up painting | B | PA | HEC PA Construction | Ms. Alicja Sulżyc | 2022-12-06 | 2022-12-12 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16242 | 840.10 | 840-10-12 | 810WS | EGAT-HEC-840-PRO-PID-00021 / 840-2-WW-02101-B1A1-ET | Support not resting properly | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-12-06 | 2022-12-12 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16243 | 840.10 | 840-10-12 | 810WS | EGAT-HEC-840-PRO-PID-00021 / 840-2-WW-02101-B1A1-ET | Valve visor bolts missing | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-12-06 | 2022-12-12 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16244 | 840.10 | 840-10-12 | 810WS | EGAT-HEC-840-PRO-PID-00021 / 840-2-WW-02101-B1A1-ET | Hose connector not installed (HSCN-001) | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-12-06 | 2022-12-12 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16245 | 840.10 | 840-10-12 | 810WS | EGAT-HEC-840-PRO-PID-00021 / 840-2-WW-02101-B1A1-ET | Touch up paint to be done on pipe, supports and valves | A | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-12-06 | 2022-12-12 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16246 | 840.10 | 840-10-12 | 810WS | EGAT-HEC-840-PRO-PID-00021 / 840-3-AV-02101-B1A1-N | Touch up paint to be done | A | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-12-06 | 2022-12-12 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16247 | 840.10 | 840-10-12 | 810WS | EGAT-HEC-840-PRO-PID-00021 / 840-2-WW-02101-B1A1-ET | Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-12-06 | 2023-04-06 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16248 | 840.10 | 840-10-12 | 810WS | EGAT-HEC-840-PRO-PID-00021 / 840-2-WW-02101-B1A1-ET | PG-2101A not installed | A | CI | HEC CI Construction | Mr. Jakub Partyka | 2022-12-06 | 2023-01-03 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16249 | 840.10 | 840-10-12 | 810WS | EGAT-HEC-840-PRO-PID-00021 | Pipe connection to pump unable to conduct inspection due to basin full of water | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-12-06 | 2022-12-12 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16250 | 840.10 | 840-10-12 | 840-P002A | 840-P002A | Rust on pump to be remove | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-12-06 | 2022-12-14 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16251 | 840.10 | 840-10-12 | Caustic Section Sanitary Lift Station | 840-LT-2101, 840-LT-2102 | Proper atex markig shall be selected on devices | A | CI | HEC CI Construction | Mr. Michał Fabiszewski | 2022-12-06 | 2023-01-25 | Walkdown |  |  | 2023-01-25 |  | V |  |  |  | RFC/RFSU
. | 16252 | 840.10 | 840-10-12 | Caustic Section Sanitary Lift Station | common | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PI Construction | Ms. Paulina Bajer | 2022-12-06 | 2023-04-26 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16253 | 840.10 | 840-10-12 | Caustic Section Sanitary Lift Station | common | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-06 | [10 empty] | RFC/RFSU
. | 16254 | 840.10 | 840-10-12 | Caustic section sanitary lift station | EGAT-HEC-840-PRO-PID-00021 | Cable tray cleaning to be done | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-06 | 2023-01-12 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16255 | 840.10 | 840-10-12 | Caustic section sanitary lift station | EGAT-HEC-840-PRO-PID-00021 | Tag No :- 840-MP0002A LCS blind plug to be provided | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-06 | 2023-01-09 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16256 | 840.10 | 840-10-12 | Caustic section sanitary lift station | EGAT-HEC-840-PRO-PID-00021 | Provide yellow tag sticker for LCS EMERGENCY PUSH BOTTON at cover side written with Polish Language [ WYŁĄCZNIK AWARYJNY ] for (Tag No :- 840-MP0002A) | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-06 | 2023-04-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16257 | 840.10 | 840-10-12 | Caustic section sanitary lift station | EGAT-HEC-840-PRO-PID-00021 | Conduit Stub-up sealing to be done | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-12-06 | 2023-01-09 | [5 empty] | V |  |  |  | RFC/RFSU
. | 16258 | 840.10 | 840-10-12 | Caustic section sanitary lift station | EGAT-HEC-840-PRO-PID-00021 | Manhole cover to be flatted | A | CV | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-12-06 | 2023-01-11 | [5 empty] | V |  |  |  | RFC/RFSU
. | 31104 | 840.10 | 840-10-10 | 840-SN-8401 | 840-SN-8401 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31139 | 840.10 | 840-10-10 | unit 840 |  | Incorrect piping identification on strong caustic line from GAP (violet instead of green colour should be applied) | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2023-03-17 | 2023-05-08 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31785 | 840.10 | 840-10-10 | 840-3/4"-LS-61001-MS-11-H | 840-3/4"-LS-61001-MS-11-H | steam trap missing | C | PI | HEC PI Construction | Mr. Jarosław Pykosz | 2023-05-07 |  | PAC | [8 empty] | RFC/RFSU
. | 32126 | 840.10 | 840-10-10 | unit 840 | 840-ST0001 | Gap in between Storage tank 840-ST0001 - crushed grouting arund bottom of the tank - the annular plate. Grouting to be repaired and gaps to be sealed. Pockets around annular plate of tank causing water stagnation and corrosion to be removed. | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-06-01 | 2023-06-27 | PAC | [8 empty] | RFC/RFSU
. | 32128 | 840.10 | 840-10-10 | unit 840 | 840-ST0001 | Handrails on the stair to the - 840-ST0001 dike to be fixed - missing nuts. | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-06-01 | 2023-06-12 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 32129 | 840.10 | 840-10-10 | unit 840 | 840-ST0001 | Grating inside the 840-ST0001 dike (sump) to be provided. | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-06-01 | 2023-06-12 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 32445 | 840.10 | 840-10-10 | unit 840 | 840-P0001A/B | Diluted Caustic Pumps 840-P0001A/B - mechanical seal leakage | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-06-14 |  | PAC | [8 empty] | RFC/RFSU
. | EGAT-RFI-CI-CW-01550.01 | 840.10 | 840-10-12 | Auxiliary | Level Transmitter | Proper orientation of 840-LT-2101 | B | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-11-23 | Construction | 2022-11-23 | 2022-11-23 | 2022-11-23 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01550.02 | 840.10 | 840-10-12 | Auxiliary | Level Transmitter | Torquing to be done | B | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01560.01 | 840.10 | 840-10-10 | Auxiliary | Temperature transmitter | 840-TT-1003,1001 Torquing to be done | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-09-26 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01560.02 | 840.10 | 840-10-10 | Auxiliary | 840-TT-1001 | LCD to be rotate | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-09-26 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01560.03 | 840.10 | 840-10-10 | Auxiliary | Temperature transmitter | 840-TT-1003, 1001 Elbow for cable entry to be apply | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-09-13 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02456.01 | 840.10 | 840-10-10 | Auxiliary | 840-LT-1001, 1002 | Calibration to be done | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-12-15 | Construction |  |  | 2022-12-13 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02456.02 | 840.10 | 840-10-10 | Auxiliary | 840-LT-1001, 1002 | Sunshade to be provide | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-02 | 2022-11-16 | Construction | 2022-11-15 |  | 2022-11-15 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02653.01 | 840.10 | 840-10-10 | AUX | 840-E0001 | Torquing to be done | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-11-22 | Construction | 2022-11-15 | 2022-11-22 | 2022-11-15 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02653.02 | 840.10 | 840-10-10 | AUX | 840-E0001 | Hook up drawing to be revised for stud bolt length | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-10-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02718.01 | 840.10 | 840-10-10 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | SS Hanging tag to be provided | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-13 | 2022-11-17 | Construction | 2022-11-15 | 2022-11-17 | 2022-11-15 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02718.02 | 840.10 | 840-10-10 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | Transmitter hole for mounting bracket plug to be provided | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-13 | 2022-11-17 | Construction | 2022-11-15 | 2022-11-17 | 2022-11-15 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02720.01 | 840.10 | 840-10-10 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | SS Hanging tag to be provided | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-13 | 2022-11-22 | Construction | 2022-11-18 | 2022-11-22 | 2022-11-18 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02720.02 | 840.10 | 840-10-10 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | Cable tray to be provided ( Capillary Tube ) | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-13 | 2022-11-22 | Construction | 2022-11-18 | 2022-11-22 | 2022-11-18 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02720.03 | 840.10 | 840-10-10 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | Torquing to be done | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-13 | 2022-12-01 | Construction |  |  | 2022-11-30 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02720.04 | 840.10 | 840-10-10 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | Sun Shade to be provided | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-13 | 2022-11-22 | Construction | 2022-11-17 | 2022-11-22 | 2022-11-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03776.01 | 840.10 | 840-10-10 | AUX | EGAT-HEC-600-INC-DWG-00007_Z0 | AT INSTRUMENT TAG NUMBER 840-LAH-1001 CABLE DUCT TRAY BONDING JUMPER TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-27 | 2022-11-18 |  | 2022-11-18 | 2022-11-18 | 2022-11-18 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03776.02 | 840.10 | 840-10-10 | AUX | EGAT-HEC-600-INC-DWG-00007_Z0 | CABLE TRAY ENTRY IN PLATFORM KICK PLATE TO BE PROVIDED AT 840-ST0001 | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-27 | 2022-12-01 |  |  |  | 2022-12-01 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03935.01 | 840.10 | 840-10-10 | 840-SL-004 | EGAT-HEC-600-INC-DLP-00001_Z0 | SUNSHADE TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03935.02 | 840.10 | 840-10-10 | 840-SL-004 | EGAT-HEC-600-INC-DLP-00001_Z0 | SS HANGING TAG TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04159.01 | 840.10 | 840-10-10 | Caustic storage and distribution system | EGAT-HEC-600-INC-TDS-00022_2 | Attached calbration certificate for measuring equipment and a copy of measuring license for mr wilfredo c paypa and mr bae hyeokdong | C | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-08 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04560.01 | 840.10 | 840-10-12 | 820 Aux Area | 840-PG-2101A,840-PG-1001A,840-PG-1001B | Capillary tube need to secure with ss tie | C | CI | HEC CI Construction | Mr. Michal Piotrowski | 2022-11-25 | 2023-04-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04560.02 | 840.10 | 840-10-12 | 820 Aux Area | 840-PG-2101A,840-PG-1001A,840-PG-1001B | Bolt length not as per hook up drawing | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-25 | 2023-04-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04560.03 | 840.10 | 840-10-12 | 820 Aux Area | 840-PG-2101A | Grouting need to be cleaned | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-25 | 2023-04-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02430.1 | 840.10 | 840-10-10 | 840 | 840-P0001A | Heat tracing cable to complete (Electrical) | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-09-22 | 2023-01-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02430.2 | 840.10 | 840-10-10 | 840 | 840-P0001A | Grouting on Local Control Panel to be done (Electrical) | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-09-22 | 2023-01-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02431.1 | 840.10 | 840-10-10 | 840 | 840-P0001B | Heat tracing cable to complete (Electrical) | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-09-22 | 2023-01-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02431.2 | 840.10 | 840-10-10 | 840 | 840-P0001B | Grouting on Local Control Panel to be done (Electrical) | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-09-22 | 2023-01-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | 00512 | 810.10 | 810-10-18 | 810 Unit | Common | Piping Insulation missing. | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00513 | 810.10 | 810-10-18 | 810 Unit | Common | Piping Electrical tracing missing. | C | EL | HEC EL Construction | Mr. Maciej Smalira | 2022-07-06 | 2023-03-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00514 | 810.10 | 810-10-18 | 810 Unit | 810-ST0001 | Two gauge hatches on the tank while only one specified in P&ID - document to be revised. Vendor drawings to be revised as well. | B | EM | HEC MS Design | Ms. Paulina Bajer | 2022-07-06 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00515 | 810.10 | 810-10-18 | 810 Unit | 810-ST0001 | Gauge hatches - cover to be fixed. | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00518 | 810.10 | 810-10-18 | 810 Unit | 810-ST0001 | Plant Water tank is filled with water - unable to check the internals | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-06 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00519 | 810.10 | 810-10-18 | 810 Unit | 810-ST0001 | Final Inspection for 810-ST0001 not completed. | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-06 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00520 | 810.10 | 810-10-18 | 810 Unit | 810-ST0001 | Missing spectacle blind on the line no. 810-12''-FW-00118 upstream the tank | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-07-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00521 | 810.10 | 810-10-18 | 810 Unit | 810-ST0001 | Strainer on LC line missing in P&ID. | B | EM | HEC PR Design | Ms. Paulina Bajer | 2022-07-06 | 2022-09-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00522 | 810.10 | 810-10-18 | 810 Unit | 810-ST0001 | Spacer should be open (810-20''-FW-00101-MS-1-ET) | A | PI | HEC PI Construction | Mr. Piotr Słowik | 2022-07-06 | 2022-08-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00523 | 810.10 | 810-10-18 | 810 Unit | 810-ST0001 | Spectacle blind should be open (810-1''-Sw-00120-B1A1-Et) | A | PI | HEC PI Construction | Mr. Piotr Słowik | 2022-07-06 | 2022-07-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00524 | 810.10 | 810-10-18 | 810 Unit | 810-ST0001 | Spectacle blind should be closed (810-4''-SW-00122-B1A1-N) | A | PI | HEC PI Construction | Mr. Piotr Słowik | 2022-07-06 | 2022-07-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00525 | 810.10 | 810-10-18 | 810 Unit | 810-SN-8108 | 810-SN-8108 - discharge line is not alligned with funnel (OY system). | A | PI | HEC PI Construction | Mr. Slawomir Dyrda | 2022-07-06 | 2022-07-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00526 | 810.10 | 810-10-18 | 810 Unit | P&D no. 810-00101 | Missing injection nozzle for chlorinated water solution | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-09-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00527 | 810.10 | 810-10-18 | 810 Unit | 810-SN-8112 | 810-SN-8112 - discharge line to shortened (unable to take a sample) | A | PI | HEC PI Construction | Mr. Slawomir Dyrda | 2022-07-06 | 2022-07-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00528 | 810.10 | 810-10-18 | 810 Unit | 810-P0006A | PG-1010A to be rotated for better visibility form pump local control panel | A | CI | HEC CI Construction | Mr. Slawomir Dyrda | 2022-07-06 | 2022-07-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00529 | 810.10 | 810-10-18 | 810 Unit | 810-P0006B | PG-1010B to be rotated for better visibility form pump local control panel | A | CI | HEC CI Construction | Mr. Slawomir Dyrda | 2022-07-06 | 2022-07-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00530 | 810.10 | 810-10-18 | 810 Unit | FV-1012 bypass line | Valve on the bypass line of FV-1012 - handle missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-07-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00531 | 810.10 | 810-10-18 | 810 Unit | P&ID no. 810-00141 | TG-1015 - gauge face invisible from the gorund level. | A | CI | HEC CI Construction | Mr. Slawomir Dyrda | 2022-07-06 | 2022-07-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00532 | 810.10 | 810-10-18 | 810 Unit | P&ID no. 900-05052 | Plant Water to 840-P0001 and 840-P0001B to be verified in P&ID - common header at Site. | B | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-07-06 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00533 | 810.10 | 810-10-18 | 810 Unit | P&ID no. 900-05052 (2) | Missing SW lines to US inside Fire Pump Building and Potable Water Building in the P&ID. | B | EM | HEC PR Design | Ms. Paulina Bajer | 2022-07-06 | 2022-09-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00534 | 810.10 | 810-10-18 | 810 Unit | 810-STRP-001 | Steam trap type under discussion with the Owner. Bimmetalic steam trap to be applied. | C | EM | HEC PI Design | Mr. Krzysztof Kaliszyk | 2022-07-06 |  | Walkdown | [8 empty] | RFC/RFSU
. | 00535 | 810.10 | 810-10-18 | 810 Unit | 810-FE-9161 | Flow orifice not installed. | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-07-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00536 | 810.10 | 810-10-18 | 810 Unit | P&ID no. 810-00011D | Valve on the bypass line of FV-9161 - handle missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-07-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00537 | 810.10 | 810-10-18 | 810 Unit | 820-US-011 | "On platform of structure" configuration shall be applied based on the typical drawing (EGAT-HEC-810-PIP-DLP-01001) | A | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-06 | 2022-10-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00538 | 810.10 | 810-10-18 | 810 Unit | Utility stations - common | Electrical tracing missing | B | EL | HEC EL Construction | Mr. Maciej Smalira | 2022-07-06 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00539 | 810.10 | 810-10-18 | 810 Unit | Common | Latest drawing no. EGAT-HEC-900-PRO-PID-05052 (2) was not provided in boundary drawing - scope of the sub-system has been revised. | A | COMM | HEC COMM | Ms. Paulina Bajer | 2022-07-06 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00540 | 810.10 | 810-10-18 | 810 Unit | 810-ST0001 | Level gauge 810-LG-1001 is still specified in Vendor data. Please verify it and revise it if necessary. | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-06 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00541 | 810.10 | 810-10-18 | 810 Unit | Common | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-07-06 | 2023-05-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00542 | 810.10 | 810-10-18 | 810 Unit | Common | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-06 |  | Walkdown | [8 empty] | RFC/RFSU
. | 00543 | 810.10 | 810-10-18 | 810 Unit | EGAT-HEC-810-PRO-PID-00101 | Necessary protection of sharp edges of cable trays against the possibility of cable damage (applies mainly to places where there are no vertical bends and horizontal tees) | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00544 | 810.10 | 810-10-18 | 810 Unit | EGAT-HEC-810-PRO-PID-00101 | Necessary verification and ensuring the correct cable bending radius in places where there are no vertical bend, horizontal tees | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00545 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1001 | The supporting structure is unstable (the support pipe is moving) - it is necessary to ensure a stable mounting structure of the trasmitter. | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00546 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1001 | Wrong TAG NO on the device plate - necessary correction: 810-LG-1001 -> 810-LT-1001 | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00547 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1001 | The correct Atex Marking is not selected on the transmitters. There are currently 3 ATEX Marking to choose from. | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00548 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1020 | Transmitter has a plastic cap - necessary installation of the cap in the ATEX execution. | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00549 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1020 | The correct Atex Marking is not selected on the transmitters. There are currently 3 ATEX Marking to choose from. | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00550 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1021 | Transmitter has a plastic cap - necessary installation of the cap in the ATEX execution. | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00551 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1021 | The correct Atex Marking is not selected on the transmitters. There are currently 3 ATEX Marking to choose from. | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00552 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1022 | Transmitter has a plastic cap - necessary installation of the cap in the ATEX execution. | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00553 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1022 | The correct Atex Marking is not selected on the transmitters. There are currently 3 ATEX Marking to choose from. | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00554 | 810.10 | 810-10-18 | 810 Unit | 810-FT-1012 | The sample line is not heated. Necessary addition of heating of the sample line. | A | EL | HEC EL Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00555 | 810.10 | 810-10-18 | 810 Unit | 810-FT-1012 | The thermostat is not properly mounted (losse installed) - the necessary correction of the assembly | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-11-16 | Walkdown |  |  | 2022-11-15 |  | V |  |  |  | RFC/RFSU
. | 00556 | 810.10 | 810-10-18 | 810 Unit | 810-FT-1012 | No ground wire connection | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00557 | 810.10 | 810-10-18 | 810 Unit | 810-FT-1012 | No information about the reduced surface resistance of the protection enclosure - the appropriate certificate will be provided | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00558 | 810.10 | 810-10-18 | 810 Unit | 810-FT-1012 | Wrong TAG NO of the power cable - necessary correction: 810-PT-1012 -> 810-FT-1012 | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00559 | 810.10 | 810-10-18 | 810 Unit | 810-PT-1010 | Necessary tightening of the cable glands | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00560 | 810.10 | 810-10-18 | 810 Unit | 810-TT-1002 | Device is not installed | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00561 | 810.10 | 810-10-18 | 810 Unit | 810-PG-1014 | Device is not installed | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00562 | 810.10 | 810-10-18 | 810 Unit | 810-TI-1002 | The display is mounted sideways (at an angle of 90 degrees) - troublesome reading of the value | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00563 | 810.10 | 810-10-18 | 810 Unit | 810-TT-1004, 810-TG-1015, 810-PG-1009 | Unable to check (no access to devices). 810-TT-1004 - cable entrance from the top. Necessary correction - cable entrance shall be from bottom | A | EM | HEC PI Design | Mr. Mariusz Celmer | 2022-07-06 | 2022-11-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00564 | 810.10 | 810-10-18 | 810 Unit | 810-FV-1012 | Damaged protective layer - necessary painting of the valve | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00565 | 810.10 | 810-10-18 | 810 Unit | 810-FV-1012 | Necessary tightening of fittings on the air regulator line | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00566 | 810.10 | 810-10-18 | 810 Unit | 810-FV-9161 | Necessary modification of the cable trays. There is currently a collision between the cable trays and the impulse line. | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00567 | 810.10 | 810-10-18 | 810 Unit | 810-FT-9161 | Transmitter has a non ATEX cap - necessary installation of the cap in the ATEX execution. | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00568 | 810.10 | 810-10-18 | 810 Unit | 810-FT-9161 | No ground wire connection | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00569 | 810.10 | 810-10-18 | 810 Unit | 810-FT-9161 | Necessary correction of the introduction of the cable into the protective enclosure - fixing the cable and improving the method of throttling | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00570 | 810.10 | 810-10-18 | 810 Unit | 860-FT-1001, 860-FT-1010, 860-FV-1001 | HEC informed during walkdown that these devices are not included in the subject subsystem - boundary need to be verified and clarified. | A | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-07-06 | 2022-09-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00571 | 810.10 | 810-10-18 | 810 Unit | 810-P0006A/B | Final Alignment for 810-P0006A/B not completed | A | ME | HEC ME Construction | Mr. Paweł Bialek | 2022-07-06 | 2022-08-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00572 | 810.10 | 810-10-18 | 810 Unit | 810-P0006A/B | Final Inspection for 810-P0006A/B not completed | A | ME | HEC ME Construction | Mr. Paweł Bialek | 2022-07-06 | 2022-08-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00573 | 810.10 | 810-10-18 | 810 Unit | 810PR-SW-1003 | Re-instatement to be done. | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-07-06 | 2022-07-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00574 | 810.10 | 810-10-18 | 810 Unit | 810-P0006A/B | Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00575 | 810.10 | 810-10-18 | 810 Unit | 810-P0006A/B | Motor Solo Run to be done/approved. | A | EL | HEC EL Construction | Mr. Michał Piotrowski | 2022-07-06 | 2022-08-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00576 | 810.10 | 810-10-18 | 810 Unit | 810PR-SW-1003 | Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00577 | 810.10 | 810-10-18 | 810 Unit | 810PR-SW-1004 | Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00578 | 810.10 | 810-10-18 | 810 Unit | 810WT-AV-1002 | Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00579 | 810.10 | 810-10-18 | 810 Unit | 810WT-LC-1001 | Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00580 | 810.10 | 810-10-18 | 810 Unit | 810WT-LC-1002 | Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00581 | 810.10 | 810-10-18 | 810 Unit | 810WT-LC-1002_R | Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00582 | 810.10 | 810-10-18 | 810 Unit | 810WT-LS-1002 | Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00583 | 810.10 | 810-10-18 | 810 Unit | 810WT-LS-1003 | Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00584 | 810.10 | 810-10-18 | 810 Unit | 810WT-OY-1001 | Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00585 | 810.10 | 810-10-18 | 810 Unit | 810WT-SW-1002 | Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00586 | 810.10 | 810-10-18 | 810 Unit | 810WT-SW-1003 | Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00587 | 810.10 | 810-10-18 | 810 Unit | 860CT-SW-1002 | Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00588 | 810.10 | 810-10-18 | 810 Unit | 810-FT-1012 | Cable Pulling, Cable termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-09-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00589 | 810.10 | 810-10-18 | 810 Unit | 810-FT-1012 (Hook-Up) | Installation w/Pressure Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-09-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00590 | 810.10 | 810-10-18 | 810 Unit | 810-FT-1012-P | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-09-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00591 | 810.10 | 810-10-18 | 810 Unit | 810-FT-9161 | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-09-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00592 | 810.10 | 810-10-18 | 810 Unit | 810-FT-9161 (Hook-Up) | Installation w/Pressure Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-09-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00593 | 810.10 | 810-10-18 | 810 Unit | 810-FT-9161-P | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-09-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00594 | 810.10 | 810-10-18 | 810 Unit | 810-FV-1012 (Hook-Up) | Installation w/Pressure Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00595 | 810.10 | 810-10-18 | 810 Unit | 810-FV-9161 (Hook-Up) | Installation w/Pressure Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00596 | 810.10 | 810-10-18 | 810 Unit | 810-LI-1001B | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00597 | 810.10 | 810-10-18 | 810 Unit | 810-LI-1021B | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00598 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1001 | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00599 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1001 | Calibration to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00600 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1001-P | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00601 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1020 | Calibration to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00602 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1021 | Calibration to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00603 | 810.10 | 810-10-18 | 810 Unit | 810-LT-1022 | Calibration to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00604 | 810.10 | 810-10-18 | 810 Unit | 810-PT-1010 | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-09-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00605 | 810.10 | 810-10-18 | 810 Unit | 810-PT-1010 (Hook-Up) | Installation w/Pressure Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-09-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00606 | 810.10 | 810-10-18 | 810 Unit | 810-PT-1010-P | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-09-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00607 | 810.10 | 810-10-18 | 810 Unit | 810-TE-1004 | Calibration to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00608 | 810.10 | 810-10-18 | 810 Unit | 810-TI-1002 | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-11-30 | Walkdown |  | 2022-11-24 | 2022-11-24 |  | V |  |  |  | RFC/RFSU
. | 00609 | 810.10 | 810-10-18 | 810 Unit | 810-TT-1002 | Calibration & Installation to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00610 | 810.10 | 810-10-18 | 810 Unit | 810-TT-1004 | Calibration to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00611 | 810.10 | 810-10-18 | 810 Unit | 860-FT-1001 | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00612 | 810.10 | 810-10-18 | 810 Unit | 860-FT-1001 (Hook-Up) | Installation w/Pressure Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00613 | 810.10 | 810-10-18 | 810 Unit | 860-FT-1001-P | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00614 | 810.10 | 810-10-18 | 810 Unit | 860-FT-1010 | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00615 | 810.10 | 810-10-18 | 810 Unit | 860-FT-1010-P | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00616 | 810.10 | 810-10-18 | 810 Unit | 860-FV-1001 | Cable Pulling, Cable Termination & Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00617 | 810.10 | 810-10-18 | 810 Unit | 860-FV-1001 (Hook-Up) | Installation w/Pressure Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00618 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A | Sand filter in polish translation at the nameplate to be corrected | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-12-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00619 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A | Housekeeping of the equipment is required specially on the top platform and top portion of the equipment body | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00620 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A | Touch up paint on gratings, grating supports, handrails and equipment body | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00621 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A | Scaffolding on the top platform to be removed | B | PA | HEC PA Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-07-26 | Walkdown | (CI works not finished) | 'Discipline' changed SS -> PA (2022-07-13) evidence attached |  |  | V |  |  |  | RFC/RFSU
. | 00622 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A | Ladder LD-01 foundation not yet available | B | AR | HEC CV Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-11-28 | Walkdown | 9/15: Disp. Changed (CV->AR) |  |  |  | V |  |  |  | RFC/RFSU
. | 00623 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A | Gratings to be align and clips to be tightened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00624 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A | Insulation cladding gap in between connection and around manhole M-3 to be sealed by mastic to avoid entrance of water inside | A | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-08-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00625 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A | PSV-3141 rust to be remove and touch up paint | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-07-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00626 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01B | Sand filter in polish translation at the nameplate to be corrected | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-12-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00627 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01B | Housekeeping of the equipment is required specially on the top platform and top portion of the equipment body | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00628 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01B | Touch up paint on gratings, grating supports, handrails and equipment body | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00629 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01B | Scaffolding on the top platform to be removed | B | PA | HEC PA Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-07-26 | Walkdown | (CI works not finished) | 'Discipline' changed SS -> PA (2022-07-13) evidence attached |  |  | V |  |  |  | RFC/RFSU
. | 00630 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01B | Ladder LD-01 foundation not yet available | B | AR | HEC CV Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-23 | Walkdown | 9/15: Disp. Changed (CV->AR) |  |  |  | V |  |  |  | RFC/RFSU
. | 00631 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01B | Gratings to be align and clips to be tightened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00632 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01B | Insulation cladding gap in between connection and around manhole M-3 to be sealed by mastic to avoid entrance of water inside | A | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-08-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00633 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01B | Cladding around Manhole M-3 need to be repair | A | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-08-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00634 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01B | PSV-3131 rust to be remove and touch up paint | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-07-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00635 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01B | Pipe support VS1 on line number 1213_810-6-WW-91204-B1A1-N-01 need to be fix and tight the U-bolt | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-07-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00636 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01C | Sand filter in polish translation at the nameplate to be corrected | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-12-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00637 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01C | Housekeeping of the equipment is required specially on the top platform and top portion of the equipment body | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00638 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01C | Touch up paint on gratings, grating supports, handrails and equipment body | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00639 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01C | Scaffolding on the top platform to be removed | B | PA | HEC PA Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-07-26 | Walkdown | (CI works not finished) | 'Discipline' changed SS -> PA (2022-07-13) evidence attached |  |  | V |  |  |  | RFC/RFSU
. | 00640 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01C | Ladder LD-01 foundation not yet available | B | AR | HEC CV Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-23 | Walkdown | 9/15: Disp. Changed (CV->AR) |  |  |  | V |  |  |  | RFC/RFSU
. | 00641 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01C | Gratings to be align and clips to be tightened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00642 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01C | Insulation cladding gap in between connection and around manhole M-3 to be sealed by mastic to avoid entrance of water inside | A | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-08-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00643 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01C | PSV-3121 rust to be remove and touch up paint | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-07-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00644 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01D | Sand Filter in polish translation at the nameplate to be corrected | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-12-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00645 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01D | Housekeeping of the equipment is required specially on the top platform and top portion of the equipment body | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00646 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01D | Touch up paint on gratings, grating supports, handrails and equipment body | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00647 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01D | Scaffolding on the top platform to be removed | B | PA | HEC PA Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-07-26 | Walkdown | (CI works not finished) | 'Discipline' changed SS -> PA (2022-07-13) evidence attached |  |  | V |  |  |  | RFC/RFSU
. | 00648 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01D | Ladder LD-01 foundation not yet available | B | AR | HEC CV Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-23 | Walkdown | 9/15: Disp. Changed (CV->AR) |  |  |  | V |  |  |  | RFC/RFSU
. | 00649 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01D | Gratings to be align and clips to be tightened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-09-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00650 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01D | Insulation cladding gap in between connection and around manhole M-3 to be sealed by mastic to avoid entrance of water inside | A | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-08-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00651 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01D | Pipe support VS1 on line number 1413_810-6-WW-91404-B1A1-N-01 need to be fix and tight the U-bolt | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-07-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00652 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01D | PSV-3111 rust to be remove and touch up paint | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-07-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00653 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-VSKID-1A | No nameplate attached on the valve skid | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00654 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-VSKID-1B | No nameplate attached on the valve skid | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00655 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-VSKID-1C | No nameplate attached on the valve skid | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00656 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-VSKID-1D | No nameplate attached on the valve skid | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00657 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-BL01A | Belt and its cover to be install and belt tensioning inspection to be conducted | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-08-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00658 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-BL01A | Flexible hose flange bolt need to be tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00659 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-BL01A | Install cover plate on the opening of the hole at the noise cover intended for flexible hose | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00660 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-BL01B | Belt and its cover to be install and belt tensioning inspection to be conducted | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-08-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00661 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-BL01B | Flexible hose flange bolt need to be tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00662 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-BL01B | Install cover plate on the opening of the hole at the noise cover intended for flexible hose | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-05 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00663 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A/B/C/D | The sample taking point (9101/3/5/7) shall be moved on PID accordingly after the PG. | B | EM | HEC MR Design | Mr. Slawomir Dyrda | 2022-07-06 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00664 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A/B/C/D | The CSC four inch valve shall be protected with a padlock. | A | COMM | HEC COMM | Mr. Slawomir Dyrda | 2022-07-06 | 2022-08-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00665 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A/B/C/D | Modify PID as there are three SG instead of 2 SG and one LG on each sand filter. | B | EM | HEC MR Design | Mr. Slawomir Dyrda | 2022-07-06 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00666 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-BL01A/B | Insert temporary gaskets on blowers outlet. | A | ME | HEC ME Construction | Mr. Slawomir Dyrda | 2022-07-06 | 2022-08-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00667 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-BL01A/B | Provide proof that top of the gooseneck downstream blowers is in fact 1 meter higher than top of sand filters vessels. | A | PI | HEC PI Construction | Mr. Slawomir Dyrda | 2022-07-06 | 2022-07-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00668 | 810.10 | 810-10-10 | Backwash Basin | 860-BA0002 | Provide proff that water discharging pipe inside of the basin is in fact 100mm higher than HHLL of the basin. | A | PI | HEC PI Construction | Mr. Slawomir Dyrda | 2022-07-06 | 2022-07-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00669 | 810.10 | 810-10-10 | Common | N/A | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-07-06 | 2023-04-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00670 | 810.10 | 810-10-10 | Common | N/A | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-06 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00671 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-FT-9110/9120/9130/9140 | Cables strained, cables not in the cable route, outside the routes. | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00672 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A/B/C/D | General comments, unscrewed air connections to the valves, there will be leaks | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00673 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A/B/C/D eg: 810-PT-0101 | General comment: Devices has a non ATEX cap - necessary installation of the cap in the ATEX execution. Unprotected housing of the device PT-0101 | A | EM | HEC MR Design | Mr. Bartosz Woźniak | 2022-07-06 | 2022-10-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00674 | 810.10 | 810-10-10 | Raw Water Treatment Shelter |  | No ground wire connection, it's cutted eg. TANK grounding | A | EL | HEC EL Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00675 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | Blowers | Pressure gauges on blowers without atex mark, but on the rest of the installation the marked. | A | EM | HEC MR Design | Mr. Bartosz Woźniak | 2022-07-06 | 2022-10-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00676 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | Blowers | Please explain why is the petlicer tube flattened? who is its producer? They should be look like photo. | A | EM | HEC MR Design | Mr. Bartosz Woźniak | 2022-07-06 | 2022-10-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00677 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A/B/C/D | Lack tag valves description on instrument air collectors | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00678 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-FT-9110/9120/9130/9140 | Why the cable for FT grounding ring are black? They should be green/yellow | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00679 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A/B/C/D | Still lack protection for sharp edge | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00680 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810 | Incomplete assembly on pressure gauges, loose valves, screws | A | EM | HEC MR Design | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00681 | 810.10 | 810-10-10 | Raw Water Treatment Shelter |  | General comment: Necessary tightening of the cable glands, ATEX plug, black cable, not ATEX, also not cheked properly 810-LT-9703. This device are present in Exi calculation Why sometoimes for LT NIVELCO devices use EXi bright blue cabel but sometimes black. The cabel are incorect as present in documentation with hook-up drwaing.V-HRI-R41-810-00000-00086_Instrument Hook-up Drawing_Z0 they shoul be ARMORED CABLE 1x1,5 bright blue | A | EM | HEC MR Design | Mr. Bartosz Woźniak | 2022-07-06 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00682 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810 | General comment: Lack cable tray cables routes on the structure, fastened to pipelines | A | EM | HEC MR Design | Mr. Bartosz Woźniak | 2022-07-06 | 2022-10-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00683 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | 810-X0001-U01A-D | Final Inspection to be done. | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-07-06 | 2022-08-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00684 | 810.10 | 810-10-10 | N/A | 810WT-PRA-1001 | Final Appearance Inspection to be done | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-06 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00685 | 810.10 | 810-10-10 | N/A | 810-AC-501 | Inspection for Hook-up / Leak Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00686 | 810.10 | 810-10-10 | N/A | 810-FT-9110 | Inspection for Cable Pulling / Test / Termination to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00687 | 810.10 | 810-10-10 | N/A | 810-FT-9120 | Inspection for Cable Pulling / Test / Termination to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00688 | 810.10 | 810-10-10 | N/A | 810-FT-9130 | Inspection for Cable Pulling / Test / Termination to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00689 | 810.10 | 810-10-10 | N/A | 810-FT-9140 | Inspection for Cable Pulling / Test / Termination to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00690 | 810.10 | 810-10-10 | N/A | 810-LV-1020 | Inspection for Calibration / Hook-up / Leak Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00691 | 810.10 | 810-10-10 | N/A | 810-XV-9117 | Inspection for Hook-up / Leak Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00692 | 810.10 | 810-10-10 | N/A | 810-XV-9118 | Inspection for Hook-up / Leak Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00693 | 810.10 | 810-10-10 | N/A | 810-XV-9127 | Inspection for Hook-up / Leak Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00694 | 810.10 | 810-10-10 | N/A | 810-XV-9128 | Inspection for Hook-up / Leak Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00695 | 810.10 | 810-10-10 | N/A | 810-XV-9137 | Inspection for Hook-up / Leak Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00696 | 810.10 | 810-10-10 | N/A | 810-XV-9138 | Inspection for Hook-up / Leak Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00697 | 810.10 | 810-10-10 | N/A | 810-XV-9147 | Inspection for Hook-up / Leak Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00698 | 810.10 | 810-10-10 | N/A | 810-XV-9148 | Inspection for Hook-up / Leak Test to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00699 | 810.10 | 810-10-10 | N/A | 810-PG-9101 | Inspection for Installation / Calibration to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00700 | 810.10 | 810-10-10 | N/A | 810-PG-9102 | Inspection for Installation / Calibration to be done | A | CI | HEC CI Construction | Mr. Bartosz Woźniak | 2022-07-06 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00701 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW01191‐01 | Pipeline not stable - shaking | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00702 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW01191‐01 | Support not fully resting on steel structure | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-08-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00703 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW01191‐01 | Hold down rope to be removed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00704 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW07191‐01 | Pipeline not stable - shaking | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00705 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW07191‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00706 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW07291‐01 | Pipeline not stable - shaking | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00707 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW07291‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00708 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW07391‐01 | Pipeline not stable - shaking | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00709 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW07391‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00710 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW60007‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00711 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW60007‐01 | Upper part of pipeline not stable - shaking with support | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00712 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW60007‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00713 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW60009‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00714 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐820SW60009‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00715 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐900SW00101‐02 | Limited access to valve | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00716 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐900SW00101‐02 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00717 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00002 | 810PR‐900SW00101‐02 | Plate on valve "Hydrogen Service" | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 |  | Walkdown | [8 empty] | RFC/RFSU
. | 00718 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐810SW18101‐01 | Pipeline not stable, line to be centered on steel structure, guides to be added | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2023-02-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00719 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐810SW18101‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00720 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐810SW60002‐01 | Pipeline not stable - shaking | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00721 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐810SW60002‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2023-03-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00722 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐810SW60003‐01 | Mastic on support cladding missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00723 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐810SW60003‐01 | Insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00724 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐810SW60003‐01 | Touch up painting | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00725 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐810SW60003‐01 | Bolt missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00726 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐820SW60003‐01 | Support (U-bolt) not tighted (nuts missing) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00727 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐820SW60003‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00728 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐820SW60003‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00729 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐820SW60004‐01 | Mastic on support clading missing or is not seal | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00730 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐820SW60004‐01 | Blind flange missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00731 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐820SW60004‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00732 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐820SW60004‐01 | Insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00733 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐820SW60004‐01 | Tape from bolts to be removed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00734 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐840SW01101‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00735 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐840SW01102‐01 | Mastic on support cladding missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00736 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐840SW01102‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00737 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐900SW00101‐01 | Support not resting on steel structure | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00738 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐900SW00101‐01 | Insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00739 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐900SW00101‐01 | Cladding on elbow not overlapping | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00740 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐900SW00101‐02 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00741 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐900SW00101‐02 | Support guides missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00742 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐900SW04109‐01 | Pipeline not stable - shaking | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2023-02-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00743 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐900SW04109‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00744 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐900SW05101‐01 | Insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00745 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐900SW05102‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00746 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐900SW05103‐01 | Pipeline tensioned by scaffolding - unable to check verticality up to scaffolding remove | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00747 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00004 | 810WS‐900SW05103‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00748 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810AV10101‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00749 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810AV10102‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00750 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810AV10103‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00751 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810LC00105‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00752 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810LC00105‐02 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00753 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810LC00105‐03 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00754 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810LS00104‐01 | Insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00755 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810LS00104‐02 | Insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00756 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810LS00104‐02 | Insulation not in line with pipeline routing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00757 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810OY14101‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00758 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810OY14102‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00759 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810OY20051‐01 | Line not stable - to be supported | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-09-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00760 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810OY20061‐01 | Line not stable - to be supported | A | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2022-09-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00761 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810OY20080‐01 | Line not stable - to be supported | A | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2022-09-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00762 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00111‐01 | Drawing info missing for flange connection | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00763 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00111‐01 | Instead of orifice intalled temporary gasket | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00764 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00111‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00765 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00113‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00766 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00113‐05 | Support guides missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00767 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00113‐05 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00768 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00113‐06 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00769 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00115‐01 | Pipeline touching sandwich wall | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-07-14 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00770 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00115‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00771 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00116‐01 | Painting tape to be removed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00772 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00116‐01 | Insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00773 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00117‐01 | Tape to be removed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00774 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00117‐01 | Insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00775 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00118‐01 | Tape to be removed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00776 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00118‐01 | Insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00777 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00119‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00778 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00119‐02 | Support SH guides installed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00779 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00119‐02 | Support SH guides installed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00780 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00119‐02 | 810-PG-1009, 810-TG-1015 limited access for take a readings - location at high | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 |  | Walkdown | [8 empty] | RFC/RFSU
. | 00781 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00119‐02 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00782 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00120‐01 | Secondary steel structure to be celeaned out | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-08-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00783 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00120‐01 | Pipline insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00784 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00120‐01 | Clarify if blind flange 'operate close' as per spec. | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00785 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00122‐01 | Stainless steel tank nozzle contaminated by rust | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00786 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW00123‐01 | Line not installed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-08-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00787 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW10101‐01 | Gap pipeline and U/G drain lines can be cause of splashes - suggestion to make a funnel | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00788 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW10102‐01 | Drain not in line with U/G drain line | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00789 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW14101‐01 | Stem tape to be removed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00790 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW14101‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00791 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW14102‐01 | Valve wheel missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00792 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW14102‐01 | Valve gearbox oriented south - to be turned | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00793 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW14102‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00794 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW14103‐01 | Support not indicated on drawing | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2022-12-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00795 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW14103‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00796 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60004‐01 | Support incomplete (counter nuts missing) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00797 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60004‐01 | Tape from bolts to be removed | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00798 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60004‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00799 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60005‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00800 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60007‐01 | Support guides missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00801 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60007‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00802 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60008‐01 | Support guides missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00803 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60008‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00804 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60009‐01 | Hoose connector missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00805 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60012‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00806 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60012‐01 | Pipeline not stable - shaking | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00807 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60012‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00808 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60013‐01 | Support not tighted | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00809 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60013‐01 | Tape to be removed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00810 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW60013‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00811 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW91001‐01 | Valve gearbox oriented north - to be turned | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00812 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW91001‐01 | Valve wheel missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00813 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW91001‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00814 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW91001‐02 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00815 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW91002‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00816 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW91003‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00817 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW91003‐01 | Support guides missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00818 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW91004‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00819 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐810SW93116‐01 | Elevation pass through pictogram missing | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00820 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐860SW00101‐01 | Support guides missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00821 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00005 | 810WT‐860SW00101‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00822 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐820SW02191‐01 | Mastic on support cladding missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00823 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐820SW02191‐01 | Pipline insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00824 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐820SW60005‐01 | Mastic on support cladding missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00825 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐820SW60005‐01 | Rusted bolts on flange connections | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00826 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐820SW60005‐01 | Pipline insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00827 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐820SW60006‐01 | Mastic on support cladding missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00828 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐820SW60006‐01 | Pipline insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00829 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐820SW60011‐01 | Pipeline not stable (shaking) | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00830 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐820SW60011‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00831 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐820SW60011‐02 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00832 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐820SW60011‐02 | No space for insulation - clash with cale tray support | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-07-14 | 2023-01-17 | Walkdown |  |  | 2023-01-16 |  | V |  |  |  | RFC/RFSU
. | 00833 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐820SW60011‐02 | Pipeline not stable (shaking) | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-14 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00834 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐820SW60012‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00835 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐900SW00101‐01 | Support not resting on steel structure | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00836 | 810.10 | 810-10-18 | EGAT‐HEC‐810‐PIP‐ISO‐00003 | 820BF‐900SW00101‐01 | Pipline insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00837 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW00101‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00838 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW00101‐02 | Insulation incomplete | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00839 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW00101‐03 | Valve gearbox incomplete painting | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00840 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW00101‐03 | Bottom part of valve gearbox corroded | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00841 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW00101‐03 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00842 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW00102‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00843 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW11101‐01 | Out of plumb | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-08-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00844 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW11101‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00845 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW60001‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00846 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW60001‐02 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00847 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW60001‐03 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00848 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW60002‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00849 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW60005‐01 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00850 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW60005‐02 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00851 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW60005‐03 | Pipline not insulated - to be done before winter season | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00852 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW60005‐03 | Out of plumb | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-07-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00853 | 810.10 | 810-10-18 | EGAT‐HEC‐860‐PIP‐ISO‐00001 | 860CT‐860SW60005‐03 | Pipeline close to sandwich wall/steel structure. No gap for insulation | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-14 | 2022-08-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00854 | 810.10 | 810-10-18 | 810 | Scrap | Scrap to be removed such as wire, cable and ETC. | A | EL | HEC EL Construction | Mr. Dariusz Wysocki | 2022-07-14 | 2022-08-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00855 | 810.10 | 810-10-18 | 810-ST0001 |  | Tank overflow discharge destination to be completed. | A | CV | HEC CV Construction | Mr. Sebastian Stępień | 2022-07-14 | 2022-08-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00919 | 810.10 | 810-10-10 | 810WT | 810WT-810SW00102-01 | Piping Insulation incomplete (Valve) | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00920 | 810.10 | 810-10-10 | 810WT | 810WT-810SW00101-01 | Piping Insulation incomplete (Valve) | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00921 | 810.10 | 810-10-10 | 810PR | 810PR-810SW00101-01 | Piping Insulation incomplete | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00922 | 810.10 | 810-10-10 | 810WT | 810WT-810WW91001-01 | Piping Insulation incomplete | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00923 | 810.10 | 810-10-10 | 810WT | 810WT-810WW91003-01 | Pipeline touching sandwich wall | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-07-20 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00924 | 810.10 | 810-10-10 | 810WT | 810WT-810WW91003-01 | Paint touch up for support guide to be done | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-07-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00925 | 810.10 | 810-10-10 | 810PR | 810PR-810WW00101-01 | Support not resting on steel structure | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-07-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00926 | 810.10 | 810-10-10 | 810PR | 810PR-810WW00101-01 | Piping Insulation incomplete | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00927 | 810.10 | 810-10-10 | 810WT | 810WT-810PRA91001-02 | Support guides missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-07-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00928 | 810.10 | 810-10-10 | 810WT | 810WT-810PRA91001-02 | Piping Insulation incomplete | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00929 | 810.10 | 810-10-10 | 810WT | 810WT-810PRA91002-01 | Pipeline touching sandwich wall | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-08-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00930 | 810.10 | 810-10-10 | 810WT | 810WT-810PRA91003-01 | Insulation not routed to sandwich wall | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00931 | 810.10 | 810-10-10 | 810WT | 810WT-810PRA91001-04 | Piping Insulation incomplete | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00932 | 810.10 | 810-10-10 | 810WT | 810WT-810PRA91001-04 | Cladding not overlapping, mastic missing. | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00933 | 810.10 | 810-10-10 | 810WT | 810WT-810RW91002-01 | Piping Insulation incomplete | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00934 | 810.10 | 810-10-10 | 810WT | 810WT-810RW91003-01 | Tag wire/plate to be removed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-07-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00935 | 810.10 | 810-10-10 | 810WT | 810WT-810RW91003-01 | Paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-07-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00936 | 810.10 | 810-10-10 | 810WT | 810WT-810RW91004-01 | Tag wire/plate to be removed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-07-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00937 | 810.10 | 810-10-10 | 810WT | 810WT-810RW91004-01 | Paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-07-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00938 | 810.10 | 810-10-10 | 810WT | 810WT-810RW91005-01 | Paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-07-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00939 | 810.10 | 810-10-10 | 810WT | 810WT-810RW91005-01 | Valve orientation to be changed for safer access | A | EM | HEC PI Design | Mr. Maciej Smalira | 2022-07-20 | 2022-09-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00940 | 810.10 | 810-10-10 | 810WT | 810WT-810RW91006-01 | Tag wire/plate to be removed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-07-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 00941 | 810.10 | 810-10-10 | 810WT | 810WT-810RW91006-01 | Paint touch up to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-07-20 | 2022-07-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01395 | 810.10 | 810-10-12 | 810-X0005 | 810-2''-CH-95002-C1FO-ET | Eletrical tracing missing | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-08-09 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01396 | 810.10 | 810-10-12 | 810-X0005 | EGAT-HEC-810-PRO-PID-00091A | Flange stud bolts to be tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-09 | 2022-08-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01397 | 810.10 | 810-10-12 | 810-X0005 | EGAT-HEC-810-PRO-PID-00091A | Calibration pot to be installed | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-09 | 2022-08-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01398 | 810.10 | 810-10-12 | 810-X0005 | EGAT-HEC-810-PRO-PID-00091A | Nameplates missing | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-09 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01399 | 810.10 | 810-10-12 | 810-X0005 | EGAT-HEC-810-PRO-PID-00091A | Internal cleaning and box-up to be done | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-09 | 2022-08-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01400 | 810.10 | 810-10-12 | 810-X0005 | EGAT-HEC-810-PRO-PID-00091A | Access to the skid (grating and step) to be provided | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-09 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01401 | 810.10 | 810-10-12 | 810-X0005 | EGAT-HEC-810-PRO-PID-00091A | Flange at TP-X0005-001 to be provided be tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-09 | 2022-08-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01402 | 810.10 | 810-10-12 | 810-X0005 | EGAT-HEC-810-PRO-PID-00091A | Loose U-bolts to be tightened in 4 locations. | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-09 | 2022-08-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01403 | 810.10 | 810-10-12 | 810-X0005 | EGAT-HEC-810-PRO-PID-00091A | Housekeeping to be done. | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-09 | 2022-08-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01404 | 810.10 | 810-10-12 | 810-X0005 | EGAT-HEC-810-PRO-PID-00091A | Valve downstream of the tank to relocated in P&ID | A | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-08-09 | 2022-09-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01405 | 810.10 | 810-10-12 | 810-X0005 | EGAT-HEC-810-PRO-PID-00091A | Hanging tags for PRVs missing | B | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-08-09 | 2022-11-09 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 01406 | 810.10 | 810-10-12 | 810-X0005 | EGAT-HEC-810-PRO-PID-00091A | Handle of manual valve is broken (to be replaced) | A | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-09 | 2022-09-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01407 | 810.10 | 810-10-12 | 810-X0005 | n/a | Piping sealing is missing on the building wall. | B | AR | HEC AR Construction | Ms. Paulina Bajer | 2022-08-09 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01408 | 810.10 | 810-10-12 | 810-X0005 | n/a | Final Inspection to be done | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-09 | 2022-08-11 | Walkdown |  | *Based on the Exception List |  |  | V |  |  |  | RFC/RFSU
. | 01409 | 810.10 | 810-10-12 | AB-810WT-CH-1002 | n/a | Air Blowing to be done | B | COMM | HEC COMM | Mr. Slawomir Dyrda | 2022-08-09 | 2022-08-25 | Walkdown |  | *Based on the Exception List |  |  | V |  |  |  | RFC/RFSU
. | 01410 | 810.10 | 810-10-12 | 810-FS-002 | n/a | Inspection for Pulling / Test / Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-09 | 2022-10-03 | Walkdown |  | *Based on the Exception List |  |  | V |  |  |  | RFC/RFSU
. | 01411 | 810.10 | 810-10-12 | Sand Filter Coagulant Dosing System | EGAT-HEC-810-PRO-PID-00091A | Provide yellow tag sticker for LCS EMERGENCY PUSH BOTTON at cover side written with Polish Language [ WYŁĄCZNIK AWARYJNY ] for all LCS and ES.. | B | EL | HEC EL Construction | Mr. Wojciech Chrzanowski | 2022-08-09 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01412 | 810.10 | 810-10-12 | Sand Fileter Coagulant Dosing System | EGAT-HEC-810-PRO-PID-00091A | Cable tray cleaning for coagulant dosing system | B | EL | HEC EL Construction | Mr. Wojciech Chrzanowski | 2022-08-09 | 2022-08-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01413 | 810.10 | 810-10-12 | Sand Fileter Coagulant Dosing System | EGAT-HEC-810-PRO-PID-00091A | Unwanted earthing cables to be removed. | B | EL | HEC EL Construction | Mr. Wojciech Chrzanowski | 2022-08-09 | 2022-08-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01414 | 810.10 | 810-10-12 | 810WT | 810WT-810CH09102-01 | Paint on nuts to be removed | A | PI | HEC PI Construction | Mr. Emil Wróblewski | 2022-08-09 | 2022-08-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01415 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-01 | Rusted bolts and nuts | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-08-09 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01416 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-01 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Emil Wróblewski | 2022-08-09 | 2022-09-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01417 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-01 | Location of flange and wall does not match on iso drawing. Asbuilt drawing to be provided | B | EM | HEC PI Design | Mr. Emil Wróblewski | 2022-08-09 | 2022-12-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01418 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Emil Wróblewski | 2022-08-09 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01419 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-02 | Rusted bolts and nuts | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-08-09 | 2022-08-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01420 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-02 | Tag wire to be removed | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-08-09 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01421 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-02 | Paint touch up for support to be done (Shoe and guides) | B | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-08-09 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01422 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-02 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Emil Wróblewski | 2022-08-09 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01423 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-03 | Rusted bolts and nuts | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-08-09 | 2022-08-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01424 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-03 | Vent hole cover to be removed | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-08-09 | 2022-08-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01425 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-03 | Line not installed as per latest revision drawing. Item no.1 (Tee) and Item no.4 (Blind flange) not installed. | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-08-09 | 2022-09-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01426 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-03 | Paint touch up for support to be done (Shoe and guides) | B | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-08-09 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01427 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-03 | Paint touch up be done | B | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-08-09 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01428 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95001-03 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Emil Wróblewski | 2022-08-09 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01429 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95002-01 | Rusted bolts and nuts | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-08-09 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01430 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95002-01 | Tape from bolts to be removed | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-08-09 | 2022-08-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01431 | 810.10 | 810-10-12 | 810WT | 810WT-810CH95002-01 | Piping insulation missing | B | IN | HEC IN Construction | Mr. Emil Wróblewski | 2022-08-09 | 2022-12-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01432 | 810.10 | 810-10-12 | 810-X0005 | n/a | 810-LT-9501 Tank level Nivelco missing ATEX gland plug | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-09 | 2022-08-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01433 | 810.10 | 810-10-12 | 810-X0005 | n/a | 810-FS-002 missing instalation, device, ect | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-09 | 2022-09-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01434 | 810.10 | 810-10-12 | 810-X0005 | n/a | Lack initial ATEX inspection | B | PER | HEC permit team | Mr. Tomasz Jozel | 2022-08-09 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01435 | 810.10 | 810-10-12 | 810-X0005 | n/a | General comments unacceptable, by Owner there are no cable routes, cables from transmitters are suspended by cable tie to the process lines, pipelines. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-09 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 01436 | 810.10 | 810-10-12 | 810-X0005 | n/a | General comments, lack for each pressure transmitter plug for manifold, drain or vent. They shall be confimed with the HOOK-UP. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-09 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01437 | 810.10 | 810-10-12 | 810-X0005 | n/a | General comments for PG. According datasheet V-HRI-R41-810-00000-00082_Instrument Data Sheet_Z1 ambiguous information which version of pressure gauge corresponds exactly with version and mode on instalation. 810-PG-9513/9523 at site is P731 but in DTR ? Which one are correct? | A | EM | HEC MR Design | Mr. Tomasz Jozel | 2022-08-09 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01438 | 810.10 | 810-10-12 | 810-X0005 | n/a | For pressure transmiter E + H We expect certification for gland plugs and cable glands, please provide the certificate for plug. Lack information when scaning QR code. In owner opinion on plug are present only Exd and size, but where is information with acreditation body. | A | EM | HEC MR Design | Mr. Tomasz Jozel | 2022-08-09 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01439 | 810.10 | 810-10-12 | 810-X0005 | n/a | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-08-09 | 2023-04-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01440 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | EGAT-HEC-900-ELE-DLP-01005_1 | Provide PVC pipe sleeve at compartment cable entry side to protect cable from sharp edge for 810-X0001-MBL01A & B | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-07-05 | 2022-07-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 01441 | 810.10 | 810-10-10 | Raw Water Treatment Shelter | EGAT-HEC-900-ELE-DLP-01005_1 | Provide yellow tag sticker for LCS Emergency Push Botton at cover side written with polish language for 810-X0001-MBL01A & B | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-07-05 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02676 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003 A/B | 810-P0003 A/B: Final Inspection to be done | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2022-10-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02677 | 810.10 | 810-10-34 | Recycle Water basin | 810WT-WW-1002 (IN) | 810WT-WW-1002 (IN): Final Inspection to be done | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02678 | 810.10 | 810-10-34 | Recycle Water basin | 810-FT-1006 | 810-FT-1006: Inspection for Installation / Pulling / IR Test / Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-10-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02679 | 810.10 | 810-10-34 | Recycle Water basin | 810-LT-1012 | 810-LT-1012: Inspection for Installation / Pulling / IR Test / Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-10-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02680 | 810.10 | 810-10-34 | Recycle Water basin | 810-LT-1013 | 810-LT-1013: Inspection for Installation / Pulling / IR Test / Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-10-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02681 | 810.10 | 810-10-34 | Recycle Water basin | 810-PG-1003A | 810-PG-1003A: Inspection for Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02682 | 810.10 | 810-10-34 | Recycle Water basin | 810-PG-1003B | 810-PG-1003B: Inspection for Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02683 | 810.10 | 810-10-34 | Recycle Water basin | 810-FV-1006 | 810-FV-1006: Inspection for Installation / Pulling / IR Test / Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02684 | 810.10 | 810-10-34 | Recycle Water basin | 810-LV-1012 | 810-LV-1012: Inspection for Installation / Pulling / IR Test / Termination / Hookup / Leak Test | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02685 | 810.10 | 810-10-34 | Recycle Water basin | 810-LV-1012 | 810-LV-1012: valve stem missing on bypass line | A | PI | HEC PI Construction | Mr. Łukasz Jekel | 2022-09-01 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02686 | 810.10 | 810-10-34 | Recycle Water basin | EGAT-HEC-810-PRO-PID-00071 | Sampling point SN-8107: unable to take a sample | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-01 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02687 | 810.10 | 810-10-34 | Recycle Water basin | EGAT-HEC-810-PRO-PID-00071 | HSCN-001: missing chain | B | PI | HEC PI Construction | Mr. Jaroslaw Pykosz | 2022-09-01 | 2022-09-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02688 | 810.10 | 810-10-34 | Recycle Water basin | EGAT-HEC-810-PRO-PID-00071 | missing support on vent line (810-3''-AV-07101-B1A1-N) | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-01 | 2022-09-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02689 | 810.10 | 810-10-34 | Recycle Water basin | EGAT-HEC-810-PRO-PID-00071 | Unable to operate pump vent valve (P0003A/B) - collission with insulation of pump discharge line | A | EM | HEC MR Design | Mr. Łukasz Jekel | 2022-09-01 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02690 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003A | "Stop" label on Local Panel of 810-P0003A. | B | EL | HEC EL Construction | Mr. Łukasz Jekel | 2022-09-01 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02691 | 810.10 | 810-10-34 | Recycle Water basin | 810-3''-WW-07104-B1A1-ET | Insulation missing (line no. 810-3''-WW-07104-B1A1-ET) | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-09-01 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02692 | 810.10 | 810-10-34 | Recycle Water basin | 810-3''-WW-07104-B1A1-ET | ET missing (line no. 810-3''-WW-07104-B1A1-ET) | B | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-09-01 | 2023-01-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02693 | 810.10 | 810-10-34 | Recycle Water basin | Common | Wet insulation to be replaced. | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-09-01 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02694 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003A/B | Insulation to be completed | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02695 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003A/B | House keeping to be done around the equipment | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2022-10-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02696 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003A/B | Jack srew to be removed and apply silicon on bolts holes | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02697 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003A/B | Touch up paint on motors and protective mesh grills | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2022-10-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02698 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003A/B | Basin access to be provided in order to check the bottom part of the pumps | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2022-10-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02699 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003A/B | Birds screen to be cleaned and touch up on the welded area | B | PA | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02700 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003A/B Basin | Permanent quick opening type cover to be provided refer to EGAT-HEC-810-PRO-PID-00071 Rev.02 | A | CV | HEC CV Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02701 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003A/B | Cable tray support to be fixed and concrete support foundation to be finished at south side area of the pump 810-P0003A | C | EL | HEC EL Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02702 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003A/B | Finishing touch required on all pipe supports concrete foundation | C | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02703 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003A/B | Scaffold around the pumps and basin to be removed | B | AR | HEC AR Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02704 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003A/B | Protective mesh grills to be repaired (proper bend, teared out bolt holes to repair) and missing bolts to be provided | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02705 | 810.10 | 810-10-34 | Recycle Water basin | 810-P0003A/B | Valves VG3C12H thread protection during painting shall be removed | A | PA | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2022-09-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02706 | 810.10 | 810-10-34 | Recycle Water basin | Common | Area not prepared for Walk down - house keeping required - existing scafolding - temporary protection (scafolding elements) block access to the interior of the basin | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-01 | 2022-10-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02707 | 810.10 | 810-10-34 | AUX/810-P0003A/B | 810-FT-1006 | Power and I&C cales not connected to the flowmeter 810-FT-1006 | A | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-01 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02708 | 810.10 | 810-10-34 | AUX/810-P0003A/B | 810-PG-1003A/B | Hook up connection of pressure gauge to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-28 |  | V |  |  |  | RFC/RFSU
. | 02709 | 810.10 | 810-10-34 | AUX/810-P0003A/B | 810-PG-1003A/B | Provide cable tray for the capillary tube | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-11-18 | Walkdown |  | 2022-11-18 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 02710 | 810.10 | 810-10-34 | AUX/810-P0003A/B | 810-FT-1006 | Power nad signal cable ends are not properly protected from atmospheric conditions - water present underneath the tape. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-10-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02711 | 810.10 | 810-10-34 | AUX/810-P0003A/B | 810-LT-1012/1013 | Length of nozzle for level transmitter to be verified | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-12-05 | Walkdown |  |  | 2022-12-02 |  | V |  |  |  | RFC/RFSU
. | 02712 | 810.10 | 810-10-34 | AUX/810-P0003A/B | 810-LT-1013 | The blind plug & bonding ground cable of level transmitter should be tightened properly | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02713 | 810.10 | 810-10-34 | AUX/810-P0003A/B | General | Provide grommet for the edge of cable tray | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02714 | 810.10 | 810-10-34 | AUX/810-P0003A/B | 810-FT-1006/FV-1006/LV-1012 | The cable of flow transmitter & control valve is not terminated | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-01 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02715 | 810.10 | 810-10-34 | AUX/810-P0003A/B | 810-FV-1006/LV-1012 | Heat tracing cable is not enough to covered the heat on the body of control valve,To be verified | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-09-01 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02716 | 810.10 | 810-10-34 | AUX/810-P0003A/B | 810-FV-1006/LV-1012 | Cable ends are not properly protected from atmospheric conditions - water present underneath the tape. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-09-01 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02717 | 810.10 | 810-10-34 | AUX/810-P0003A/B | General | Initial ATEX inspection | B | PER | HEC permit team | Owner Maintenance team | 2022-09-01 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02718 | 810.10 | 810-10-34 | Recycle Water basin | EGAT-HEC-810-PRO-PID-00071 | Motor earthing cable to be tigntned (Tag no:- 810-MP0003A & B) | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-01 | 2023-01-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02719 | 810.10 | 810-10-34 | Recycle Water basin | EGAT-HEC-810-PRO-PID-00071 | Power Cable Gland to be tightned at motor side (Tag no:- 810-MP0003A & B) | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-01 | 2022-09-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02720 | 810.10 | 810-10-34 | Recycle Water basin | EGAT-HEC-810-PRO-PID-00071 | Motor Cleaning to be done (Tag no:- 810-MP0003A & B) | B | ME | HEC ME Construction | Mr. Arkadiusz Tryniszewski | 2022-09-01 | 2022-10-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02721 | 810.10 | 810-10-34 | Recycle Water basin | EGAT-HEC-810-PRO-PID-00071 | LCS Cleaning and to be done and Spare holes blind plug to be provided (Tag no:- 810-MP0003A & B) | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-01 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02722 | 810.10 | 810-10-34 | Recycle Water basin | EGAT-HEC-810-PRO-PID-00071 | Provide yellow tag sticker for LCS EMERGENCY PUSH BOTTON at cover side written with Polish Language [ WYŁĄCZNIK AWARYJNY ] for all LCS and ES.. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-01 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02723 | 810.10 | 810-10-34 | Recycle Water basin | EGAT-HEC-810-PRO-PID-00071 | Conduit sealing to be done | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-01 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 02724 | 810.10 | 810-10-34 | Recycle Water basin | EGAT-HEC-810-PRO-PID-00071 | Cable tag to be provided for entry and exit of the conduits | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-01 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03796 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061 | Missing initial ATEX inspection for instruments. | B | PER | HEC permit team | Mr. Tomasz Jozel | 2022-08-24 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03797 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061 | X0003-X03B Cable tray covers should be added, all the cables have to be protected. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03798 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061 | XV-9352 Grounding to be tightened. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03799 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061 | XV-9351 Grounding to be tightened. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03800 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061 | XV-9351 Plugs to be tightened. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03801 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061 | X0003-X03A Cable tray covers should be added, all the cables have to be protected. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03802 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061 | PS-9301, FS-9302, LS-9304 Tags missing, and unacceptable radius cable bend. | A | EM | HEC MR Design | Owner Maintenance team | 2022-08-24 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03803 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061 | FS-9302 Cable connection to be fixed, the cable bend at this angle and protection at the connection point have to be added. | A | EM | HEC MR Design | Owner Maintenance team | 2022-08-24 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03804 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061 | LT-9303 Cable is not in the Ex standard, have to be replaced, ground cable to be added, blind plugs have to be verified. | A | EM | HEC MR Design | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03805 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061 | PT-9311 bling plug Ex standard has to be verified | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03806 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061 | PT-9321 bling plug Ex standard has to be verified. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03807 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061A | No access to LT-9314 on 81-X0003-X01A and LT-9324 on 81-X0003-X01B | B | ME | HEC ME Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-22 | Walkdown |  | change category from A to B |  |  | V |  |  |  | RFC/RFSU
. | 03808 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061A | XV-9322 Tighten mounting , tubing to be done, | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-02 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 03809 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061A | XV-9324 Tighten mounting , tubing to be done, | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03810 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061B | no pressure gauge PG-9331, PG-9341, PG-9332, PG-9342 | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-09-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03811 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061B | PT-9333 tubing, cable pulling to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03812 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061B | FT-9334 no access to sensor | B | ME | HEC ME Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-22 | Walkdown |  | change category from A to B |  |  | V |  |  |  | RFC/RFSU
. | 03813 | 810.10 | 810-10-32 | Thickener Package | EGAT-HEC-810-PRO-PID-00061A | AT-9312 No Access | B | ME | HEC ME Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-22 | Walkdown |  | change category from A to B |  |  | V |  |  |  | RFC/RFSU
. | 03814 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | LT-9205 No access. | B | ME | HEC ME Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-22 | Walkdown |  | change category from A to B |  |  | V |  |  |  | RFC/RFSU
. | 03815 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | PG-9221, PG-9222, PG-9231, PG-9232 Gauges missing. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03816 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | FT-9221 Missing cable grommet for cable tray, loose cables on the sensing device. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-09 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 03817 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | PG-9241, PG-9242, PG-9251, PG-9252 Gauges missing. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03818 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | FT-9241 Cables should not touch the pipeline, and cable tray should be added. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03819 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | XV-9891 bling plug have to be replaced with Ex blind plugs, cable routing to be corrected. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03820 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | LG-R-9891 pipeline touch level gauge | B | ME | HEC ME Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03821 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | PT-9894 bling plug have to be replaced with Ex blind plugs. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03822 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | PT-9895 bling plug have to be replaced with Ex blind plugs. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03823 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | XV-9892 Missing grommet for cable tray, cable missing tag number. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03824 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | FI-9893 tag number is wrong (9839), bling plug have to be replaced with Ex blind plugs, vents to be tightened, thermostat to be screwed on. | A | CI | HEC CI Construction | Owner Maintenance team | 2022-08-24 | 2022-12-12 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 03825 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | LT-9893 bling plug have to be replaced with Ex blind plugs, cable routing to be corrected. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03826 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | AT-9896 No access, mistake in enclosure name label "?" to be replaced with "Ś" | A | EM | HEC MR Design | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03827 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | XZS-9261 Cable can't touch the pipeline. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03828 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | XZS-9262 Cable can't touch the pipeline. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03829 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | LT-9265 Cable can't touch the pipeline. | A | CI | HEC CI Construction | Owner Maintenance team | 2022-08-24 | 2022-12-16 | Walkdown |  |  | 2022-12-12 |  | V |  |  |  | RFC/RFSU
. | 03830 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | XZS-9264 Grounding to be done, bling plug have to be replaced with Ex blind plugs. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03831 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | PG-9282 pointer bellow zero | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03832 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | PT-9271 missing cable tag | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03833 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | PT-9271 bling plug have to be replaced with Ex blind plugs, cable tray to be added. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03834 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | PT-9281 bling plug have to be replaced with Ex blind plugs, cable tray to be added. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03835 | 810.10 | 810-10-32 | Thickener Package | V-HRI-R41-810-00000-90101 | PT-9291 bling plug have to be replaced with Ex blind plugs, cable tray to be added. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03836 | 810.10 | 810-10-32 | Thickener Package area |  | Final Inspection for 810-X0003 to be done | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03837 | 810.10 | 810-10-32 | Thickener Package area |  | 810WT-CH-1010: re-instatement (after Hydro) to be done | A | PI | HEC PI Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-10-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03838 | 810.10 | 810-10-32 | Thickener Package area |  | 810-X0003-P01A/B: Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Krzysztof Nolbert | 2022-08-24 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03839 | 810.10 | 810-10-32 | Thickener Package area |  | 810WT-WW-1011: Final Apperance Inspection to be done | C | IN | HEC IN Construction | Mr. Krzysztof Nolbert | 2022-08-24 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03840 | 810.10 | 810-10-32 | Thickener Package area |  | Motor Solo Run for 810-X0003-MX02A to be done | A | EL | HEC EL Construction | J.W.JEONG | 2022-08-24 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03841 | 810.10 | 810-10-32 | Thickener Package area |  | Motor Solo Run for 810-X0003-MX02B to be done | A | EL | HEC EL Construction | J.W.JEONG | 2022-08-24 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03842 | 810.10 | 810-10-32 | Thickener Package area |  | LP.810-X0003-MX02A: Cable Termination & Test to be done | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-24 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03843 | 810.10 | 810-10-32 | Thickener Package area |  | LP.810-X0003-MX02B: Cable Termination & Test to be done | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-24 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03844 | 810.10 | 810-10-32 | Thickener Package area |  | LP.810-X0003-X03/LCP/UPS: Cable Termination & Test to be done | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-24 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03845 | 810.10 | 810-10-32 | Thickener Package area |  | C.810-X0003-MX02A/CS: Cable Termination & Test to be done | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-24 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03846 | 810.10 | 810-10-32 | Thickener Package area |  | C.810-X0003-MX02B/CS: Cable Termination & Test to be done | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-24 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03847 | 810.10 | 810-10-32 | Thickener Package area |  | 810-XV-9321: Inspection for Installation / Pulling / IR Test / Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03848 | 810.10 | 810-10-32 | Thickener Package area |  | 810-XV-9322: Inspection for Installation / Pulling / IR Test / Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03849 | 810.10 | 810-10-32 | Thickener Package area |  | 810-LT-9314: Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03850 | 810.10 | 810-10-32 | Thickener Package area |  | 810-LT-9324: Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03851 | 810.10 | 810-10-32 | Thickener Package area |  | 810-AT-9312: Inspection for Calibration / Installation / Pulling / IR Test / Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03852 | 810.10 | 810-10-32 | Thickener Package area |  | 810-PSV-9331: Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03853 | 810.10 | 810-10-32 | Thickener Package area |  | 810-PSV-9341: Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03854 | 810.10 | 810-10-32 | Thickener Package area |  | 810-PG-9331: Inspection for Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03855 | 810.10 | 810-10-32 | Thickener Package area |  | 810-PG-9332: Inspection for Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03856 | 810.10 | 810-10-32 | Thickener Package area |  | 810-PG-9341: Inspection for Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03857 | 810.10 | 810-10-32 | Thickener Package area |  | 810-PG-9342: Inspection for Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03858 | 810.10 | 810-10-32 | Thickener Package area |  | 810-PT-9333: Inspection for Installation / Pulling / IR Test / Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03859 | 810.10 | 810-10-32 | Thickener Package area |  | 810-FT-9334: Inspection for Installation / Pulling / IR Test / Termination | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03860 | 810.10 | 810-10-32 | Thickener Package area |  | 810-XV-9351: Inspection for Calibration / Installation / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03861 | 810.10 | 810-10-32 | Thickener Package area |  | 810-XV-9352: Inspection for Calibration / Installation / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03862 | 810.10 | 810-10-32 | Thickener Package area |  | 810-XV-9362: Inspection for Calibration / Installation / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03863 | 810.10 | 810-10-32 | Thickener Package area |  | 810-XV-9361: Inspection for Calibration / Installation / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03864 | 810.10 | 810-10-32 | Thickener Package area |  | 810-BPV-9381: Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-24 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03865 | 810.10 | 810-10-32 | Thickener Package area |  | General comment: Electrical tracing missing | B | EL | HEC EL Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03866 | 810.10 | 810-10-32 | Thickener Package area |  | General comment: Insulation missing | C | IN | HEC IN Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03867 | 810.10 | 810-10-32 | Thickener Package area |  | No access to upper part of thickener. Unable to check. Separate walk down required. | A | SS | HEC SS Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03868 | 810.10 | 810-10-32 | Thickener Package area |  | Incorrect tag number for turbidity analyzer - inconsistency with P&ID (9312). | B | EM | HEC MR Design | Mr. Andrzej Przechrzta | 2022-08-24 | 2023-01-09 | Walkdown |  |  | 2023-01-05 |  | V |  |  |  | RFC/RFSU
. | 03869 | 810.10 | 810-10-32 | Thickener Package area |  | Line not connected to turbidity analyzer | A | CI | HEC CI Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-11-30 | Walkdown |  | 2022-11-29 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 03870 | 810.10 | 810-10-32 | Thickener Package area |  | Sampling point 9301, 9302 - discharge line to be shortened (unable to take a sample) | A | PI | HEC PI Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-09-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03871 | 810.10 | 810-10-32 | Thickener Package area |  | Missing blind nozzle upstream XV-9312 and XV-9322 on P&ID. | B | PI | HEC PI Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03872 | 810.10 | 810-10-32 | Thickener Package area |  | Missing coupling on HSCN 005, HSCN 004 | A | PI | HEC PI Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-09-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03873 | 810.10 | 810-10-32 | Thickener Package area |  | Plug on drain valves to be corrected into flange on P&ID | B | PI | HEC PI Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03874 | 810.10 | 810-10-32 | Thickener Package area |  | Missing drain valves upstream XV-9361 and XV-9351 on P&ID. | B | PI | HEC PI Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-09-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03875 | 810.10 | 810-10-32 | Thickener Package area |  | Bolts to be tightened on water outlet line from centrifuge. | A | PI | HEC PI Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-09-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03876 | 810.10 | 810-10-32 | Thickener Package area |  | Missing nameplates on centrifuges. | C | ME | HEC ME Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03877 | 810.10 | 810-10-32 | Thickener Package area |  | Safety issue: space and height difference between centrifuge and platform is too big, dangerous for stuff. | B | EM | HEC MR Design | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03878 | 810.10 | 810-10-32 | Thickener Package area |  | Misssing anti acid coating for catch basin. | B | AR | HEC CV Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-11-09 | Walkdown |  | Changed category from A to B |  |  | V |  |  |  | RFC/RFSU
. | 03879 | 810.10 | 810-10-32 | Thickener Package area |  | Pressure regulator between block valve and solenoid valve to be shown on P&ID. | B | EM | HEC MR Design | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03880 | 810.10 | 810-10-32 | Thickener Package area |  | Missing tag labels for PRV 9311 and PRV 9321. | C | ME | HEC ME Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2023-06-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03881 | 810.10 | 810-10-32 | Thickener Package area |  | Safety issue: vent line from storage tank to be located in safe location. | A | PI | HEC PI Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03882 | 810.10 | 810-10-32 | Thickener Package area |  | Tag labels for PG 9312 and 9322 to be switched. | B | CI | HEC CI Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-11-10 | Walkdown |  |  | 2022-11-09 |  | V |  |  |  | RFC/RFSU
. | 03883 | 810.10 | 810-10-32 | Thickener Package area |  | 810-1 1/2"-CH-93118-N1A1-N to be directed to catch basin pit. | A | PI | HEC PI Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-09-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03884 | 810.10 | 810-10-32 | Thickener Package area |  | Tie in point no. X0003 installed on wrong line. | A | PI | HEC PI Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-09-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03885 | 810.10 | 810-10-32 | Thickener Package area | 810-SHT-CC-100 / Raw water Treatment shelter | Safety issue: nails inside basin and between centrifuge and west wall. | A | AR | HEC AR Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2022-10-17 | Walkdown | 2022-10-05: Disp. CV-> AR |  |  |  | V |  |  |  | RFC/RFSU
. | 03886 | 810.10 | 810-10-32 | Thickener Package area |  | House keeping to be done | B | PI | HEC PI Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03887 | 810.10 | 810-10-32 | Thickener Package area |  | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Mr. Andrzej Przechrzta | 2022-08-24 | 2023-04-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03888 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-P01A | Touch up painting on the pump | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03889 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-P01A | House keeping around the equipment | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03890 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-P01A | Drain line shall be free from any debris | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03891 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-P01B | Touch up painting on the pump | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03892 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-P01B | House keeping around the equipment | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03893 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-P01B | Drain line shall be free from any debris | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03894 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-X01A | Access ladder to be installed - walkdown inspection to be repeated in scope of Thickener (810-X0003-X01A/B) because lack of access. | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03895 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-X01A | Final Inspection to be done | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03896 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-X01B | Access ladder to be install | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03897 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-X01B | Final Inspection to be done | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03898 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-X03A | Expansion joint needs to be tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-09-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03899 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-X03A | Nameplate missing for the centrifuge | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2023-03-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03900 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-X03B | Expansion joint needs to be tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-09-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03901 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-X03B | Nameplate missing for the centrifuge | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2023-03-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03902 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-X03B | Underneath platform structure needs to be clean and touch up | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03903 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-ST01 | Tank nameplate missing | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03904 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-ST01 | Pumps nameplate missing | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03905 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-ST01 | Passivation required inside the tank | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-09-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03906 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-ST01 | Calibration pot valves handwheel (BA-93104 and BA-93107) orientation to be reviewed by Engineering | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03907 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-ST01 | Permanent blind to be installed at 810-1"-CH-93116-N1A1-N/B2 line | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2022-09-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03908 | 810.10 | 810-10-32 | Thickener Package area | 810-X0003-ST01 | Pipe support PS-10 section3 of framework clashes the pipe line 810-3/4"-SW-93116-B1A1-N | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-24 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03909 | 810.10 | 810-10-32 | Thickener |  | Acces to the equipment (loading shute) is not according to Standards - EN-PN 14 122-2 Machines Safety , Permanent access to the equipment, 4.1.2 b - EN-PN 14 122-3 Machines Safety , Stairs … 5.7 | C | EM | HEC MR Design | Mr. Artur Szczelina | 2022-08-24 | 2023-06-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03910 | 810.10 | 810-10-32 | Thickener |  | There are no visible description at equipment, switches, etc. The operator at control pannel should know which equipment he want to switch on/off. | A | EM | HEC MR Design | Mr. Artur Szczelina | 2022-08-24 | 2022-12-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03911 | 810.10 | 810-10-32 | Thickener |  | Safety switches do not meet the Machinery Directive 06/42 / EC- Polish law, Ordinance of the Ministry of Economy of October 21, 2008 in clause 1.2.4.3 "The emergency stop device must: be equipped with CLEARLY RECOGNIZABLE, VISIBLE and QUICKLY ACCESSIBLE controls." Pomps MP02, MP01 – safety switches are not visible and quickly accessible Polymer Dissolving Unit - safety switch not qickly accessible. | C | EM | HEC EL Design | Mr. Artur Szczelina | 2022-08-24 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03912 | 810.10 | 810-10-32 | Thickener |  | Access to valve, flowmeter and upper service platform are not possible | A | SS | HEC SS Construction | Mr. Krzysztof Nolbert | 2022-08-24 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03913 | 810.10 | 810-10-32 | Thickener |  | House keeping | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-08-24 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03914 | 810.10 | 810-10-32 | Thickener |  | Pump's motors not grounded | A | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2022-08-24 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03915 | 810.10 | 810-10-32 | Thickener |  | Power cables not connected | A | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2022-08-24 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03916 | 810.10 | 810-10-32 | Thickener |  | Not used pipe ends (blue painted) not plugged | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-08-24 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03917 | 810.10 | 810-10-32 | Polymer dissolving tank |  | temporary flange at tank draining line | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-08-24 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03918 | 810.10 | 810-10-32 | Centrifuges |  | Pipe not fixed to the steel structure | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-08-24 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 03919 | 810.10 | 810-10-32 | Centrifuges |  | Bolts at the flanges under centrifuges are not fixed | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-08-24 | 2022-09-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04126 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007-P01A/B/C | Final Inspection | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04127 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810WT-CH-1005 | Final Inspectio for Insuatlion | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04128 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810WT-CH-1006 | Final Inspectio for Insuatlion | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04129 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810WT-CH-1009 | Final Inspectio for Insuatlion | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04130 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-BPV-9711 | Inspection for Calibration / Installation | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04131 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-BPV-9712 | Inspection for Calibration / Installation | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04132 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | EGAT-HEC-810-PRO-PID-00091B | Missing pressure regulator on SW line between globe valve and solenoid valve on P&ID. | B | CI | HEC CI Construction | Ms. Małgorzata Juszczyk | 2022-08-30 | 2023-01-20 | Walkdown |  |  | 2022-12-30 |  | V |  |  |  | RFC/RFSU
. | 04133 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | EGAT-HEC-810-PRO-PID-00091B | Missing hanging tag for PRVs. | B | CI | HEC CI Construction | Ms. Małgorzata Juszczyk | 2022-08-30 | 2022-11-23 | Walkdown |  | 2022-11-18 | 2022-11-18 |  | V |  |  |  | RFC/RFSU
. | 04134 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | EGAT-HEC-810-PRO-PID-00091B | Missing package nameplate. | B | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2022-08-30 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04135 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | EGAT-HEC-810-PRO-PID-00091B | End blind missing on 1" connection | A | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2022-08-30 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04136 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | EGAT-HEC-810-PRO-PID-00091B | No access to upper part of clarifier. | A | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2022-08-30 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04137 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007-P01A | Touch up panting on motor | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04138 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007-P01A | House keeping on the entire skid | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2023-03-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04139 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007-P01A | Nameplate of motor to be provided | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04140 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007-P01A | Missing U-bolt at PS-10 refer to drawing number V-HRI-R41-810-00000-00064 Rev. 3 Sheet 303 | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-12-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04141 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007-P01A | Tank nameplate to be provided | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-12-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04142 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007-P01A | Rust inside the tank to be remove | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-10-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04143 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007-P01A | Bolts at calibration pot to be tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-10-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04144 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007-ST01 | LCP plastic cover at the back of control panel to be removed | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-10-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04145 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007 | Grouting at the bottom of the tank to be repair | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-10-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04146 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007 | Loose wire connection at 810-LT-9703 to be fixe | A | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04147 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007 | U-bolts to be tightened - general comment | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04148 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007 | Valve BA-97206 handdle should be fully open | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04149 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007 | Tank cover handle to be fixed | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04150 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | 810-X0007 | Internal cleaning of flocculant auto dissolving unit is required | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-10-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04152 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | Common | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-08-30 | 2023-04-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04153 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | Common | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-08-30 |  | Walkdown | [8 empty] | RFC/RFSU
. | 04154 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | EGAT-HEC-810-PRO-PID-00091B | Provide yellow tag sticker for LCS EMERGENCY PUSH BOTTON at cover side written with Polish Language [ WYŁĄCZNIK AWARYJNY ] for all LCS in this system | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-30 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04155 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | EGAT-HEC-810-PRO-PID-00091B | Touch paint for motor to be done (Tag no:-810-X0007-MP01A) | B | ME | HEC ME Construction | Mr. Adam Siewiorek | 2022-08-30 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04156 | 810.10 | 810-10-30 | Thickner Flocculant Dosing System | EGAT-HEC-810-PRO-PID-00091B | Final inspection for cable and cable tray to be done. | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-30 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04157 | 810.10 | 810-10-30 | AUX/Raw Water Shelter | General | Provide additional cable tray for the long cable of instrument | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04158 | 810.10 | 810-10-30 | AUX/Raw Water Shelter | General | Replace the blind plug of all transmitter on spare cable entry | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04159 | 810.10 | 810-10-30 | AUX/Raw Water Shelter | 810-PT-9711/9721/9731 | Make a proper bend & correct loop arrangement of long cable of instrument transmitter | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04160 | 810.10 | 810-10-30 | AUX/Raw Water Shelter | General | Provide grommet for the edge of cable tray | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04161 | 810.10 | 810-10-30 | AUX/Raw Water Shelter | 810-PS-9701/FS-9702/LS-9704 | Provide hanging tag for level switch,pressure switch & flow switch, wrong radius bend fo cable connections. | A | EM | HEC MR Design | Mr. Tomasz Jozel | 2022-08-30 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04162 | 810.10 | 810-10-30 | AUX/Raw Water Shelter | General | All plastic plug in spare cable entry of instrument shall be change by metal plug with Atex specification | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04163 | 810.10 | 810-10-30 | AUX/Raw Water Shelter | 810-LT-9703 | The flexible connector of level transmitter should be tightened properly, cable and gland/plug need to be verify, according the project requirements, and ATEX. | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04164 | 810.10 | 810-10-30 | AUX/Raw Water Shelter | 810-LT-9703 | Missing ground cable on level transmitter | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04165 | 810.10 | 810-10-30 | AUX/Raw Water Shelter | 810-X0007-PO1A/B/C | Instrument cable tray is moving,should be fix by bolt | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04349 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | 860CT-FW-1001 | Re-instatement (after Hydro) 860CT-FW-1001 | A | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-08-30 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04350 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | 860CT-FW-1001 (IN) | Final Inspection 860CT-FW-1001 (IN) | C | IN | HEC IN Construction | Mr. Krzysztof Nolbert | 2022-08-30 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04351 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | 860-DV-1002 | Inspection for Calibration / Installation / Pulling / IR Test /Termination | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04352 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | 860-DV-1003 | Inspection for Calibration / Installation / Pulling / IR Test /Termination | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04353 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | 860-DV-1004 | Inspection for Calibration / Installation / Pulling / IR Test /Termination | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04354 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | 860-DV-1005 | Inspection for Calibration / Installation / Pulling / IR Test /Termination | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04355 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | 860-DV-1006 | Inspection for Calibration / Installation / Pulling / IR Test /Termination | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04356 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | 860-DV-1007 | Inspection for Calibration / Installation / Pulling / IR Test /Termination | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04357 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | 860-DV-1008 | Inspection for Calibration / Installation / Pulling / IR Test /Termination | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-30 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04358 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CT-FW-1001 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04359 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CT-FW-1002 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04360 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CT-FW-1003 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04361 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CT-FW-1004 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04362 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CT-FW-1005 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04363 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CT-FW-1006 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04364 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CT-FW-1007 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04365 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CT-FW-1008 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04366 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CTV-FW-1001 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04367 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CTV-FW-1002 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04368 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CTV-FW-1003 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04369 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CTV-FW-1004 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04370 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CTV-FW-1005 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04371 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CTV-FW-1006 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04372 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | WF-860CTV-FW-1007 | Water Flushing | C | COMM | HEC COMM | J.W.JEONG | 2022-08-30 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04373 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | EGAT-HEC-810-HSE-PID-00202 | Missing electrical tracing | B | EL | HEC EL Construction | Ms. Małgorzata Juszczyk | 2022-08-30 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04374 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | EGAT-HEC-810-HSE-PID-00202 | Handwheel missing on manual valve downstream 860-DV-1003 | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-08-30 | 2022-09-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04375 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | EGAT-HEC-810-HSE-PID-00202 | Missing handwheel on automatic part of deluge valves | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-08-30 | 2022-10-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04376 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | Common | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-08-30 | 2023-04-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04377 | 810.12 | 810-12-14 | Fire Water Deluge System for Cooling Tower System | Common | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-08-30 |  | Walkdown | [8 empty] | RFC/RFSU
. | 04946 | 810.10 | 810-10-20 | 810-X0008 | 810PR-DMW-1001 | Re-instatement (after Hydro) 810PR-DMW-1001 to be done | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-09-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04947 | 810.10 | 810-10-20 | 810-X0008 | 810WS-CC-1003 | Re-instatement (after Hydro) 810WS-CC-1003 to be done | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-09-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04948 | 810.10 | 810-10-20 | 810-X0008 | 810WS-CH-1007 | Re-instatement (after Hydro) 810WS-CH-1007 to be done | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-10-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04949 | 810.10 | 810-10-20 | 810-X0008 | 810WS-DMW-1002 | Re-instatement (after Hydro) 810WS-DMW-1002 to be done | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04950 | 810.10 | 810-10-20 | 810-X0008 | 810WS-DMW-1004 | Re-instatement (after Hydro) 810WS-DMW-1004 to be done | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04951 | 810.10 | 810-10-20 | 810-X0008 | 810WS-DMW-1006 | Re-instatement (after Hydro) 810WS-DMW-1006 to be done | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-09-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04952 | 810.10 | 810-10-20 | 810-X0008 | 810WSV-WW-1003 | Re-instatement (after Hydro) 810WSV-WW-1003 to be done | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-09-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04953 | 810.10 | 810-10-20 | 810-X0008 | AB-810WS-LC-2001 | PRECOMMISSIONING TEST SHEET FOR AIR BLOWING missing | A | COMM | HEC COMM | Ms. Paulina Bajer | 2022-09-02 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04954 | 810.10 | 810-10-20 | 810-X0008 | 810WSV-WW-1003 | Inspection of Final Painting missing | B | PA | HEC PA Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04957 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-P01A/B (IN) | Final Equipment Insulation to be done | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04958 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-P02A/B (IN) | Final Equipment Insulation to be done | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04959 | 810.10 | 810-10-20 | 810-X0008 | LP.810-AT-9801 | Cable Termination & Test to be done | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04960 | 810.10 | 810-10-20 | 810-X0008 | LP.810-AT-9856/9857 | Cable Puling , Termination & Test to be done | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04961 | 810.10 | 810-10-20 | 810-X0008 | LP.810-AT-9876/9877 | Cable Puling , Termination & Test to be done | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04962 | 810.10 | 810-10-20 | 810-X0008 | LP.810-AT-9888 | Cable Puling , Termination & Test to be done | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04963 | 810.10 | 810-10-20 | 810-X0008 | LP.810-AT-9896 | Cable Puling , Termination & Test to be done | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04964 | 810.10 | 810-10-20 | 810-X0008 | LP.810-X0008-MP03A/S.C. | Cable Puling , Termination & Test to be done | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04965 | 810.10 | 810-10-20 | 810-X0008 | LP.810-X0008-MP03B/S.C. | Cable Puling , Termination & Test to be done | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04966 | 810.10 | 810-10-20 | 810-X0008 | LP.810-X0008-MP04A/S.C. | Cable Puling , Termination & Test to be done | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04967 | 810.10 | 810-10-20 | 810-X0008 | LP.810-X0008-MP04B/S.C. | Cable Puling , Termination & Test to be done | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04968 | 810.10 | 810-10-20 | 810-X0008 | 810-AR-001 | Inspection for Calibration / Installation / Pulling / IR Test /Termination / Hookup / Leak to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04969 | 810.10 | 810-10-20 | 810-X0008 | 810-PSV-9811 | Inspection for Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04970 | 810.10 | 810-10-20 | 810-X0008 | 810-PSV-9821 | Inspection for Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04971 | 810.10 | 810-10-20 | 810-X0008 | 810-PT-9833 | Inspection for Installation / Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04972 | 810.10 | 810-10-20 | 810-X0008 | 810-FE-9834 | Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04973 | 810.10 | 810-10-20 | 810-X0008 | 810-FT-9834 | Inspection for Installation / Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04974 | 810.10 | 810-10-20 | 810-X0008 | 810-FE-9804 | Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04975 | 810.10 | 810-10-20 | 810-X0008 | 810-FT-9804 | Inspection for Installation / Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04976 | 810.10 | 810-10-20 | 810-X0008 | 810-PSV-9841 | Inspection for Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04977 | 810.10 | 810-10-20 | 810-X0008 | 810-XV-9849 | Inspection for Calibration / Installation / Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04978 | 810.10 | 810-10-20 | 810-X0008 | 810-XV-9850 | Inspection for Calibration / Installation / Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04979 | 810.10 | 810-10-20 | 810-X0008 | 810-FE-9805 | Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04980 | 810.10 | 810-10-20 | 810-X0008 | 810-FT-9805 | Inspection for Installation / Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04981 | 810.10 | 810-10-20 | 810-X0008 | 810-PSV-9861 | Inspection for Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04982 | 810.10 | 810-10-20 | 810-X0008 | 810-XV-9869 | Inspection for Calibration / Installation / Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04983 | 810.10 | 810-10-20 | 810-X0008 | 810-XV-9870 | Inspection for Calibration / Installation / Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04984 | 810.10 | 810-10-20 | 810-X0008 | 810-AT-9856 | Inspection for Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04985 | 810.10 | 810-10-20 | 810-X0008 | 810-AT-9858 | Inspection for Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04986 | 810.10 | 810-10-20 | 810-X0008 | 810-FO-9830 | Inspection for Calibration / Installationv to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04987 | 810.10 | 810-10-20 | 810-X0008 | 810-XV-9838 | Inspection for Calibration / Installation / Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04988 | 810.10 | 810-10-20 | 810-X0008 | 810-TT-9837 | Inspection for Installation / Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04989 | 810.10 | 810-10-20 | 810-X0008 | 810-FE-9839 | Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04990 | 810.10 | 810-10-20 | 810-X0008 | 810-FT-9839 | Inspection for Installation / Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04991 | 810.10 | 810-10-20 | 810-X0008 | 810-FE-9840 | Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04992 | 810.10 | 810-10-20 | 810-X0008 | 810-FT-9840 | Inspection for Installation / Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04993 | 810.10 | 810-10-20 | 810-X0008 | 810-FV-9839 | Inspection for Installation / Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04994 | 810.10 | 810-10-20 | 810-X0008 | 810-FV-9840 | Inspection for Installation / Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04995 | 810.10 | 810-10-20 | 810-X0008 | 810-FI-9851 | Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04996 | 810.10 | 810-10-20 | 810-X0008 | 810-FI-9852 | Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04997 | 810.10 | 810-10-20 | 810-X0008 | 810-FI-9886 | Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04998 | 810.10 | 810-10-20 | 810-X0008 | 810-PT-9899 | Inspection for Installation / Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 04999 | 810.10 | 810-10-20 | 810-X0008 | 810-PSV-9883 | Inspection for Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05000 | 810.10 | 810-10-20 | 810-X0008 | 810-PSV-9884 | Inspection for Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05001 | 810.10 | 810-10-20 | 810-X0008 | 810-AT-9886 | Inspection for Calibration / Installation / Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05002 | 810.10 | 810-10-20 | 810-X0008 | 810-FI-9883 | Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05003 | 810.10 | 810-10-20 | 810-X0008 | 810-FE-9883 | Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05004 | 810.10 | 810-10-20 | 810-X0008 | 810-XV-9882 | Inspection for Installation / Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05005 | 810.10 | 810-10-20 | 810-X0008 | 810-AT-9896 | Inspection for Calibration / Installation / Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05006 | 810.10 | 810-10-20 | 810-X0008 | 810-FI-9893 | Inspection for Calibration / Installationv to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05007 | 810.10 | 810-10-20 | 810-X0008 | 810-XV-9892 | Inspection for Installation / Pulling / IR Test /Termination / Hookup / Leak Test to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05008 | 810.10 | 810-10-20 | 810-X0008 | 810-JA-514(IS) | Inspection for Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05009 | 810.10 | 810-10-20 | 810-X0008 | 810-JA-515(IS) | Inspection for Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05010 | 810.10 | 810-10-20 | 810-X0008 | 810-JA-522(IS) | Inspection for Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05011 | 810.10 | 810-10-20 | 810-X0008 | 810-JA-523(IS) | Inspection for Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05012 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-P03BA | Inspection for Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05013 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-P03BB | Inspection for Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05014 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-P04AA | Inspection for Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05015 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-P04AB | Inspection for Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05016 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-P04BA | Inspection for Pulling / IR Test /Termination to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05017 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008 | Grating on the drain line to be installed | A | AR | HEC AR Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-10-13 | Walkdown | 9/21 disp. change AR->SS 9/22: Disp. SS->AR |  |  |  | V |  |  |  | RFC/RFSU
. | 05018 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-BL01A/B | PSV tag is missing | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05019 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-BL01A/B | Housekeeping to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05020 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-BL01A/B | Rust on PSV to be removed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05021 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-P03A | SS flange resting on CS pipe support need to be isolated | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05022 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-P03A | BA988624 Valve is resting on CS pipe support need to isolate | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05023 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-P03A/B | Missing nameplate | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05024 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-P04A/B | Missing nameplate | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05025 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-P04A/B | Rust on motor to be remove | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05026 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-ST01 | Bolt on flange connection on 1 1/2'' flange with line number 810-1''-CH-98512-N1A1-N need to be install as per DWG | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05027 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-ST01 | BAXXX missing name tag and has a limited access due to collision with flange ( 1'' pipe line @ 810-1''-AV-98001-NA1-N line number) | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05028 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-ST01 | BA98605 valve handle has limited access for operating to be modify | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05029 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-ST01 | BAXXX missing name tag valve handle open & close position need to adjust (beside BA98620) | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05030 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-ST02 | Drain line (810-1''-CH-98613-N1A1-ET) pipe suppot position to be installed properly | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05031 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U01A | Touch-up painting of the vessel body to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05032 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U01A/B | nameplate to be verified as per DWG | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05033 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U01A/B | Missing nameplate on the skid | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05034 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U01A/B | Platform grating to be cleaned and touch up painting to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05035 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U01A/B | Housekeeping to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2023-03-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05036 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U01A/B | Touch-up painting of the handrail to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05037 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U01A/B (Skid) | valve missing name tag and to be relocated ( 266044) | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05038 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U01A/B (Skid) | BA98206 valve handle has limited access for operating ( to be relocated) | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05039 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U01A/B (Skid) | BA98312 valve handle has limited access for operating ( to be relocated) | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05040 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U01B | Touch-up painting of the vessel body to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05041 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U02A | Manhole ( M2) loose bolt to be tighten | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05042 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U02A | Rust on M2 manhole to be removed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05043 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U02A | VG820H to be rectified ( Limited access to operate) | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05044 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U02A | PSV9611 name tag is missing | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05045 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U02A | Loose bolt at 2'' flange near N5 | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05046 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U02A | Touch-up painting of the vessel body to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05047 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U02A/B | Housekeeping to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2023-03-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05048 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U02A/B | Platform to be cleaned and touch-up painting to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05049 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U02A/B | Touch-up painting of the handrail to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05050 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U02A/B | Polish nameplate to be modified ( Wrong translation) | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05051 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U02B | PSV 9861 name tag is missing | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05052 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-U02B | Touch-up painting of the vessel body to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05053 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-X01A | Missing U-bolt on 3/4'' valve to pipe | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05054 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-X01A | Missing plug on 3/4'' valve | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05055 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-X01A | Carbon steel plug on stainless steel valve to be change | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05056 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-X01A | Tubing line near the drain line to be fixed | A | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-08 | Walkdown |  |  | 2022-11-05 |  | V |  |  |  | RFC/RFSU
. | 05057 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-X01A | Loose bolt to be tightened at 6'' line ( 810-6''-DMW-98302-L1A0-N | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05058 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-X01A/B | Drain line coming from the skid to be installed | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05059 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-X01A/B | BA 9846 Valve handle has limited access for operating | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05060 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-X01A/B | BA 9816 valve handle has limited access for operating | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05061 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-X01A/B | 1'' pipe touching the skid platform to be modified | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05062 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-X01A/B | BA98034 valve handle has limited access for operating | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05063 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-X01A/B | Polish nameplate to be modified ( Wrong translation) | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-12-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05064 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-X01B | Missing bolt and loose bolting need to install and final bolting | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05065 | 810.10 | 810-10-20 | 810-X0008 | 810-X0008-X01B | Cable tray to be relocated not obstructing with the nameplate | A | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-09 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 05066 | 810.10 | 810-10-20 | 810-X0008 | 810-X000-U02B | Damage plastic cover on the U-bolt need to be replaced | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05067 | 810.10 | 810-10-20 | 810-X0008 | 810-X008-CSKID 5 & 4 | Access Ladder and platform to be provided on each skid | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2023-05-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05068 | 810.10 | 810-10-20 | 810-X0008 | 810-X008-CSKID 5 & 4 | Housekeeping to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05069 | 810.10 | 810-10-20 | 810-X0008 | 810-X008-CSKID 5 & 4 | Excess grouting on the skid concrete foundation to be remove | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05070 | 810.10 | 810-10-20 | 810-X0008 | 810-X008-CSKID4 | BAXXX missing name tag valve handle has limited access for operating beside BA98708 | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05071 | 810.10 | 810-10-20 | 810-X0008 | 810-X008-CSKID4 | BA98711 valve handle has limited access for operating to be modify | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05072 | 810.10 | 810-10-20 | 810-X0008 | 810-X008-CSKID4 | BA98622 Valve is resting on CS pipe support need to isolate | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05073 | 810.10 | 810-10-20 | 810-X0008 | 810-X008-CSKID5 | Damage insulation to be repaired | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05074 | 810.10 | 810-10-20 | 810-X0008 | 810-X008-CSKID5 | BA98713 valve handle has limited access for operating due to insulation | A | EM | HEC MR Design | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05075 | 810.10 | 810-10-20 | 810-X0008 | 810-X008-CSKID5 | BA98723 valve handle has limited access for operating due to insulation | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05076 | 810.10 | 810-10-20 | 810-X0008 | 810-X008-CSKID5 | BA98611 valva handle has limited access to operate due to collision with the cable tray | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05077 | 810.10 | 810-10-20 | 810-X0008 | 810-X008-CSKID5 | BA9862 valve handle has limited access to operate due to collision with pipe support | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-02 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05078 | 810.10 | 810-10-20 | Demineralization |  | Area not prepared for Walk down - house keeping required - in the whole area there are garbage, rags, unnecessary fragments of pipelines and structures etc. - existing scafolding - at Acid dosing and Caustic dosing, sump pits are completely filled with mud. | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-02 | 2022-11-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05079 | 810.10 | 810-10-20 | Demineralization |  | Safety switches do not meet the Machinery Directive 06/42/EC - Polish law, Ordinance of the Ministry of Economy of October 21, 2008 in clause 1.2.4.3 "The emergency stop device must: be equipped with CLEARLY RECOGNIZABLE, VISIBLE and QUICKLY ACCESSIBLE controls." Emergency STOP button at pump's control pannel is not easy accesable. There are no possibility to quick push the Emergency STOP button using one hand. | A | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2022-09-02 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05080 | 810.10 | 810-10-20 | Demineralization Acid dosing, Caustic dosing |  | There are swapped places of control pannels for pump drives - e.g. for Acid dosing Skid - pannel asociated with pump drive 810-X0008-P04A is close to the pump 810-X0008-P04B and vice versa. The same situation is at Caustic dosing Skid | A | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2022-09-02 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05081 | 810.10 | 810-10-20 | Demineralization |  | At few devices (valves and blowers 810-X0008-BL01A i …BL01B) there are no identification plates | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-02 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05082 | 810.10 | 810-10-20 | Demineralization Caustic dosing |  | At the grounding board clamp (close to 820-PDP-001) there are few not fixed connections. | A | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2022-09-02 | 2022-10-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05083 | 810.10 | 810-10-20 | Demineralization Acid dosing |  | No easy access for service and maintenance of equipment located on the top of Acid tank 810-X0008-ST02 | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-02 | 2022-11-29 | Walkdown |  | change category from A to B |  |  | V |  |  |  | RFC/RFSU
. | 05084 | 810.10 | 810-10-20 | Demineralization Acid dosing, Caustic dosing | Specific item is required | Part of piping insulation is not installed | C | IN | HEC IN Construction | Mr. Krzysztof Nolbert | 2022-09-02 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05085 | 810.10 | 810-10-20 | Demineralization Acid dosing, Caustic dosing |  | There are necessary to install intermediate steps and platforms for access from the ground to the skid's service platforms | C | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-02 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05086 | 810.10 | 810-10-20 | Demineralization Acid dosing, Caustic dosing |  | There are no access for few devices at high location on the chemical dosing skids | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-02 | 2022-11-29 | Walkdown |  | change category from A to B |  |  | V |  |  |  | RFC/RFSU
. | 05087 | 810.10 | 810-10-20 | Demineralization Acid dosing |  | Handle of valve BA-98608 very close to support structure - danger of injury to the operator hand | B | EM | HEC MR Design | Mr. Krzysztof Nolbert | 2022-09-02 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05088 | 810.10 | 810-10-20 | Demineralization Acid dosing |  | Handle of valve BABA-98606 in open position block possibility to open valve BA-98605 | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-02 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05089 | 810.10 | 810-10-20 | Demineralization Resin trap |  | Tubing (2 pcs) from Silica Analyzer to the draining channel are not supported and fixed. | B | CI | HEC CI Construction | Mr. Krzysztof Nolbert | 2022-09-02 | 2022-11-08 | Walkdown |  |  | 2022-11-05 |  | V |  |  |  | RFC/RFSU
. | 05090 | 810.10 | 810-10-20 | Demineralization Resin trap |  | No acces to valves BA98304, BA98405 | A | EM | HEC MR Design | Mr. Krzysztof Nolbert | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05091 | 810.10 | 810-10-20 | Demineralization Package | EGAT-HEC-810-PRO-PID-00151A~J | Provide yellow tag sticker for LCS EMERGENCY PUSH BOTTON at cover side written with Polish Language [ WYŁĄCZNIK AWARYJNY ] for all LCS | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-10-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05092 | 810.10 | 810-10-20 | Demineralization Package | EGAT-HEC-810-PRO-PID-00151A~J | Body earthing is missing for motor Tag no:- 810-X008-MBL01A/B to be provided | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05093 | 810.10 | 810-10-20 | Demineralization Package | EGAT-HEC-810-PRO-PID-00151A~J | Earthing cable loose connection for motor base support for 810-x008-MBL01A/B and stub-up conduit pipe sealing to be done. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05094 | 810.10 | 810-10-20 | Demineralization Package | EGAT-HEC-810-PRO-PID-00151A~J | Blind plug to be provided for LCS spare hole. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05095 | 810.10 | 810-10-20 | Demineralization Package | EGAT-HEC-810-PRO-PID-00151A~J | Earthing busbar bolts loose connection to be tighten for all bolts. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05096 | 810.10 | 810-10-20 | Demineralization Package | EGAT-HEC-810-PRO-PID-00151A~J | Body earthing to be provided for Analyzer 810-AR-562 & 810-AR-563. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05097 | 810.10 | 810-10-20 | Demineralization Package | EGAT-HEC-810-PRO-PID-00151A~J | Cable gland loose to be tightened for analyzer 810-AR-562 & 810-AR-563 power cable. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-09-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05098 | 810.10 | 810-10-20 | Demineralization Package | EGAT-HEC-810-PRO-PID-00151A~J | Analyzer panel is shaking to be rectify for 810-AR-562 & 810-AR-563 | A | CI | HEC CI Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05099 | 810.10 | 810-10-20 | Demineralization Package | EGAT-HEC-810-PRO-PID-00151A~J | Cable Ladder tray earthing bonding jumper is missing to be provided near 810-JD-562(Instrument) | A | CI | HEC CI Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05100 | 810.10 | 810-10-20 | Demineralization Package | EGAT-HEC-810-PRO-PID-00151A~J | Body earthing to be provided for all instrument (JB)810-JA-106, JB-107,JD-006(IS), JA-013(IS), JA-012(IS) | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05101 | 810.10 | 810-10-20 | Demineralization Package | EGAT-HEC-810-PRO-PID-00151A~J | Drain tubing line support is missing to be provided for 810-AC-561 | A | CI | HEC CI Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-11-08 | Walkdown |  |  | 2022-11-05 |  | V |  |  |  | RFC/RFSU
. | 05102 | 810.10 | 810-10-20 | Demineralization Package | EGAT-HEC-810-PRO-PID-00151A~J | Final inspection for Cable and Cable tray to be done | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05103 | 810.10 | 810-10-20 | Demineralization Package | EGAT-HEC-810-PRO-PID-00151A~J | Duct Sealing to be provided for stub-up conduit pipe for 810-X008-MP01A / B. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05104 | 810.10 | 810-10-20 | AUX/810 Demineralization Shelter | General | Provide addditional cable tray for the long cable of all skid instrument | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05105 | 810.10 | 810-10-20 | AUX/810 Demineralization Shelter | General | IS cable & NIS cable shall be separate cable tray on skid instrument | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-09 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 05106 | 810.10 | 810-10-20 | AUX/810 Demineralization Shelter | General | The SS cable Tag of skid instrument is not matching to the HEC document drawing,to be verified | C | ME | HEC ME Construction | Owner Maintenance team | 2022-09-02 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05107 | 810.10 | 810-10-20 | AUX/810 Demineralization Shelter | General | Replace the temporary blind plug on spare cable entry of all instrument with atex specification | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05108 | 810.10 | 810-10-20 | AUX/810 Demineralization Shelter | General | Make a proper bend & correct loop arrangement of long cable of skid instrument | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-09 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 05109 | 810.10 | 810-10-20 | AUX/810 Demineralization Shelter | 810-PDIT-9873/9853 | The drain plug of pressure defferential transmitter is blocking by structure support | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05110 | 810.10 | 810-10-20 | AUX/810 Demineralization Shelter | 810-PDIT-9853 | The hanging tag of pressure defferential transmitter is missing | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05111 | 810.10 | 810-10-20 | AUX/810 Demineralization Shelter | General | Provide hanging tag for all air manifold | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05112 | 810.10 | 810-10-20 | AUX/810 Demineralization Shelter | 810-PT-9833/FT-9839 | Hook up connection of pressure transmitter to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05113 | 810.10 | 810-10-20 | AUX/810 Demineralization Shelter | 810-FE-9834/FE-9840/FT-9839/FO-9830 | Flow element,flow transmitter are not installed | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-12-02 | Walkdown |  | 2022-11-30 | 2022-12-02 |  | V |  |  |  | RFC/RFSU
. | 05114 | 810.10 | 810-10-20 | AUX/810 Demineralization Shelter | 810-FT-9834 | Heat tracing cable of flow transmitter is missing,to be verified | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-09-02 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05115 | 810.10 | 810-10-20 | AUX/810 Demineralization Shelter | 810-FT-9834 | Tubing installation connection for high side & low side of flow transmitter is not correct,to be verified | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05116 | 810.10 | 810-10-20 | AUX/810 Demineralization Shelter | 810-P0001A/B & 810-P0002A/B | All pressure gauge on the motor side should be visible installation | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-24 | Walkdown |  |  | 2022-11-18 |  | V |  |  |  | RFC/RFSU
. | 05117 | 810.10 | 810-10-20 | AUX/810-SL-003 | 810-FV-9839 | Provide elbow connector for the cable glanding entry of control valve to avoid touching to the pipe line insulation | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05118 | 810.10 | 810-10-20 | AUX/810-SL-003 | 810-FT-9839 | On the spare tapping point of flow transmitter blind plug is missing | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05119 | 810.10 | 810-10-20 | AUX/810-SL-003 | 810-FT-9839/TT-9837 | Provide grommet for the edge of cable tray | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-10-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05120 | 810.10 | 810-10-20 | AUX/810-SL-003 | 810-XV-9838/FT-9840/LT-9883/9893 | Cable glanding of on/off valve & insttrument transmitter to be tightened properly | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05121 | 810.10 | 810-10-20 | AUX/810-SL-003 | 810-TT-9837 | Temperature transmitter have no access | B | ME | HEC ME Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-23 | Walkdown |  | change category from A to B |  |  | V |  |  |  | RFC/RFSU
. | 05122 | 810.10 | 810-10-20 | AUX/810-SL-003 | 810-XV-9838 | the local indication for open/closed of on/off valve to be adjust | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05123 | 810.10 | 810-10-20 | AUX/810-SL-003 | 810-PG-9885/9884 | Syphoon tube of pressure gauge need to change & Atex mark with data sheet to be verify | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05124 | 810.10 | 810-10-20 | AUX/810-SL-003 | 810-XV-9881 | Bolt torquing to be done | A | PI | HEC PI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05125 | 810.10 | 810-10-20 | AUX/810-SL-003 | 810-LG-9891 | Level guage is touching to the process pipe line | B | ME | HEC ME Construction | Owner Maintenance team | 2022-09-02 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05126 | 810.10 | 810-10-20 | AUX/810-SL-003 | EGAT-HEC-810-PRO-PID-00151D/E | In P&ID the tag number PDIT-9853 of 810-X0008-U02A is same tag to the 810-X0008-U02B,P&ID to be verify & update | A | EM | HEC PR Design | Mr. Tomasz Jozel | 2022-09-02 | 2022-12-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05127 | 810.10 | 810-10-20 | Demineralization Package | AT-1011/9856/9857/9858/9878/9877/9886/9896/ | No access to cabinet/rack whith instruments | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05128 | 810.10 | 810-10-20 | Demineralization Package | General | Initial ATEX inspection | B | PER | HEC permit team | Owner Maintenance team | 2022-09-02 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05129 | 810.10 | 810-10-20 | Demineralization Package | Common | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-09-02 | 2023-03-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05130 | 810.10 | 810-10-20 | Demineralization Package | Common | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-02 |  | Walkdown | [8 empty] | RFC/RFSU
. | 05131 | 810.10 | 810-10-20 | Demineralization Package | 810-PSV-9861 | PSV-9861: tag missing | B | CI | HEC CI Construction | Ms. Alicja Sulżyc | 2022-09-02 | 2022-11-08 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 05132 | 810.10 | 810-10-20 | Demineralization Package | 810-X0008-X01A/B | Resin trap outlets not connected to the trench | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-10-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05133 | 810.10 | 810-10-20 | Demineralization Package | 810-X0008-X01A/B | Nut bolts missings on flange connections | A | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05134 | 810.10 | 810-10-20 | Demineralization Package | 810-6''-WW-98402-L1A0-N | Missing bolts on flange connection (810-6''-WW-98402-L1A0-N) | A | ME | HEC ME Construction | Mr. Jaroslaw Pykosz | 2022-09-02 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05135 | 810.10 | 810-10-20 | Demineralization Package | 810-X0008-X01A/B | Cover missing | A | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-11-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05136 | 810.10 | 810-10-20 | Demineralization Package | PID-00151E | tag no. of XV-9846 to be verified at Site. | B | ME | HEC ME Construction | Mr. Jaroslaw Pykosz | 2022-09-02 | 2023-01-17 | Walkdown |  | change category from B to C |  |  | V |  |  |  | RFC/RFSU
. | 05137 | 810.10 | 810-10-20 | Demineralization Package | PID-00151D | FT-9804/FT-9839: flowmeter to be connected properly (exchanged cabinets and cable connections) | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-09-02 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05138 | 810.10 | 810-10-20 | Demineralization Package | 810-XV-9845 | XV-9845: no access to the valve | C | ME | HEC ME Construction | Mr. Jaroslaw Pykosz | 2022-09-02 |  | Walkdown |  | Changed from Category B |  |  | V |  |  | 2023-03-10 | RFC/RFSU
. | 05139 | 810.10 | 810-10-20 | Demineralization Package | 810-PDT-9853 | PDT-9853: missing hanging tag | B | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-09-02 | 2022-11-09 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 05140 | 810.10 | 810-10-20 | Demineralization Package | PID-00151A/B | PG-9811/SN-9801 configuration to be corrected in P&ID (the same applies filter B). | B | EM | HEC PR Design | Mr. Łukasz Jekel | 2022-09-02 | 2022-11-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05141 | 810.10 | 810-10-20 | Demineralization Package | PID-00151G | PG-9884/9885 to be exchanged at Site. | B | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-11-23 | Walkdown |  |  | 2022-11-18 |  | V |  |  |  | RFC/RFSU
. | 05142 | 810.10 | 810-10-20 | Demineralization Package | PID-00151G | Note 4 in P&ID to be applied - no acces to the instrument (FT-9886) | C | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-09-02 |  | Walkdown | [8 empty] | RFC/RFSU
. | 05143 | 810.10 | 810-10-20 | Demineralization Package | PID-00151G | Manual valve on header piping of blower to be specified in P&ID | B | EM | HEC PR Design | Mr. Jaroslaw Pykosz | 2022-09-02 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05144 | 810.10 | 810-10-20 | Demineralization Package | PID-00151G | Manual valve on header piping of blower - not able to operate | A | PI | HEC PI Construction | Mr. Łukasz Jekel | 2022-09-02 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05145 | 810.10 | 810-10-20 | Demineralization Package | PID-00151G | Stopper to be added for manual valve on drain line from blower discharge line | A | PI | HEC PI Construction | Ms. Alicja Sulżyc | 2022-09-02 | 2022-10-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05146 | 810.10 | 810-10-20 | Demineralization Package | PID-00151G | missing valve upstream of XV-9838 | A | PI | HEC PI Construction | Mr. Jaroslaw Pykosz | 2022-09-02 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05147 | 810.10 | 810-10-20 | Demineralization Package | PID-00151G | XV-9838: too short bolting | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05148 | 810.10 | 810-10-20 | Demineralization Package | PID-00151H | Manual valve upstream of XV-9881: hanging tag missing, handwheel to be installed properly | C | ME | HEC ME Construction | Mr. Łukasz Jekel | 2022-09-02 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05149 | 810.10 | 810-10-20 | Demineralization Package | PID-00151H | Valve on vent line - not able to operate (collision with the flange) | A | ME | HEC ME Construction | Mr. Łukasz Jekel | 2022-09-02 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05150 | 810.10 | 810-10-20 | Demineralization Package | PID-00151H | PRVs 9881/9882 to be exchanged | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05151 | 810.10 | 810-10-20 | Demineralization Package | PID-00151H | YSTR-98611/98621 to be exchanged | A | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05152 | 810.10 | 810-10-20 | Demineralization Package | PID-00151H | Anti acid coating | B | AR | HEC AR Construction | Ms. Alicja Sulżyc | 2022-09-02 | 2022-11-28 | Walkdown | 9/15: Punch Disp. Changed (CV->AR) | Category changed fro A to B |  |  | V |  |  |  | RFC/RFSU
. | 05153 | 810.10 | 810-10-20 | Demineralization Package | PID-00151H/I | Pits to be cleaned and grating to be provided | B | EM | HEC MR Design | Ms. Paulina Bajer | 2022-09-02 | 2022-12-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05154 | 810.10 | 810-10-20 | Demineralization Package | PID-00151H | Drain valve downstream of XV-9882 missing in P&ID. | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-09-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05155 | 810.10 | 810-10-20 | Demineralization Package | PID-00151H/G | FT-9883/9851//9852: to be rotated at 90 degress | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-09-02 | 2022-11-09 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 05156 | 810.10 | 810-10-20 | Demineralization Package | PID-00151H | Drain valve downstream of SN-9808 to be specified in P&ID. | B | EM | HEC PR Design | Mr. Jaroslaw Pykosz | 2022-09-02 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05157 | 810.10 | 810-10-20 | Demineralization Package | PID-00151H | Support clamp missing on vent line. | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05158 | 810.10 | 810-10-20 | Demineralization Package | PID-00151I | Manual valve upstream of XV-19881 not able to operate | A | EM | HEC MR Design | Mr. Jaroslaw Pykosz | 2022-09-02 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05159 | 810.10 | 810-10-20 | Demineralization Package | PID-00151I | Drain valve downstream of SN-9810 to be specified in P&ID. | B | EM | HEC PR Design | Ms. Paulina Bajer | 2022-09-02 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05160 | 810.10 | 810-10-20 | Demineralization Package | PID-00151I | Missing tag nos. of PRVs. | B | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-09-02 | 2022-11-15 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 05161 | 810.10 | 810-10-20 | Demineralization Package | PID-00151H/I | LG/TG on both chemical skids to be installed with better visability and access for the operator | C | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-09-02 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05162 | 810.10 | 810-10-20 | Demineralization Package | PID-00151H | Local panels of the pumps to be exchanged. | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-09-02 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05163 | 810.10 | 810-10-20 | Demineralization Package | PID-00151C | Handwheel for manual valve upstream of PT-9833 missing | A | PI | HEC PI Construction | Mr. Jaroslaw Pykosz | 2022-09-02 | 2022-10-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05164 | 810.10 | 810-10-20 | Demineralization Package | PID-00151C | FT-983 not connected | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-09-02 | 2022-09-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05165 | 810.10 | 810-10-20 | Demineralization Package | PID-00161 | Drain valve on demi water line from 810-X0008 missing in P&ID. | B | EM | HEC PR Design | Ms. Paulina Bajer | 2022-09-02 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05166 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-05 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05167 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-04 | Tape to be removed and touch up paint to be done. | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05168 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-04 | Mastic missing on elbows and supports | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05169 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-04 | Piping Insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05170 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-04 | Tape to be removed on vent and to be covered by insulation and cladding | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05171 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-04 | Tag missing (860-BVP-9301) | B | EM | HEC MR Design | Mr. Jakub Partyka | 2022-09-02 | 2022-11-16 | Walkdown | [8 empty] | RFC/RFSU
. | 05172 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-03 | Insulation not protected from rain water. Wet insulation to be exchanged for dry one. | B | EM | HEC MR Design | Mr. Maciej Smalira | 2022-09-02 | 2022-10-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05173 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-03 | Mastic missing on supports | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05174 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-03 | Piping Insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05175 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-02 | Insulation not protected from rain water. Wet insulation to be exchanged for dry one. | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05176 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-02 | Mastic missing on elbows and supports | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05177 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-02 | Piping Insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05178 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-01 | Tag plate to be removed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-09-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05179 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-01 | Insulation not protected from rain water. Wet insulation to be exchanged for dry one. | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05180 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-01 | Mastic missing on elbows and supports | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05181 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-01 | Piping Insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05182 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL00102-01 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-02 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05183 | 810.10 | 810-10-20 | 860CT | 860CT-860SUL07101-01 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-02 | 2022-09-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05244 | 810.10 | 810-10-20 | 810WS | 810WS-810WW98008-01 | Pipeline shaking due to pipe not resting on support | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05245 | 810.10 | 810-10-20 | 810WS | 810WS-810WW98008-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05246 | 810.10 | 810-10-20 | 810WS | 810WS-810WW98008-01 | Paint touch up for Support to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05247 | 810.10 | 810-10-20 | 810WS | 810WS-810WW98011-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05248 | 810.10 | 810-10-20 | 810WS | 810WS-810WW98015-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05249 | 810.10 | 810-10-20 | 810WS | 810WS-810WW98010-01 | Pipeline shaking | A | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05250 | 810.10 | 810-10-20 | 810WS | 810WS-810WW98010-01 | Pipe touch contact with tubing | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-10 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 05251 | 810.10 | 810-10-20 | 810WS | 810WS-810WW98014-01 | Pipeline shaking | A | EM | HEC MR Design | Mr. Maciej Smalira | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05252 | 810.10 | 810-10-20 | 810WS | 810WS-810WW98014-01 | Cap to be removed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05253 | 810.10 | 810-10-20 | 810WS | 810WS-810WW98016-01 | Cap to be removed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05254 | 810.10 | 810-10-20 | 810WS | 810WS-810WW98016-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05255 | 810.10 | 810-10-20 | 810WS | 810WS-810WW98002-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05256 | 810.10 | 810-10-20 | 810WS | 810WS-810WW98005-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05257 | 810.10 | 810-10-20 | 810WS | 810WS-810PRA98001-01 | Valve and flange connection to be cleaned from soil | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05258 | 810.10 | 810-10-20 | 810WS | 810WS-810PRA98001-02 | Valve wheel limited access. Stem extension to be discussed | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05259 | 810.10 | 810-10-20 | 810WS | 810WS-810PRA98001-02 | Pipeline not resting | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05260 | 810.10 | 810-10-20 | 810WS | 810WS-810PRA98001-02 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05261 | 810.10 | 810-10-20 | 810WS | 810WS-810PRA98001-02 | Tag plates to be removed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05262 | 810.10 | 810-10-20 | 810WS | 810WS-810PRA98001-02 | Rusted plug to be painted | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05263 | 810.10 | 810-10-20 | 810WS | 810WS-810PRA98001-03 | Cable tray in touch contact with pipe | A | EL | HEC EL Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05264 | 810.10 | 810-10-20 | 810WS | 810WS-810PRA98002-01 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05265 | 810.10 | 810-10-20 | 810WS | 810WS-810PRA98002-01 | Tag plates to be removed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05266 | 810.10 | 810-10-20 | 810WS | 810WS-810PRA98003-01 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05267 | 810.10 | 810-10-20 | 810WS | 810WS-810PRA98003-01 | Tag plates to be removed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05268 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98003-01 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05269 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98003-01 | Overlap of cladding on support oriented up. Incomplete seal by mastic | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05270 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98003-01 | Mastic on support not sealed completely | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05271 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98003-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05272 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98004-02 | Pipeline touch contact with steel structure | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05273 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98004-02 | Pipe material has been changed. To be verified | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05274 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98004-02 | Mastic missing on elbows and supports | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05275 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98004-02 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-06 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05276 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98019-01 | Mastic missing on support | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05277 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98019-01 | Piping Insulation to be completed | B | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05278 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98004-01 | Loose bolts on support | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05279 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98004-01 | Instrument missing (810-AT-9886) | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-10 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 05280 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98004-01 | Indication tube horizontal position | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05281 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98004-01 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05282 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98004-01 | Piping Insulation to be completed (End before line of the wall) | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05283 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98004-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-06 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05284 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98002-01 | Rusted bolts and nuts to be cleaned (between flanges) | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05285 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98002-01 | Tag plates to be removed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05286 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98002-01 | Pipeline touching sandwich wall | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05287 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98002-01 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05288 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98002-01 | Touch up paint to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05289 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98002-01 | Gap on cladding overlap | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05290 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98002-01 | Tubing shaking (810-XV-9882) | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05291 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98002-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-06 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05292 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98519-01 | Pipe and supports to be cleaned | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05293 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-01 | Guides missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05294 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-01 | Mastic missing on support | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05295 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-01 | Mastic missing on ET cover plate | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05296 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-01 | Piping Insulation to be completed (Vent) | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05297 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-01 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05298 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-02 | Mastic missing on elbows | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05299 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-02 | Piping Insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05300 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-02 | Instrument missing (810-AT-9896) | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-10 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 05301 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-02 | Cable tray in touch contact with pipe | A | EL | HEC EL Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05302 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98020-01 | Mastic on support not sealed completely | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05303 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-03 | Guides missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05304 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-03 | Loose bolts on support and not center on steel structure | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05305 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-03 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05306 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-03 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05307 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98008-03 | Indication tube horizontal position | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05308 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98011-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05309 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98012-01 | Tag plates to be removed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05310 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98006-01 | Loose bolts on support and not center on steel structure | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05311 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98006-01 | Loose bolts on support | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05312 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98006-01 | Valve to be cleaned from dirt (810-XV-9892) | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05313 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98006-01 | Piping Insulation missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05314 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98006-01 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05315 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98006-01 | Tubing shaking (810-XV-9892) | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05316 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98006-01 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05317 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98006-01 | Support in touch contact with sandwich wall | B | AR | HEC AR Construction | Mr. Jakub Partyka | 2022-09-06 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05318 | 810.10 | 810-10-20 | 810WS | 810WS-810CH98619-01 | Pipe and supports to be cleaned | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05319 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98005-01 | Mastic on support not sealed completely (east side) | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05320 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98005-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05321 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98004-01 | Short bolts on support | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05322 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98004-01 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05323 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98004-01 | Mastic on support not sealed completely | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05324 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98002-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05325 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98002-01 | Tag plates to be removed | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05326 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98002-01 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05327 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98002-01 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05328 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98002-01 | Mastic on support not sealed completely | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05329 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98007-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05330 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98007-01 | Orifice missing (810-FE-9805) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05331 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98007-01 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05332 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98007-01 | Damaged cladding to be replaced | B | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-06 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05333 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98007-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05334 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98007-01 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05335 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98006-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05336 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98006-01 | Orifice missing (810-FE-9804) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05337 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98006-01 | Rusted nuts on embedded plate | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05338 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98006-01 | Mastic missing on support | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05339 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98006-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05340 | 810.10 | 810-10-20 | 810WS | 810WS-810CC98006-01 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05341 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98008-01 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05342 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98008-01 | Touch contact with blind flange of other line. Cladding to be revised for common solution | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05343 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98008-01 | Piping Insulation to be completed (Vent) | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05344 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98008-02 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05345 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98008-02 | Mastic missing on support | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05346 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98008-02 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05347 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98009-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05348 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98010-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05349 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98003-01 | Loose bolts on flange connection. Flange connection not aligned | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05350 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98003-01 | Handwheel missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05351 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98003-01 | Loose plug | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05352 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98003-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05353 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98006-01 | Pipe spool not connected to pump | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05354 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98006-01 | Paint touch up for valve handwheel to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05355 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98006-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-06 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05356 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98020-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05357 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98021-01 | Support not properly resting on steel structure | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05358 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98021-01 | Orifice missing (810-FE-9840) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05359 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98021-01 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05360 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98021-01 | Mastic missing on support | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05361 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98021-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05362 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98021-02 | Paint touch up for valve handwheel to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05363 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98021-02 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05364 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98035-01 | Valve orientation stem west. Isometric drawing to be updated | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-06 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05365 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98035-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05366 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98036-01 | Rusted nuts on embedded plate | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05367 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98036-01 | Mastic missing on support | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05368 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98036-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05369 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00102-02 | Orifice missing (810-FO-9830) | A | EM | HEC MR Design | Mr. Maciej Smalira | 2022-09-06 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05370 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00102-02 | Short bolts (810-FV-9830) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05371 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00102-02 | Loose bolts and Short bolts on support | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05372 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00102-02 | Tape to be removed from valve stem | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05373 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00102-02 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05374 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00102-01 | Insulation in touch contact with toe plate | B | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05375 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00102-01 | Mastic missing on elbows | B | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05376 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00102-01 | Insulation straps to be installed properly | B | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05377 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00102-01 | Rusted cladding bolts | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05378 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00102-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05379 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00102-01 | Paint touch up for valve handwheel to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05380 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98022-01 | Guides missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05381 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98022-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05382 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98022-01 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05383 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98022-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05384 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98022-01 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05385 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98022-01 | Indication tube horizontal position | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05386 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98023-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05387 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98025-01 | Traces of rust to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05388 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98026-01 | Guides missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05389 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98026-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05390 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98026-01 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05391 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98026-01 | Indication tube horizontal position | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05392 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98019-01 | Orifice missing (810-FE-9839) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05393 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98019-01 | Paint touch up for valve handwheel to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05394 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98019-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05395 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98034-01 | Rusted nuts on embedded plate | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05396 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98034-01 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05397 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98034-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05398 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98018-01 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05399 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98018-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05400 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98013-01 | Paint touch up for valve handwheel to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05401 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98013-01 | Mastic missing on support | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05402 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98013-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05403 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98016-01 | Paint touch up for valve handwheel to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05404 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98016-01 | Mastic missing on support | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05405 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98016-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05406 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00101-01 | Item no.10 & 11 not installed (Gate valve & 810-AP-1011) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05407 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00101-01 | Instrument missing (810-AT-1011) | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-10 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 05408 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00101-01 | Continuation drawing wrong numbering on sheet number. Drawing to be updated | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-06 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05409 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98031-01 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05410 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98031-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-11-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05411 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98032-01 | Piping Insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05412 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98032-01 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05413 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98033-01 | Guides missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05414 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98033-01 | Piping Insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05415 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98033-01 | Pipe wall pass through not finished (not sealed) | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05416 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW98033-01 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05417 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00113-02 | Insulation in touch contact with toe plate | B | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05418 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00113-02 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05419 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00113-01 | Rusted nuts on embedded plate | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05420 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00113-01 | Piping Insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05421 | 810.10 | 810-10-20 | 810WS | 810WS-900DMW02101-03 | Paint touch up for valve handwheel to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05422 | 810.10 | 810-10-20 | 810WS | 810WS-900DMW02101-03 | Piping Insulation to be completed. Damage cladding to be replaced | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-06 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05423 | 810.10 | 810-10-20 | 810WS | 810WS-900DMW02101-02 | Rusted nuts on embedded plate | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05424 | 810.10 | 810-10-20 | 810WS | 810WS-900DMW02101-02 | Paint touch up for valve handwheel to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05425 | 810.10 | 810-10-20 | 810WS | 810WS-900DMW02101-02 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05426 | 810.10 | 810-10-20 | 810WS | 810WS-900DMW02101-01 | Mastic missing on support | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05427 | 810.10 | 810-10-20 | 810WS | 810WS-900DMW02101-01 | Mastic missing on reducer | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05428 | 810.10 | 810-10-20 | 810WS | 810WS-900DMW02101-01 | Damaged cladding to be replaced. Rusted scratch on cladding | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05429 | 810.10 | 810-10-20 | 810WS | 810WS-900DMW02101-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05430 | 810.10 | 810-10-20 | 810PR | 810PR-900DMW02101-02 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05431 | 810.10 | 810-10-20 | 810PR | 810PR-900DMW02101-02 | Cladding on support not properly installed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05432 | 810.10 | 810-10-20 | 810PR | 810PR-900DMW02101-02 | Mastic on support not sealed completely. Rusted cladding and gap at cladding overlap | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05433 | 810.10 | 810-10-20 | 810PR | 810PR-900DMW02101-02 | Piping Insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05434 | 810.10 | 810-10-20 | 810PR | 810PR-900DMW02101-01 | Valve to be cleaned and touch up paint to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05435 | 810.10 | 810-10-20 | 810PR | 810PR-900DMW02101-01 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05436 | 810.10 | 810-10-20 | 810PR | 810PR-900DMW02101-01 | Incorrect Instrument tag (900-PG-2104) | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05437 | 810.10 | 810-10-20 | 810PR | 810PR-900DMW02101-01 | Mastic on support not sealed completely | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05438 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00112-01 | Paint touch up for support to be done (line stopper rusted) | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05439 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00112-01 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05440 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00113-03 | Valve orientation stem west. Isometric drawing to be updated | B | EM | HEC PI Design | Mr. Jakub Partyka | 2022-09-06 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05441 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00113-03 | Paint touch up for support to be done | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05442 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00113-03 | Piping Insulation missing | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05443 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW15101-01 | Loose bolts and nuts (810-AR-001) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05444 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW16101-01 | Tank nozzle traces of rust | B | ME | HEC ME Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 05445 | 810.10 | 810-10-20 | 810WS | 810WS-810DMW00111-01 | Tank nozzle traces of rust | B | ME | HEC ME Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06383 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing System | AB-810WT-CH-1003 | Air Blowing | A | COMM | HEC COMM | Ms. Paulina Bajer | 2022-09-09 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06384 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing System | AB-810WT-CH-1004 | Air Blowing | A | COMM | HEC COMM | Ms. Paulina Bajer | 2022-09-09 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06385 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing System | 810WT-CH-1003 (IN) | Final Insulation | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-09 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06386 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing System | 810WT-CH-1004 (IN) | Final Insulation | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-09 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06387 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing System | 810-BPV-9611 | Inspection for Calibration / Installation | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-09-09 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06388 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing System | 810-BPV-9612 | Inspection for Calibration / Installation | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-09-09 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06389 | 810.10 | 810-10-38 | AUX/Raw Water Shelter | 810-PT-9611/9621/9631 | All manifold drain/vent plug of pressure transmitter are missing | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-09-09 | 2022-10-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06390 | 810.10 | 810-10-38 | AUX/Raw Water Shelter | 810-X006-P01A/B/C | Provide grommet for the edge of cable tray near to JB | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-09-09 | 2022-10-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06391 | 810.10 | 810-10-38 | AUX/Raw Water Shelter | General | Replace the blind plug for all spare cable entry of instrument with Atex specification | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-09-09 | 2022-10-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06392 | 810.10 | 810-10-38 | AUX/Raw Water Shelter | General | Provide additional cable tray for the long cable of instrument | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-09-09 | 2022-12-09 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 06393 | 810.10 | 810-10-38 | AUX/Raw Water Shelter | General | Make a proper bend & correct loop arrangement of long cable for all instrument | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-09-09 | 2022-11-09 | Walkdown |  |  | 2022-11-08 | [5 empty] | RFC/RFSU
. | 06394 | 810.10 | 810-10-38 | AUX/Raw Water Shelter | General | Initial Atex inspection to be done | B | PER | HEC permit team | Owner Maintenance team | 2022-09-09 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06395 | 810.10 | 810-10-38 | AUX/Raw Water Shelter | 810-PG-9613/9623/9633 | On all pressure gauge drain/vent line side are missing | A | ME | HEC ME Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-09 | 2022-11-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06396 | 810.10 | 810-10-38 | AUX/Raw Water Shelter | 810-PG-9633 | The drain line side of pressure gauge is broken | A | ME | HEC ME Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-09 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06397 | 810.10 | 810-10-38 | AUX/Raw Water Shelter | General | No ground cable for all instrument | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-09 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06398 | 810.10 | 810-10-38 | AUX/Raw Water Shelter | 810-LT-9603 | Mounting installation & cable glanding of level transmitter should be tightened properly | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-09 | 2022-10-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06399 | 810.10 | 810-10-38 | AUX/Raw Water Shelter | General | Vendor labeling/cable tag from JB to instrument shall be change with HEC approved document tag | C | CI | HEC CI Construction | Owner Maintenance team | 2022-09-09 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06400 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006-ST01 | BA 96206 handle to be fixed | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06401 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006-ST01 | 810-PG-96103 to be fixed | A | EM | HEC MR Design | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2022-11-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06402 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006-ST01 | U bolt to in line with BA 96303 be tigthened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2022-10-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06403 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006-ST01 | 810-PG-9623 to be fixed | A | EM | HEC MR Design | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2022-11-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06404 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006-ST01 | BA96107 missing bolt on handle to be replaced and tigthened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06405 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006-ST01 | Missing nameplate on the motor | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2023-03-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06406 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006-ST01 | XV9882 loose bolt on handle to be fixed | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2022-10-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06407 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006-ST01 | Missing nameplate on the tank | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2023-03-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06408 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006-ST01 | Loose bolt on top of the tank to be tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06409 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006-ST01 | CS nut to be replaced with galvanized nut | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06410 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006 | Platform and portable ladder to be provided on the skid | C | EM | HEC MR Design | Mr. Krzysztof Kaliszyk | 2022-09-09 |  | Walkdown | [8 empty] | RFC/RFSU
. | 06411 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006-ST01 | Crack on the flange to be repaired | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2023-02-08 | Walkdown |  |  |  | DA | V |  |  |  | RFC/RFSU
. | 06412 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006-ST01 | Housekeeping to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06413 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006-ST01 | Missing bolt on the anchor to be provided | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2022-10-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06414 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006 | Permanent blind to be installed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06415 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006 | U-bolt at line 810-1"-CH-96124-C1A0 to be fixed and tigthened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2022-10-18 | Walkdown | [8 empty] | RFC/RFSU
. | 06416 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006 | Flange to flange connection with damage paint to be repaired | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06417 | 810.10 | 810-10-38 | 810-X0006 | 810-X0006 | CH-96401 & CH96301 CS flange and SS bolt and nuts to be verefied | C | EM | HEC MR Design | Mr. Krzysztof Kaliszyk | 2022-09-09 | 2023-03-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06418 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing | 810-X0006 | Safety switches do not meet the Machinery Directive 06/42 / EC- Polish law, Ordinance of the Ministry of Economy of October 21, 2008 in clause 1.2.4.3 "The emergency stop device must: be equipped with CLEARLY RECOGNIZABLE, VISIBLE and QUICKLY ACCESSIBLE controls." | C | EM | HEC EL Design | Mr. Krzysztof Nolbert | 2022-09-12 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06419 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing | 810-X0006 | There are not possible easy identificated drive related to cooperated control panel | B | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-12 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06420 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing | 810-X0006 | Blind flange not installed | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-09-12 | 2022-10-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06421 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing | 810-X0006 | Part of instruments not properly installed | A | EM | HEC MR Design | Mr. Krzysztof Nolbert | 2022-09-12 | 2022-11-21 | Walkdown | 2022-11-18 | 2022-11-21 |  |  | V |  |  |  | RFC/RFSU
. | 06422 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing | 810-X0006 | Anti acid coating to be provided | B | AR | HEC AR Construction | Ms. Paulina Bajer | 2022-09-12 | 2022-12-14 | Walkdown | 9/19: Disp. change CV->AR | 'Punch Category' changed A -> B (2022-11-15) evidence attached |  |  | V |  |  |  | RFC/RFSU
. | 06423 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing | 810-X0006 | Manual valve downstream of the tank (nozzle N2) to be relocated in P&ID to line no. 810-1''-CH-96101-C1A0-N) | B | EM | HEC PR Design | Ms. Paulina Bajer | 2022-09-12 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06424 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing | 810-X0006 | PG-9613/PG-9623 - to installed properly (loose bolts) | A | EM | HEC MR Design | Ms. Paulina Bajer | 2022-09-12 | 2022-11-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06425 | 810.10 | 810-10-38 | Clarifier Coagulant Dosing | 810-X0006 | Insulation missing at coagulant lines outside of the building. | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-09-12 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06426 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93025-01 | Pipeline is shaking. Additional hold down support to be considered | A | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-06 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06427 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93025-01 | Guides installed. No support indication on the drawing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06428 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93025-01 | Hardrail to be modified. Too close to pipeline | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06429 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93025-01 | Out of level. Support to be adjusted | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-10-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06430 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93025-01 | Rusted plug to be painted | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06431 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93027-01 | Pipeline is shaking. Additional hold down support to be considered | A | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-06 | 2022-10-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06433 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93027-01 | Tape to be removed from valve handwheel | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06434 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93027-01 | Rusted plug to be painted | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06435 | 810.10 | 810-10-32 | 810WT | 810WT-810CH93001-01 | Valve not installed (810-BPV-9381) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06436 | 810.10 | 810-10-32 | 810WT | 810WT-810CH93001-01 | Short bolts on flange connection (810-X0003-M01) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06437 | 810.10 | 810-10-32 | 810WT | 810WT-810CH93001-01 | Valve stem wrong orientation as per drawing (actual west) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06438 | 810.10 | 810-10-32 | 810WT | 810WT-810CH93001-01 | Rusted weld joint to be cleaned | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06439 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93026-01 / 810WT-810WW93028-01 | Loose bolts on flange connection (Centrifuge) | A | ME | HEC ME Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-09-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06440 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93026-01 / 810WT-810WW93028-01 | Flange connection to be cleaned (Centrifuge) | B | ME | HEC ME Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06441 | 810.10 | 810-10-32 | 810WT | 810WT-810WW06102-01 | Figure 8 rusted. To be cleaned. | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06442 | 810.10 | 810-10-32 | 810WT | 810WT-810WW06102-01 | Figure 8 covered by plastic to be removed | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06443 | 810.10 | 810-10-32 | 810WT | 810WT-810WW06102-01 | Pipeline wall pass through mark missing. To be reflected in ISO drawing. | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-06 | 2022-10-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06444 | 810.10 | 810-10-32 | 810WT | 810WT-810WW06102-01 | Pipeline touching sandwich wall | C | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-06 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06445 | 810.10 | 810-10-32 | 810WT | 810WT-810WW06102-01 | Tape, Tags, Markings to be removed and Touchup paint to be done. | B | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-10-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06446 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93001-01 / 810WT-810WW93002-01 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06447 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93001-01 / 810WT-810WW93002-01 | Tape, Tags, Markings to be removed and Touchup paint to be done. | B | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06448 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93001-01 / 810WT-810WW93002-01 | Instrument missing (810-AT-9312) | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-12-02 | Walkdown |  | 2022-11-22 | 2022-11-21 |  | V |  |  |  | RFC/RFSU
. | 06449 | 810.10 | 810-10-32 | 810WT | 810WT-810WW06101-01 | Figure 8 rusted. To be cleaned. | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06450 | 810.10 | 810-10-32 | 810WT | 810WT-810WW06101-01 | Figure 8 covered by plastic to be removed | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06451 | 810.10 | 810-10-32 | 810WT | 810WT-810WW06101-01 | Guides installed. No support indication on the drawing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06452 | 810.10 | 810-10-32 | 810WT | 810WT-810WW06101-01 | Tape, Tags, Markings to be removed and Touchup paint to be done. | B | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06453 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93021-01 | Rusted screws on valve visor. To be change to SS | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-06 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06454 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93021-01 | Instrument missing (810-PG-9332) | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06455 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93021-01 | Piping Insulation not installed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06456 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93022-01 | Piping Insulation not installed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06457 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93031-01 | Valve visor missing | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06458 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93031-01 | Rusted screws on valve visor. To be change to SS | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-06 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06459 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93031-01 | Instrument missing (810-PG-9342) | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06460 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93031-01 | Piping Insulation not installed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06461 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93032-01 | Piping Insulation not installed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06462 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93032-01 | Touch up paint to be done | B | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-10-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06463 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93024-01 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-09-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06464 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93024-01 | Instrument missing (810-PT-9333) | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-08 | Walkdown |  |  | 2022-11-08 |  | V |  |  |  | RFC/RFSU
. | 06465 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93024-01 | Piping Insulation not installed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06466 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93024-02 | Piping Insulation not installed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06467 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93024-03 | Valve visor to be cleaned from paint | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06468 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93024-03 | Paint touch up for Support to be done. | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-11-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06636 | 810.10 | 810-10-18 | 810WT | 810WT‐810SW00123‐01 | Rusted screws on valve visor. To be changed to SS | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-06 | 2023-03-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 06637 | 810.10 | 810-10-18 | 810WT | 810WT‐810SW00123‐01 | Touch up paint to be done for valve, pipe and support | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-06 | 2022-10-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 7410 | 810.10 | 810-10-32 | 810WT | 810WT-810WW93027-01 | Out of level. Support to be adjusted | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-06 | 2022-10-04 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12339 | 810.10 | 810-10-42 | Fire Water Pump System | EGAT-HEC-200-HSE-PID-00201 | Duct Sealing to be provided for stub-up conduit pipe | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-04 | 2023-01-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12340 | 810.10 | 810-10-42 | Fire Water Pump System | EGAT-HEC-200-HSE-PID-00201 | Grommet to be provided for the sharp edge of the cable tray for 810-MP0004 A/B panel side. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-04 | 2023-01-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12341 | 810.10 | 810-10-42 | Fire Water Pump System | EGAT-HEC-200-HSE-PID-00201 | Cable tray cover to be provided | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-04 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12342 | 810.10 | 810-10-42 | Fire Water Pump System | EGAT-HEC-200-HSE-PID-00201 | Cable scratch to be cover with raychem heat shrink sleeve for LP.820-MP0005A at intermediate JB side. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-04 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12343 | 810.10 | 810-10-42 | AUX Area | 810-P0005A | Missing Pressure gauge PG-1008/1009 | A | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12344 | 810.10 | 810-10-42 | AUX Area | 810-P0005B | Missing Pressure Gauge PG-1011/1010 | A | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12345 | 810.10 | 810-10-42 | AUX Area | 810-P0005A/B | Oil leveller - loose / leakage to be fixed / no oil | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12346 | 810.10 | 810-10-42 | AUX Area | 810-P0005A/B | Coupling cover fasteners to be replaced (installed with different bolts and nuts) | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12347 | 810.10 | 810-10-42 | AUX Area | General | No nameplates (nameplates installed does not indicate the pump tag number - 810-P0005A/B, 0004A/B and diesel tank) | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2023-03-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12348 | 810.10 | 810-10-42 | AUX Area | 810-P0005A/B | Painting documentation to be provided - pump base were painted at site - proper inspectin to be implemented | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 |  | Walkdown | [8 empty] | RFC/RFSU
. | 12349 | 810.10 | 810-10-42 | AUX Area | 810-P0005A | PRV-0008 to be installed | A | CI | HEC CI Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12350 | 810.10 | 810-10-42 | AUX Area | 810-P0005A/B | Grease fitting cover missing | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12351 | 810.10 | 810-10-42 | AUX Area | General | Housekeeping | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12352 | 810.10 | 810-10-42 | AUX Area | General | Expansion joints on suction/ discharge proper setting to be done (810-P0005A/B, P0004A/B) | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12353 | 810.10 | 810-10-42 | AUX Area | 810-P0004A | Mounting bolt washers are small and need to be replaced | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-12-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12354 | 810.10 | 810-10-42 | AUX Area | 810-P0004A | Coupling cover to be fixed | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12355 | 810.10 | 810-10-42 | AUX Area | 810-P0004A | Terminal box paint damage to be touched-up | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12356 | 810.10 | 810-10-42 | AUX Area | 810-P0004A | Copper tube on top of pump are loose - to be tightened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12357 | 810.10 | 810-10-42 | AUX Area | 810-P0004A | Pump skid - base underneath are not painted | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2023-03-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12358 | 810.10 | 810-10-42 | AUX Area | 810-P0004A | Painting documentation to be provided - pump base were painted at site - proper inspectin to be implemented | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 |  | Walkdown | [8 empty] | RFC/RFSU
. | 12359 | 810.10 | 810-10-42 | AUX Area | 810-P0004A | 3/4 OY drain - 1 line plumbness to be corrected | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12360 | 810.10 | 810-10-42 | AUX Area | 810-P0004A | Pump screen cover to be fixed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12361 | 810.10 | 810-10-42 | AUX Area | 810-P0004A | Grease fitting cover missing | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12362 | 810.10 | 810-10-42 | AUX Area | 810-P0004A | Local Platform touch-up to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2023-03-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12363 | 810.10 | 810-10-42 | AUX Area | 810-P0004A | Local Panel touch-up and cleaning | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12364 | 810.10 | 810-10-42 | AUX Area | 810-P0004B | Exhaust pipe temporary support the wall to be removed | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12365 | 810.10 | 810-10-42 | AUX Area | General | Stud bolt for stainless flange connection to be verified | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12366 | 810.10 | 810-10-42 | AUX Area | General | Touch-up painting | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12367 | 810.10 | 810-10-42 | AUX Area | 810-P0004B | Copper tube on top of pump are loose - to be tightened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12368 | 810.10 | 810-10-42 | AUX Area | 810-P0004B | Pump screen cover to be fixed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12369 | 810.10 | 810-10-42 | AUX Area | 810-P0004B | Battery to be installed and rack cover protection needed. | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2023-01-31 | Walkdown |  |  |  | HEC | V |  |  |  | RFC/RFSU
. | 12370 | 810.10 | 810-10-42 | AUX Area | 810-P0004B | Exhaust bellow are rusted | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12371 | 810.10 | 810-10-42 | AUX Area | 810-P0004B | Coupling cover to be fixed | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12372 | 810.10 | 810-10-42 | AUX Area | 810-P0004B | Check valve on line # 810-1/2"-FW-20030-MS-1-N (Vendor side) direction not correct. | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12373 | 810.10 | 810-10-42 | AUX Area | 810-P0004B | Line # 810-1/2"-FW-20041-MS-1-N is shaking - additional support to be installed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-12-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12374 | 810.10 | 810-10-42 | AUX Area | 810-P0004B-ST | Fuel tank Overflow line and drain line is connected to ditch and not inside the dike wall as per P&ID - to be corrected | A | EM | HEC PI Design | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12375 | 810.10 | 810-10-42 | AUX Area | 810-P0004B-ST | Protection and information of overflow during fuel filling on tank is not cleared - Alarm or monitoring system for during overflow to be provided. | B | EM | HEC SE Design | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12376 | 810.10 | 810-10-42 | AUX Area | 810-P0004B-ST | Grating on open ditch floor openings to be installed | B | AR | HEC AR Construction | Mr. Krzysztof Kaliszyk | 2022-11-04 | 2022-12-08 | Walkdown |  | 'Punch Category' changed A -> B (2022-11-30) evidence attached |  |  | V |  |  |  | RFC/RFSU
. | 12377 | 810.10 | 810-10-42 | AUX Area | 810-P0004A | Final Inspection of 810-P0004A to be done | A | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12378 | 810.10 | 810-10-42 | AUX Area | 810-P0004B | Final Inspection of 810-P0004B to be done | A | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12379 | 810.10 | 810-10-42 | AUX Area | 810-P0005B | Final Inspection of 810-P0005B | A | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12380 | 810.10 | 810-10-42 | AUX Area | 810WT-AV-1001 | Final Appeareance Inspection | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-04 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12381 | 810.10 | 810-10-42 | AUX Area | 810-P0004A | Motor Solo Run for 810-MP0004A to be done | A | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12382 | 810.10 | 810-10-42 | AUX Area | 810-FE-1007 | 810-FE-1007: inspection for installation to be done | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12383 | 810.10 | 810-10-42 | AUX Area | 810-FT-1007 | 810-FT-1007: Inspection for Calibration to be done | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12384 | 810.10 | 810-10-42 | AUX Area | 810-PRV-0006 | 810-PRV-0006:Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12385 | 810.10 | 810-10-42 | AUX Area | 810-PRV-0008 | 810-PRV-0008: Inspection for Calibration / Installation to be done | A | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2022-11-04 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12386 | 810.10 | 810-10-42 | AUX Area | 810-PRV-0009 | 810-PRV-0009: Inspection for Calibration / Installation to be done; hanging tag missing | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12387 | 810.10 | 810-10-42 | AUX Area | WF-810WT-FW-1004 | Water Flushing (WF-810WT-FW-1004) to be done | A | COMM | HEC COMM | Ms. Paulina Bajer | 2022-11-04 | 2022-11-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12388 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00202 | PG-1006 not installed | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12389 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00202 | PG-1007 not installed | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12390 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00201 | PG-1008 not installed | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12391 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00201 | PG-1009 not installed | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12392 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00201 | PG-1010 not installed | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12393 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00201 | PG-1011 not installed | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12394 | 810.10 | 810-10-42 | AUX Area | General comment | Spacers instead of spectacle blinds installed at Site in comparison to P&ID | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2022-11-04 | 2023-02-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12395 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00202 | PRV-0006 - missing tag id | B | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2022-11-04 | 2022-11-23 | Walkdown |  | 2022-11-18 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12396 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00202 | PRV-0007 - missing tag id | B | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2022-11-04 | 2022-11-23 | Walkdown |  | 2022-11-18 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12397 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00202 | All drain and overflow lines from Diesel Tank should be routed to the tank curbed area instead of directly to the OY | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12398 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00202 | Line no. 810-14''-FW-20006-MS-1-N: handhweel for manual valve not installed | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-11-04 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12399 | 810.10 | 810-10-42 | AUX Area | 810-12''-FW-00118-MS-1-N | Line no. 810-12''-FW-00118-MS-1-N: pin missing for LC valve | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-11-04 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12400 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00203 | Minimum distance 1,5m between check valves should be provided | C | EM | HEC MR Design | Mr. Damian Maciejaszek | 2022-11-04 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12401 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00204 | Check valves direcition on pressure sensing line to be verified in P&ID; note 11 ion P&ID to be verified | B | EM | HEC SE Design | Mr. Damian Maciejaszek | 2022-11-04 | 2023-01-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12402 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00201 | rubber handle for manual valve on drain line form the pump to be provided | B | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2022-11-04 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12403 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00202 | EXPJ-008: missing nameplate | B | PI | HEC PI Construction | Mr. Jakub Szukszta | 2022-11-04 | 2022-11-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12404 | 810.10 | 810-10-42 | AUX Area / 810-SHT-CC-300 | EGAT-HEC-200-HSE-PID-00202 | Pit to be cleaned and dewatered | A | AR | HEC CV Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12405 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00202 | LG-1002: missing hanging tag | B | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2022-11-04 | 2022-11-23 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12406 | 810.10 | 810-10-42 | AUX Area / 810-SHT-CC-300 | EGAT-HEC-200-HSE-PID-00202 | Cover for pit to be provided | A | AR | HEC CV Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12407 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00202 | Drain valve downstream of PRV-0006 to be specified in P&ID | B | EM | HEC SE Design | Ms. Małgorzata Juszczyk | 2022-11-04 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12408 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00203 | PG-1004 not installed | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12409 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00203 | PG-1005 not installed | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12410 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00203 | missing handwheels for LO valves on fire water lines to loop network and 810-P0004B | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-11-04 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12411 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00203 | missing pin fo LC valve (line no. 810-12''-FW-00118-MS-1-N) | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-11-04 | 2022-11-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12412 | 810.10 | 810-10-42 | AUX Area | EGAT-HEC-200-HSE-PID-00203 | PG-2973 not installed | A | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-04 | 2023-01-25 | Walkdown |  |  | 2023-01-25 |  | V |  |  |  | RFC/RFSU
. | 12413 | 810.10 | 810-10-42 | AUX Area | 810-FT-1007 | FT-1007: insulation not completed | B | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-04 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12414 | 810.10 | 810-10-42 | AUX Area | 810-FT-1007 | FT-1007: loose cable for electrical tracing | B | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-11-04 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12415 | 810.10 | 810-10-42 | AUX Area | Fire Water Tank | Manual valves on fire water lines to the tank: pins to be replaced | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-11-04 | 2022-11-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12416 | 810.10 | 810-10-42 | AUX Area | Fire Water Tank | Fire Water line from PSV: locking device to be provided for CSO valve. | C | COMM | HEC COMM | Ms. Małgorzata Juszczyk | 2022-11-04 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12417 | 810.10 | 810-10-42 | AUX Area | Common | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-11-04 | 2023-04-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12418 | 810.10 | 810-10-42 | AUX Area | Common | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-04 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12419 | 810.10 | 810-10-42 | AUX Area | Common | Nameplates for pumps to be provided | C | ME | HEC ME Construction | Ms. Alicja Sulżyc | 2022-11-04 |  | Walkdown | [8 empty] | RFC/RFSU
. | 12420 | 810.10 | 810-10-42 | AUX Area / 810-SHT-CC-300 | Common | Grating to be provided for trench | A | CV | HEC CV Construction | Ms. Alicja Sulżyc | 2022-11-04 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12421 | 810.10 | 810-10-42 | Fire Water pumps | General | Damaged glanding on motor junction box - visible welding mark | A | EL | HEC EL Construction | Owner Maintenance team | 2022-11-04 | 2023-01-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 12422 | 810.10 | 810-10-42 | Fire Water pumps | General | Glanding shall be tightened | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12423 | 810.10 | 810-10-42 | Fire Water pumps | General | Replace the blind plug of instrument with Atex specification | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-11-17 | Walkdown |  | 2022-11-17 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 12424 | 810.10 | 810-10-42 | Fire Water pumps | General | Loose grounding, shall be tightened | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-11-30 | Walkdown |  | 2022-11-29 | 2022-11-29 |  | V |  |  |  | RFC/RFSU
. | 12425 | 810.10 | 810-10-42 | Fire Water pumps | General | The warning labels shall be bilignual (Polish labels shall be added) | C | ME | HEC ME Construction | Owner Maintenance team | 2022-11-04 |  | Walkdown | [8 empty] | RFC/RFSU
. | 12426 | 810.10 | 810-10-42 | Fire Water pumps | General | Provide grommet for cable tray | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-04 | 2022-11-23 | Walkdown |  | 2022-11-22 | 2022-11-21 |  | V |  |  |  | RFC/RFSU
. | 13095 | 810.10 | 810-10-26 |  | 810-ST0002 | Final Inspection | A | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-11-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13096 | 810.10 | 810-10-26 |  | 300UG-DMW-SD-0001 | Re-instatement (300UG-DMW-SD-0001) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-11-08 | 2022-11-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13097 | 810.10 | 810-10-26 |  | 810-TT-1018 | Inspection for Cable Pulling / Termination / IR Test / Installation / Calibration | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13098 | 810.10 | 810-10-26 |  | 810-FT-1018 | Inspection for Calibration / Hook-up Installation | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13099 | 810.10 | 810-10-26 |  | 810-FT-1019 | Inspection for Calibration / Hook-up Installation | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13100 | 810.10 | 810-10-26 |  | 810-FT-1020 | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13101 | 810.10 | 810-10-26 |  | 810-LT-1026 | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13102 | 810.10 | 810-10-26 |  | 810-LT-1027 | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13103 | 810.10 | 810-10-26 |  | 810-PG-1011 | Inspection for Installation | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13104 | 810.10 | 810-10-26 |  | 810-PRV-0003 | Inspection for Installation | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13105 | 810.10 | 810-10-26 |  | 810-PT-1031 | Inspection for Calibration / Hook-up Installation | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13106 | 810.10 | 810-10-26 |  | 810-PT-1034 | Inspection for Calibration / Hook-up Installation | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13107 | 810.10 | 810-10-26 |  | 810-TE-1005 | Inspection for Installation / Calibration | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13108 | 810.10 | 810-10-26 |  | 810-TE-1006 | Inspection for Installation / Calibration | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13109 | 810.10 | 810-10-26 |  | 810-TG-1018 | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13110 | 810.10 | 810-10-26 |  | 810-TT-1005 | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13111 | 810.10 | 810-10-26 |  | 810-TT-1006 | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13112 | 810.10 | 810-10-26 |  | 810-TT-1008 | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13113 | 810.10 | 810-10-26 |  | 810-TW-0001 | Inspection for Calibration | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13114 | 810.10 | 810-10-26 |  | 840-FT-1003 | Inspection for Calibration / Hook-up Installation | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-08 | 2022-11-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13116 | 810.10 | 810-10-26 |  | 810WS-DMW-1003 | Final Appeareance Inspection | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-12-12 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13117 | 810.10 | 810-10-26 |  | 300PR-DMW-2002 | Final Appeareance Inspection | A | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-11-23 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13118 | 810.10 | 810-10-26 |  | 810WS-DMW-1005 | Final Appeareance Inspection | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-12-12 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13119 | 810.10 | 810-10-26 |  | 810-P0007A/B (IN) | Final Appeareance Inspection | A | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-11-23 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13120 | 810.10 | 810-10-26 | Demi Water Storage and Supply System | EGAT-HEC-810-PRO-PID-00151A~J | Provide yellow tag sticker for LCS EMERGENCY PUSH BOTTON at cover side written with Polish Language [ WYŁĄCZNIK AWARYJNY ] for ( Tag no:-810-MP0007A/B) | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-08 | 2022-11-23 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13121 | 810.10 | 810-10-26 | Demi Water Storage and Supply System | EGAT-HEC-810-PRO-PID-00151A~J | Duct Sealing to be done for the Stub-up Conduit. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-08 | 2022-11-14 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13122 | 810.10 | 810-10-26 | Demi Water Storage and Supply System | Common | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-11-08 | 2023-05-08 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13123 | 810.10 | 810-10-26 | Demi Water Storage and Supply System | Common | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-08 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 13124 | 810.10 | 810-10-26 |  | EGAT-HEC-300-PRO-PID-90541 | Insulation to be completed | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-08 | 2023-04-06 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13125 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Cover to be provided for pit | C | CV | HEC CV Construction | Ms. Paulina Bajer | 2022-11-08 | 2023-04-14 |  | Gusan |  |  |  | V |  |  |  | RFC/RFSU
. | 13126 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Grounding for LT-1026 to be connected | A | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-11-25 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13127 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Hanging tags missing for PSV-0007A/B | B | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-11-30 |  |  | 2022-11-28 | 2022-11-28 |  | V |  |  |  | RFC/RFSU
. | 13128 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Spectacle blind instead of spacer to be specified in P&ID in vent line | B | EM | HEC PR Design | Ms. Małgorzata Juszczyk | 2022-11-08 | 2022-11-21 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13129 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Rusted bolts | B | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-11-08 | 2022-11-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13130 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Housekeeping of the roof to be done | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-12-22 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13131 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Sampling point 8113: unable to take a sample | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-11-08 | 2022-11-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13132 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Sampling point 8113: corrosion to be removed | B | PA | HEC PA Construction | Ms. Małgorzata Juszczyk | 2022-11-08 | 2022-12-07 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13133 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Manual valve on nitrogen line unable to operate | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-11-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13134 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Railings to be adjusted | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-12-22 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13135 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Rusted valves | B | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-12-15 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13136 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Stairs to be completed | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-12-22 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13137 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Gratings to be adjusted at tank body | B | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-12-22 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13138 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Electrical tracing to be provided for bypass of TV-1005 | B | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-11-08 | 2023-01-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13139 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | Insulation to be provided for bypass of TV-1005 | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-08 | 2023-02-17 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13140 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | plug instead of end flange provided for drain valve on line no. 810-14''-DMW-00103-L1A0-ET | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-11-08 | 2022-11-17 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13141 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161 | rusted spectacle blind on LS line | B | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-11-08 | 2022-11-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13142 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00161/171 | Locking device to be provided | C | COMM | HEC COMM | Ms. Małgorzata Juszczyk | 2022-11-08 | [10 empty] | RFC/RFSU
. | 13143 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00171 | No access to the valve on pump discharge line (pump B) | C | EM | HEC PI Design | Ms. Paulina Bajer | 2022-11-08 | [6 empty] | V |  |  |  | RFC/RFSU
. | 13144 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00171 | Sampling point no. 8114: unable to take a sample | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-11-08 | 2022-11-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13145 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00171 | Sampling point no. 8114: ET to be provided | B | EL | HEC EL Construction | Ms. Małgorzata Juszczyk | 2022-11-08 | 2023-01-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 13146 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00171 | Sampling point no. 8114: insultion to be provided | C | IN | HEC IN Construction | Ms. Małgorzata Juszczyk | 2022-11-08 | 2023-04-06 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13147 | 810.10 | 810-10-26 |  | common | Insulation to be completed | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-08 | 2023-04-06 | [5 empty] | V |  |  |  | RFC/RFSU
. | 13148 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00171 | Hanging tag for FT-1019 missing | B | CI | HEC CI Construction | Ms. Paulina Bajer | 2022-11-08 | 2022-11-18 |  |  | 2022-11-18 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 13149 | 810.10 | 810-10-26 |  | EGAT-HEC-840-PRO-PID-00011 | Corossion to be removed from bypass valve of FV-1003 | B | PA | HEC PA Construction | Ms. Małgorzata Juszczyk | 2022-11-08 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 13150 | 810.10 | 810-10-26 |  | EGAT-HEC-810-PRO-PID-00181 | TT-1018 not installed | A | CI | HEC CI Construction | Ms. Małgorzata Juszczyk | 2022-11-08 | 2022-11-23 |  |  | 2022-11-18 | 2022-11-17 |  | V |  |  |  | RFC/RFSU
. | 14734 | 810.10 | 810-10-36 | Clarifier Package | 810WT-WW-1007_R(PA) | Final Painting | B | PA | HEC PI Construction | Ms. Paulina Bajer | 2022-11-21 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14735 | 810.10 | 810-10-36 | Clarifier Package | 810WT-WW-1005 | Final Appeareance Inspection | B | IN | HEC IN Construction | J.W.JEONG | 2022-11-21 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14736 | 810.10 | 810-10-36 | Clarifier Package | 810WT-WW-1006 | Final Appeareance Inspection | B | IN | HEC IN Construction | J.W.JEONG | 2022-11-21 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14737 | 810.10 | 810-10-36 | Clarifier Package | 810WT-WW-1006-R | Final Appeareance Inspection | C | IN | HEC IN Construction | J.W.JEONG | 2022-11-21 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14738 | 810.10 | 810-10-36 | Clarifier Package | 810WT-WW-1007 | Final Appeareance Inspection | B | IN | HEC IN Construction | J.W.JEONG | 2022-11-21 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14739 | 810.10 | 810-10-36 | Clarifier Package | 810WT-WW-1007_R | Final Appeareance Inspection | B | IN | HEC IN Construction | J.W.JEONG | 2022-11-21 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14740 | 810.10 | 810-10-36 | Clarifier Package | 810WT-WW-1008 | Final Appeareance Inspection | B | IN | HEC IN Construction | J.W.JEONG | 2022-11-21 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14741 | 810.10 | 810-10-36 | Clarifier Package | 810-AT-9202 | Installation & Calibration, Installation w/Pressure Test | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-11-21 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14742 | 810.10 | 810-10-36 | Clarifier Package | 810-AT-9207 | Installation & Calibration, Installation w/Pressure Test | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-11-21 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14743 | 810.10 | 810-10-36 | Clarifier Package | 810-AT-9212 | Installation & Calibration, Installation w/Pressure Test | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-11-21 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14744 | 810.10 | 810-10-36 | Clarifier Package | 810-BPV-9271 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-11-21 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 14745 | 810.10 | 810-10-36 | Clarifier Package | 810-BPV-9272 | Installation & Calibration | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-11-21 | 2022-12-12 | Walkdown |  |  | 2022-12-05 |  | V |  |  |  | RFC/RFSU
. | 14746 | 810.10 | 810-10-36 | Clarifier Package | 810-FE-9201 (TAG) | Calibration | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-11-21 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14747 | 810.10 | 810-10-36 | Clarifier Package | 810-FE-9211 (TAG) | Calibration | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-11-21 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14748 | 810.10 | 810-10-36 | Clarifier Package | 810-FE-9241 (TAG) | Calibration | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-11-21 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14749 | 810.10 | 810-10-36 | Clarifier Package | 810-FE-9334 (TAG) | Calibration | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-11-21 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14750 | 810.10 | 810-10-36 | Clarifier Package | 810-JA-514 (IS) (TAG) | Installation & Calibration | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-21 | 2022-12-21 | Walkdown |  |  | 2022-12-20 |  | V |  |  |  | RFC/RFSU
. | 14751 | 810.10 | 810-10-36 | Clarifier Package | 810-JA-515 (IS) (TAG) | Installation & Calibration | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-21 | 2022-12-21 | Walkdown |  |  | 2022-12-20 |  | V |  |  |  | RFC/RFSU
. | 14752 | 810.10 | 810-10-36 | Clarifier Package | 810-PRO-PID-00021C | Anti caustic coating to be provided | B | CV | HEC Marin Const. | Ms. Alicja Sulżyc | 2022-11-21 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14753 | 810.10 | 810-10-36 | Clarifier Package | 810-PRO-PID-00021C | Removable steel cover to be provided | B | CV | HEC Marin Const. | Ms. Alicja Sulżyc | 2022-11-21 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14754 | 810.10 | 810-10-36 | Clarifier Package | 810-PRO-PID-00021C/810-X0002-P03B/C | Collision between hadwheel and insulation | B | ME | HEC ME Construction | Ms. Alicja Sulżyc | 2022-11-21 | 2023-02-01 | Walkdown |  |  |  | HEC | V |  |  |  | RFC/RFSU
. | 14755 | 810.10 | 810-10-36 | Clarifier Package | 810-PRO-PID-00021A/00021B | Sampling point 8103, 9203,9206, 9207 - discharge line to be shortened (unable to take a sample) | B | PI | HEC PI Construction | Ms. Alicja Sulżyc | 2022-11-21 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14756 | 810.10 | 810-10-36 | Clarifier Package | 810-PRO-PID-00021B | TSTR 007 not insulated | B | IN | HEC IN Construction | Ms. Alicja Sulżyc | 2022-11-21 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14757 | 810.10 | 810-10-36 | Clarifier Package | 810-PRO-PID-00021A | Insluation missing on sampling points 9201, 9202. Housekeeping to be done | B | IN | HEC IN Construction | Ms. Alicja Sulżyc | 2022-11-21 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14758 | 810.10 | 810-10-36 | Clarifier Package | 810-PRO-PID-00021A | Handwheel collision | A | PI | HEC PI Construction | Ms. Alicja Sulżyc | 2022-11-21 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14759 | 810.10 | 810-10-36 | Clarifier Package | 810-PRO-PID-00021A | SN-9201, 9202, 9204, 9205 - connection with sampling cabnet to be optimized to ensure easy access and free walkway | B | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-11-21 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14760 | 810.10 | 810-10-36 | Clarifier Package |  | BPV-9271: missing hanging tag | C | PI | HEC PI Construction | Mr. Jaroslaw Pykosz | 2022-11-21 | 2023-04-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14761 | 810.10 | 810-10-36 | Clarifier Package |  | Ladders to be completed (not installed to the ground and bars at the top of ladder and entrance gates missing) | A | SS | HEC SS Construction | Ms. Paulina Bajer | 2022-11-21 | 2022-12-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14762 | 810.10 | 810-10-36 | Clarifier Package | EGAT-HEC-810-PRO-PID-00021A | AT-9202, AT-9212: sensor to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-11-21 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14763 | 810.10 | 810-10-36 | Clarifier Package |  | end flanges instead of plugs on drain valves installled at Site | B | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-21 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14764 | 810.10 | 810-10-36 | Clarifier Package | EGAT-HEC-810-PRO-PID-00021C | drain valve (with plug) to specified in P&ID upstream of SN-9207 | B | EM | HEC PI Design | Ms. Paulina Bajer | 2022-11-21 | 2022-12-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14765 | 810.10 | 810-10-36 | Clarifier Package | EGAT-HEC-810-PRO-PID-00021C | LG-R-9261 to be rotated 90 degress to be visible for the operator. | B | CI | HEC CI Construction | Mr. Jaroslaw Pykosz | 2022-11-21 | 2022-12-12 | Walkdown |  |  | 2022-12-12 |  | V |  |  |  | RFC/RFSU
. | 14766 | 810.10 | 810-10-36 | 810-X0002-X01A | 810-X0002-X01A | Missing safety to be installed | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14767 | 810.10 | 810-10-36 | 810-X0002-X01A | 810-X0002-X01A | Missing anchor bolt of the ladder to be installed | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14768 | 810.10 | 810-10-36 | 810-X0002-X04A/B | 810-X0002-X04A/B | Missing shim on the eyebolt | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2022-12-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14769 | 810.10 | 810-10-36 | 810-X0002-X03A/B | 810-X0002-X03A/B | Platform structure to be cleaned and touch-up painting to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2023-03-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14770 | 810.10 | 810-10-36 | 810-X0002 | 810-X0002 | missing handrail to be installed | A | SS | HEC SS Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2022-12-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14771 | 810.10 | 810-10-36 | 810-X0002 | 810-X0002 | Missing cover for the basin to be installed | B | CV | HEC Marin Const. | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14772 | 810.10 | 810-10-36 | 810-X0002-M01A/B | 810-X0002-M01A/B | Touch-up painting of the motor to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2022-12-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14773 | 810.10 | 810-10-36 | 810-X0002-M02A/B | 810-X0002-M02A/B | Touch-up painting of the motor to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14774 | 810.10 | 810-10-36 | 810-X0002-P02A/B | 810-X0002-P02A/B | Loose bolt on safety cover to be tightened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14775 | 810.10 | 810-10-36 | 810-X0002-P02A/B | 810-X0002-P02A/B | Touch-up painting to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14776 | 810.10 | 810-10-36 | 810-X0002-P01B | 810-X0002-P01B | Loose oil glass to be tightened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2022-12-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14777 | 810.10 | 810-10-36 | 810-X0002-P02A/B | 810-X0002-P02A/B | Rust to be removed | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14778 | 810.10 | 810-10-36 | 810-X0002 | 810-X0002 | Shaking ladder cage to be modified | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2022-12-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14779 | 810.10 | 810-10-36 | 810-X0002-ST01 | 810-X0002-ST01 | Houskeeping to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14780 | 810.10 | 810-10-36 | 810-X0002-ST01 | 810-X0002-ST01 | Manhole cover to be tightened | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14781 | 810.10 | 810-10-36 | 810-X0002-ST01 | 810-X0002-ST01 | Access to skid to be provided ( Grating ) | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-21 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14782 | 810.10 | 810-10-36 |  | common | Housekeeping to be done in clarifier area (scaffolding to be removed, all materials left after construction works, sharp objects, rubbish to be removed) | C | ME | HEC ME Construction | Ms. Paulina Bajer | 2022-11-21 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14786 | 810.10 | 810-10-36 |  | EGAT-HEC-810-PRO-PID-00021A | HSCN-003, HSCN-005: chain to be provided | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-21 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14787 | 810.10 | 810-10-36 |  | EGAT-HEC-810-PRO-PID-00021A | Funnel to be provided for SN-9201/9202 | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-21 | 2023-01-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14788 | 810.10 | 810-10-36 |  | Common | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PI Construction | Ms. Paulina Bajer | 2022-11-21 | 2023-04-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14789 | 810.10 | 810-10-36 |  | Common | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-21 |  | Walkdown | [8 empty] | RFC/RFSU
. | 14791 | 810.10 | 810-10-36 | Clarifier Package |  | Tagging for sampling points to be provided | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-21 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14792 | 810.10 | 810-10-36 | Clarifier Package | 810-FT-9201 | Rearrange signal Exi cable | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-21 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14793 | 810.10 | 810-10-36 | Clarifier Package | 810-LT-9204, 810-LT-9214 | Ex blind plugs missing | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-21 | 2022-12-02 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 14794 | 810.10 | 810-10-36 | Clarifier Package | 810-JA-512, 810-JA-513, 810-JA-514, 810-JA-515 | Junction box missing grounding | A | EL | HEC EL Construction | Owner Maintenance team | 2022-11-21 | 2022-12-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14795 | 810.10 | 810-10-36 | Clarifier Package | 810-FT-9221 | Cable glland missing Atex | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-21 | 2022-12-02 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 14796 | 810.10 | 810-10-36 | Clarifier Package | 810-XV-9261, 810-XV-9262 | Additional support for the tubing needed | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-21 | 2022-12-07 | Walkdown |  |  | 2022-12-02 |  | V |  |  |  | RFC/RFSU
. | 14797 | 810.10 | 810-10-36 | Clarifier Package | 810-XV-9311, 810-XV-9321 | Cable tray grommet missing | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-21 | 2022-12-02 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 14798 | 810.10 | 810-10-36 | Clarifier Package | 810-XV-9311 | Solenoid cable to be arranged properly | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-21 | 2022-12-02 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 14799 | 810.10 | 810-10-36 | Clarifier Package | 810-AR-512 | Analyzers system not finished yet (pH sensor not installed, lack of cable, grounding missing, discrepancy between site and V-HRI-R14-810-00000-00103). Necessary additional Walk Down for this analyzer system. | C | CI | HEC CI Construction | Owner Maintenance team | 2022-11-21 | 2023-03-29 | Walkdown |  | Changed from Category A |  |  | V |  |  | 2023-03-08 | RFC/RFSU
. | 14800 | 810.10 | 810-10-36 | Clarifier Package | 810-AC-511 | Nameplate shall be updated according to V-HRI-R41-810-00000-00102-Z2 | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-21 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14801 | 810.10 | 810-10-36 | Clarifier Package | 810-AC-511 | Warning nameplate shall be updated according to V-HRI-R41-810-00000-00102-Z2 | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-21 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14802 | 810.10 | 810-10-36 | Clarifier Package | 810-AC-511 | Water from purge controller enclosure shall be removed and explained and removed reason for water getting there | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-21 | 2022-12-13 | Walkdown |  |  | 2022-12-12 |  | V |  |  |  | RFC/RFSU
. | 14803 | 810.10 | 810-10-36 | Clarifier Package | 810-AC-511 | Add tag names for analyzer and sensors | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-21 | 2022-12-02 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 14804 | 810.10 | 810-10-36 | Clarifier Package | EGAT-HEC-810-PRO-PID-00021A-D | Earthing to be tightned at motor side for (Tag no:- 810-X0002-MP03A,B&C) | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-21 | 2022-12-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14805 | 810.10 | 810-10-36 | Clarifier Package | EGAT-HEC-810-PRO-PID-00021A-D | LCS Blind plug to be provided for (Tag no:-810-X0002-MX04A&B) | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-21 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14806 | 810.10 | 810-10-36 | Clarifier Package | EGAT-HEC-810-PRO-PID-00021A-D | Power Cable termination is not completed for (Tag no:- 810-AR-512) | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-21 | 2023-01-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14807 | 810.10 | 810-10-36 | Clarifier Package | EGAT-HEC-810-PRO-PID-00021A-D | Motor cleaning to be done | B | ME | HEC ME Construction | Mr. Arkadiusz Tryniszewski | 2022-11-21 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14808 | 810.10 | 810-10-40 |  | 850-P0013 A & B | Final Inspection | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-24 | 2022-12-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14809 | 810.10 | 810-10-40 |  | 810-P0010 | Final Inspection | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-24 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14810 | 810.10 | 810-10-40 |  | B1UG-WW-SD-0001 | PRESSURE TEST | A | PI | HEC PI Construction | Mr. Jaroslaw Pykosz | 2022-11-24 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14811 | 810.10 | 810-10-40 |  | B1UG-WW-SD-0001-H | PRESSURE TEST | A | PI | HEC PI Construction | Mr. Jaroslaw Pykosz | 2022-11-24 | 2022-12-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14812 | 810.10 | 810-10-40 |  | B1UG-WW-SD-0001 | Re-instatement (after Hydro) B1UG-WW-SD-0001 | A | PI | HEC PI Construction | J.W.JEONG | 2022-11-24 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14813 | 810.10 | 810-10-40 |  | B1UG-WW-SD-0001-H | Re-instatement (after Hydro) B1UG-WW-SD-0001-H | A | PI | HEC PI Construction | J.W.JEONG | 2022-11-24 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14814 | 810.10 | 810-10-40 |  | 850WT-WW-1003 | Final Appeareance Inspection | C | IN | HEC IN Construction | J.W.JEONG | 2022-11-24 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14815 | 810.10 | 810-10-40 |  | B1UG-WW-SD-0001-F | Final Appeareance Inspection | C | IN | HEC IN Construction | J.W.JEONG | 2022-11-24 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14816 | 810.10 | 810-10-40 |  | B1UG-WW-SD-0001-C | Final Appeareance Inspection | C | IN | HEC IN Construction | J.W.JEONG | 2022-11-24 | 2022-12-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14817 | 810.10 | 810-10-40 |  | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2023-01-18 | Walkdown |  |  | 2023-01-18 |  | V |  |  |  | RFC/RFSU
. | 14827 | 810.10 | 810-10-40 | Wastewater Collection Basin System | EGAT-HEC-970-PRO-PID-00051 | Blind plug to be provide for the LCS spare holes for 810-MP0009A/B, 810-MP0010 and 850-MP0013A/B | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-24 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14828 | 810.10 | 810-10-40 | Wastewater Collection Basin System | EGAT-HEC-970-PRO-PID-00051 | Provide yellow tag sticker for LCS EMERGENCY PUSH BOTTON at cover side written with Polish Language [ WYŁĄCZNIK AWARYJNY ] for (Tagno:- ) LCS & E-Stop | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-24 | 2023-05-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14829 | 810.10 | 810-10-40 | Waste water Collection Basin | EGAT-HEC-970-PRO-PID-00051 | 850-MP0013A/B Loose earth on LCS to be tightned | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-24 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14830 | 810.10 | 810-10-40 | Waste water Collection Basin | EGAT-HEC-970-PRO-PID-00051 | 850-MP0013A/B LCS support & Cable tray touch-up paint to be apply. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-24 | 2023-01-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14831 | 810.10 | 810-10-40 | Waste water Collection Basin | EGAT-HEC-970-PRO-PID-00051 | 810-MP0009A/B, 810-MP0010 in cable tray cable dressing to be done properly, Sharp Edges to be protected | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-24 | 2023-01-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14832 | 810.10 | 810-10-40 | Wastewater Collection Basin System | EGAT-HEC-970-PRO-PID-00051 | Perforated tray covering and cable stub-up conduit pipe duct sealing to be done. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-11-24 | 2023-01-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14833 | 810.10 | 810-10-40 | Wastewater Collection Basin System | 810-LT-0511 | Sunshade bolts to be tightened - punch still valid (since last Walk Down) | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-24 | 2022-12-05 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 14834 | 810.10 | 810-10-40 | Wastewater Collection Basin System | 810-TE-5103 | Cable should go under cable tray, not above | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-24 | 2022-12-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14835 | 810.10 | 810-10-40 | Wastewater Collection Basin System | 810-TE-5103 | Proper Atex markig shall be selected on device | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-24 | 2023-02-09 | Walkdown |  |  | 2023-01-27 |  | V |  |  |  | RFC/RFSU
. | 14836 | 810.10 | 810-10-40 | Wastewater Collection Basin System | 810-TE-5103 | Cable tray grommets to be fixed and added | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-24 | 2022-12-02 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 14838 | 810.10 | 810-10-40 | Wastewater Collection Basin System | 850-LT-0511 | Cable tag missing | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-24 | 2022-12-02 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 14839 | 810.10 | 810-10-40 | Wastewater Collection Basin System | 850-FT-0511 | Grounding to be repaired | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-24 | 2022-12-02 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 14840 | 810.10 | 810-10-40 | AUX Area | 900-AC-001, 900-AC-003 | Nameplate shall be updated according to V-SEC-I14-000-00000-00026-Z0 - punch still valid (since last Walk Down) | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-24 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14841 | 810.10 | 810-10-40 | AUX Area | 900-AC-001, 900-AC-003 | Warning nameplate is only in English. Polish warning nameplate shall be added. - punch still valid (since last Walk Down) | C | CI | HEC CI Construction | Owner Maintenance team | 2022-11-24 |  | Walkdown | [8 empty] | RFC/RFSU
. | 14842 | 810.10 | 810-10-40 | AUX Area | 900-AC-001, 900-AC-003 | Horn an beacon TAG NOs missing - punch still valid (since last Walk Down) | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-24 | 2022-12-02 | Walkdown |  |  | 2022-12-01 |  | V |  |  |  | RFC/RFSU
. | 14843 | 810.10 | 810-10-40 | AUX Area | 900-AC-001 | Analyzer chamber missing | C | CI | HEC CI Construction | Owner Maintenance team | 2022-11-24 |  | Walkdown |  | Changed from Category A | [5 empty] | 2023-03-07 | RFC/RFSU
. | 14844 | 810.10 | 810-10-40 | AUX Area | 900-AT-5101, 900-AT-5102, 900-AT-5103, 900-AT-5107, 900-AT-5108, 900-AT-5109 | Necessary additional Walk Down for test&calibration these analyzers. - punch still valid (since last Walk Down) | A | CI | HEC CI Construction | Owner Maintenance team | 2022-11-24 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14845 | 810.10 | 810-10-40 | 810-BA0009 | 810-BA0009 | Ladder cut bolt to be protected | B | CV | HEC CV Construction | Mr. Krzysztof Kaliszyk | 2022-11-24 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14846 | 810.10 | 810-10-40 | 850-BA0013 | 850-P0013A/B | Rusted bolt and nuts to be clean and protected with molykote | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2022-11-24 | 2023-03-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14847 | 810.10 | 810-10-40 | 850-BA0013 | 850-P0013A/B | Ladder cutted bolt to be protected | B | CV | HEC CV Construction | Mr. Krzysztof Kaliszyk | 2022-11-24 | 2022-11-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14848 | 810.10 | 810-10-40 | 850-BA0013 | 850-P0013A/B | Additional pipe support at line 850-4"-WW-05107-LGP41-N | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-11-24 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14849 | 810.10 | 810-10-40 | 850-BA0013 | 850-P0013A/B | Temporary protection on suction side (line 850-4"-WW-05107-LGP41-N) to be removed | B | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2022-11-24 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14851 | 810.10 | 810-10-40 |  | EGAT-HEC-970-PRO-PID-00051 | Pumps 850-P0013A/B to be tightened to the chain | A | ME | HEC ME Construction | Mr. Jaroslaw Pykosz | 2022-11-24 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14852 | 810.10 | 810-10-40 |  | EGAT-HEC-970-PRO-PID-00051 | drain valve downstream of SAMPLING POINT NO. 5103 to be specified in P&ID | B | EM | HEC PI Design | Mr. Jaroslaw Pykosz | 2022-11-24 | 2022-12-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14853 | 810.10 | 810-10-40 |  | EGAT-HEC-970-PRO-PID-00051 | rusted bolts | B | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-24 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14854 | 810.10 | 810-10-40 |  | 850-BA0013 | rusted supports | B | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-11-24 | 2022-12-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14855 | 810.10 | 810-10-40 |  | 850-BA0009 | bolts to be tightened on support | A | PI | HEC PI Construction | Mr. Jaroslaw Pykosz | 2022-11-24 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14856 | 810.10 | 810-10-40 |  | 850-BA0009/BA0013 | Piping sealing to be done | C | CV | HEC IN Construction | Ms. Paulina Bajer | 2022-11-24 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14857 | 810.10 | 810-10-40 |  | EGAT-HEC-970-PRO-PID-00051 | Hot insulation to be provided for flowmeters | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-24 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14858 | 810.10 | 810-10-40 |  | EGAT-HEC-970-PRO-PID-00051 | Insulation to be completed | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-11-24 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14859 | 810.10 | 810-10-40 |  | EGAT-HEC-970-PRO-PID-00051 | AT-5107/5108/5109 and AT-5101/5102/5103: two spare flange connections to be marked in P&ID | B | EM | HEC PI Design | Ms. Paulina Bajer | 2022-11-24 | 2022-12-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14864 | 810.10 | 810-10-40 | 850-BA0013 | 850-BA0013 | HANDWHEEL AROUND PIT TO BE PAINTED | B | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-11-24 | 2022-12-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14865 | 810.10 | 810-10-40 | 810-BA0009 | 810-BA0009 | HANDWHEEL AROUND PIT TO BE PAINTED | B | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-11-24 | 2022-12-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14866 | 810.10 | 810-10-40 |  | 810-BA0009 AND 850-BA0013 | NO SAFETY ACCESS TO 810-BA0009 AND TO 850-BA0013 | A | CV | HEC CV Construction | Mr. Jakub Partyka | 2022-11-24 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14869 | 810.10 | 810-10-40 | 810-P0009A | 810-6"-WW-05101-B1A1-ET | PIPES PENETRATION THROUGH CEILING NOT CENTERED AND COLLIDE WITH INSULATION. TO BE RECTIFY | A | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-11-24 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14870 | 810.10 | 810-10-40 | 810-P0009B | 810-6"-WW-05101-B1A1-ET | PIPES PENETRATION THROUGH CEILING NOT CENTERED AND COLLIDE WITH INSULATION. TO BE RECTIFY | A | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-11-24 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14871 | 810.10 | 810-10-40 | 810-P0010 | 810-6"-WW-05101-B1A1-ET | PIPES PENETRATION THROUGH CEILING NOT CENTERED AND COLLIDE WITH INSULATION. TO BE RECTIFY | A | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-11-24 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14872 | 810.10 | 810-10-40 | 850-P0013A | 850-2"-WW-05101-LGP41-ET | PIPES PENETRATION THROUGH CEILING NOT CENTERED AND COLLIDE WITH INSULATION. TO BE RECTIFY | A | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-11-24 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14873 | 810.10 | 810-10-40 | 850-P0013B | 850-2"-WW-05101-LGP41-ET | PIPES PENETRATION THROUGH CEILING NOT CENTERED AND COLLIDE WITH INSULATION. TO BE RECTIFY | A | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-11-24 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14874 | 810.10 | 810-10-40 | 850-P0013A | 850-2"-WW-05101-LGP41-ET | LINE SHAKING - ADDITIONAL SUPPORT TO BE CONSIDERED | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-11-24 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14875 | 810.10 | 810-10-40 | 850-P0013B | 850-2"-WW-05101-LGP41-ET | LINE SHAKING - ADDITIONAL SUPPORT TO BE CONSIDERED | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-11-24 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14876 | 810.10 | 810-10-40 | 850-P0013B | 850-4"-WW-05107-LGP41-N | CHEMICAL CLEANING AND PASSIVATION | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-11-24 | 2022-11-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14877 | 810.10 | 810-10-40 | 850-P0013B | 850-4"-WW-05107-LGP41-N | RUSTED BOLTS FOR CAMLOCK TO BE RECTIFY | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-11-24 | 2022-11-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14878 | 810.10 | 810-10-40 | AROUND PG 5105 | 900-6"-WW-00114-B1A1-ET | ET BOX TO BE INSTALLED PROPERLY - INSULATION TO BE CLOSED(SILICONE TO BE APPLIED) | A | EL | HEC PI Construction | Mr. Jakub Partyka | 2022-11-24 | 2023-01-09 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14879 | 810.10 | 810-10-40 | NEAR FT 5102 | 900-2"-WW-00105-B1A1-ET | AFTER FINAL INSULATION VALVE CANNOT BE OPERATED - TO BE RECTIFY | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-11-24 | 2022-11-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14880 | 810.10 | 810-10-40 | Wastewater Collection Basin System | EGAT-HEC-970-PRO-PID-00051 | Hose conector chain to be provided | C | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2022-11-24 | 2023-02-13 | Walkdown |  |  |  | (PI/CV) 배관 아니면 토목 설치 아이템 같습니다.아이템은 아래 P&ID상 아이템입니다. FE Comment | V |  |  |  | RFC/RFSU
. | 14881 | 810.10 | 810-10-40 | 850-BA0013 |  | Rust on fixing elements and steel structure | C | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2022-11-24 | 2023-03-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14882 | 810.10 | 810-10-40 |  | n/a | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-11-24 | 2023-02-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14883 | 810.10 | 810-10-40 |  | n/a | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-11-24 |  | Walkdown | [8 empty] | RFC/RFSU
. | 14885 | 810.10 | 810-10-40 |  | EGAT-HEC-970-PRO-PID-00051 | Stairs to the platform above interconnection lines to GAP (PDH-GAP border) not completed, loose railings | B | SS | HEC SS Construction | Ms. Paulina Bajer | 2022-11-24 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14900 | 810.10 | 810-10-20 | General | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2022-12-02 | Walkdown |  |  | 2022-12-02 |  | V |  |  |  | RFC/RFSU
. | 14901 | 810.10 | 810-10-26 | General | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2022-12-02 | Walkdown |  |  | 2022-12-02 |  | V |  |  |  | RFC/RFSU
. | 14902 | 810.10 | 810-10-30 | General | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14903 | 810.10 | 810-10-32 | General | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2022-12-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14904 | 810.10 | 810-10-34 | General | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2022-11-30 | Walkdown |  | 2022-11-28 | 2022-11-28 |  | V |  |  |  | RFC/RFSU
. | 14905 | 810.10 | 810-10-38 | General | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2022-12-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 14906 | 810.10 | 810-10-42 | General | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | C | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2023-02-16 | Walkdown |  |  | 2023-02-15 |  | V |  |  |  | RFC/RFSU
. | 14907 | 810.12 | 810-12-14 | General | RFI for CI discipline | All RFI of this subsystem for CI discipline to be closed | A | CI | HEC CI Construction | J.W.JEONG | 2022-11-24 | 2022-12-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16678 | 810.10 | 810-10-19 | Plant Water Distribution System | 200PR1-SW-0001 | Reinstatement | A | PI | HEC PI Construction | J.W.JEONG | 2022-12-08 | 2023-01-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16679 | 810.10 | 810-10-19 | Plant Water Distribution System | 810PR-SW-1001 | Reinstatement | A | PI | HEC PI Construction | J.W.JEONG | 2022-12-08 | 2022-12-29 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16680 | 810.10 | 810-10-19 | Plant Water Distribution System | 900-PRO-PID-05052(1) | Plant water line to 700-P0001A/B not connected | A | PI | HEC PI Construction | Ms. Alicja Sulżyc | 2022-12-08 | 2023-01-03 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16681 | 810.10 | 810-10-19 | Plant Water Distribution System | 900-PRO-PID-05052(1) | Ladder not fixed (access ladder to drain valve on line 900-2"-SW-00101-B1A1-ET | B | CV | HEC CV Construction | Ms. Alicja Sulżyc | 2022-12-08 | 2023-01-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16682 | 810.10 | 810-10-19 | Plant Water Distribution System | utility stations | On some utlitility stations collision of the valve with insulation | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16683 | 810.10 | 810-10-19 | Plant Water Distribution System | 900-PRO-PID-05052(1) | SW to 850-P0002A: pipelines shaking | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-08 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16684 | 810.10 | 810-10-19 | Plant Water Distribution System | 900-PRO-PID-05052(1) | Electrical tracing to be teminated | B | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16685 | 810.10 | 810-10-19 | Plant Water Distribution System | utility stations | Coupling missing | B | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16686 | 810.10 | 810-10-19 | Plant Water Distribution System | 900-PRO-PID-05052(1) | Sealing on insulation to be corrected (area 850) | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16687 | 810.10 | 810-10-19 | Plant Water Distribution System | 900-PRO-PID-05052(1) | Touch -up painting for supports to be provided | B | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-08 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16688 | 810.10 | 810-10-19 | Plant Water Distribution System |  | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-05-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16689 | 810.10 | 810-10-19 | Plant Water Distribution System |  | Missing nameplates for piping (Method Statement for Piping Nameplate Attachment) | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-08 |  | Walkdown | [8 empty] | RFC/RFSU
. | 16690 | 810.10 | 810-10-19 | Plant Water Distribution System | 900-PRO-PID-05052(1) | Touch-up paiting fo handwheels | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-08 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16691 | 810.10 | 810-10-19 | Plant Water Distribution System | 900-PRO-PID-05052(1) | Utilitiy stations: piping support to be provided | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-08 | 2023-02-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 16692 | 810.10 | 810-10-20 | Plant Water Distribution System | 900-PRO-PID-05052(1) | Rusted end flange (900-3''-SW-00101-B1A1-ET; 900-2''-SW-00101-B1A1-ET) | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-08 | 2022-12-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 21127 | 810.12 | 810-12-10 | unit 600/610 | EGAT-HEC-810-HSE-PID-00021 | Electrical tracing to be provided | A | EL | HEC EL Construction | Ms. Paulina Bajer | 2022-12-30 | 2023-01-18 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21128 | 810.12 | 810-12-10 | unit 600/610 | EGAT-HEC-810-HSE-PID-00021 | Insulation to be provided | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2022-12-30 | 2023-03-31 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21129 | 810.12 | 810-12-10 | unit 600/610 | EGAT-HEC-810-HSE-PID-00021 | Plug on drain valve missing (line no 600-10''-FW-00001-MS-1-ET) | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-30 | 2023-01-04 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21130 | 810.12 | 810-12-10 | unit 600/610 | EGAT-HEC-810-HSE-PID-00021 | Fire water distribution for loading arms to be verified in P&ID | B | EM | HEC SE Design | Ms. Paulina Bajer | 2022-12-30 | 2023-01-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21131 | 810.12 | 810-12-10 | unit 600/610 | EGAT-HEC-810-HSE-PID-00021 | Piping upstream of TSTR-005 to be connected | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-30 | 2023-02-14 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21132 | 810.12 | 810-12-10 | unit 600/610 | EGAT-HEC-810-HSE-PID-00021 | Housekeeping to be done in Deluge Valve shelter | C | AR | HEC AR Construction | Ms. Paulina Bajer | 2022-12-30 | 2023-01-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21133 | 810.12 | 810-12-10 | unit 600/610 | EGAT-HEC-810-HSE-PID-00021 | Temporary support to be replaced with permanent one | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-30 | 2023-01-20 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21134 | 810.12 | 810-12-10 | unit 600/610 | EGAT-HEC-810-HSE-PID-00021 | missing spray nozzle at loading arms area to be installed | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2022-12-30 | 2023-01-20 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21135 | 810.12 | 810-12-10 | unit 600/610 | EGAT-HEC-810-HSE-PID-00021 | Piping to be sealed while passing though the wall | C | AR | HEC AR Construction | Ms. Paulina Bajer | 2022-12-30 | 2023-01-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21136 | 810.12 | 810-12-10 | unit 600/610 | common | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-30 | 2023-04-20 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21137 | 810.12 | 810-12-12 | unit 600/610 | EGAT-HEC-810-HSE-PID-00201 | Housekeeping to be done in Deluge Valve shelter | C | AR | HEC AR Construction | Ms. Paulina Bajer | 2022-12-30 | 2023-01-24 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21138 | 810.12 | 810-12-12 | unit 600/610 | EGAT-HEC-810-HSE-PID-00203 | P&ID to be updated - 2 spray nozzles for each pump 600-P0002A, 600-P0002B, 600-P0003A, 600-P0003B to be specified | B | EM | HEC SE Design | Ms. Paulina Bajer | 2022-12-30 | 2023-01-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21139 | 810.12 | 810-12-12 | unit 600/610 | EGAT-HEC-810-HSE-PID-00203 | Drain valve missing in P&ID in line no. 600-1''-FW-00251-MS-2-N | B | EM | HEC SE Design | Ms. Paulina Bajer | 2022-12-30 | 2023-01-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21140 | 810.12 | 810-12-12 | unit 600/610 | EGAT-HEC-810-HSE-PID-00203 | Drain valve missing in P&ID in line no. 600-2''-FW-00260-MS-2-N | B | EM | HEC SE Design | Ms. Paulina Bajer | 2022-12-30 | 2023-01-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21141 | 810.12 | 810-12-12 | unit 600/610 | EGAT-HEC-810-HSE-PID-00203 | Drain valve missing in P&ID in line no. 600-2''-FW-00270-MS-2-N | B | EM | HEC SE Design | Ms. Paulina Bajer | 2022-12-30 | 2023-01-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21142 | 810.12 | 810-12-12 | unit 600/610 | EGAT-HEC-810-HSE-PID-00203 | Drain valve missing in P&ID in line no. 600-2''-FW-00280-MS-2-N | B | EM | HEC SE Design | Ms. Paulina Bajer | 2022-12-30 | 2023-01-16 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21143 | 810.12 | 810-12-12 | unit 600/610 | EGAT-HEC-810-HSE-PID-00201 | Piping to be sealed while passing though the wall | C | AR | HEC AR Construction | Ms. Paulina Bajer | 2022-12-30 | 2023-01-20 | [5 empty] | V |  |  |  | RFC/RFSU
. | 21144 | 810.12 | 810-12-12 | unit 600/610 | common | METHOD STATEMENT FOR PIPING SERVICE IDENTIFICATION AND FLOW DIRECTION shall be applied for all pipelines in the sub-systems. | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2022-12-30 | 2023-04-20 | [5 empty] | V |  |  |  | RFC/RFSU
. | 23180 | 810.10 | 810-10-30 | 810WT | 810WT-810CH93118-01 | Pipeline size on isometric does not correspond to P&ID and actual installed on site. Isometric drawing to be updated | B | EM | HEC PI Design | Mr. Jakub Partyka | 2022-09-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23181 | 810.10 | 810-10-30 | 810WT | 810WT-810CH08101-01 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23182 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97002-01 | Pipe and weld joints to be cleaned and passivated | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23183 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97002-02 | The cladding on supports not properly sealed by mastic. Water goes into the rockwool insulation. To be exchanged for dry one. | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23184 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97002-02 | Piping Insulation to be completed | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23185 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97002-02 | Pipe wall pass through not finished (not sealed) | B | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23186 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97002-03 | Pipeline bended (misalignment) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23187 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97002-03 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23188 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97002-03 | Mastic missing on elbows and supports | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23189 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97004-02 | The cladding on supports not properly sealed by mastic. Water goes into the rockwool insulation. To be exchange for dry one. | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23190 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97004-02 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23191 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97004-02 | Pipe wall pass through not finished (not sealed) | B | AR | HEC AR Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23192 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97004-03 | Paint touch up for support to be done (support rusted) | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23193 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97004-03 | Cladding overlap located to high which allows water to get inside. Insulation to be reoriented | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23194 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97004-03 | Mastic missing on supports | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23195 | 810.10 | 810-10-30 | 810WT | 810WT-810CH97004-03 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23196 | 810.10 | 810-10-30 | 810WT | 810WT-810CH92002-03 | Piping Insulation missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23197 | 810.10 | 810-10-30 | 810WT | 810WT-810CH92004-02 | Guides installed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23198 | 810.10 | 810-10-30 | 810WT | 810WT-810CH92004-02 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23199 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07103-01 | Support off center and Guides missing | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23200 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07103-01 | Flange face of valve rusted to be cleaned and covered | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23201 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07103-01 | Instrument missing (810-PG-1003B) | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-17 | Walkdown |  |  | 2023-01-16 |  | V |  |  |  | RFC/RFSU
. | 23202 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07103-01 | Tape to be removed from valve stem | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23203 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07103-01 | Touch contact with valve wheel of the other line | A | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-13 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23204 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07103-01 | Rusted screws on valve visor. To be changed to SS | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23205 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07103-01 | Valve visor damaged. To be replaced | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23206 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07103-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23207 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-01 | Support off center and Guides missing | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23208 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-01 | Flange face of valve rusted to be cleaned and covered | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23209 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-01 | Instrument missing (810-PG-1003A) | A | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-17 | Walkdown |  |  | 2023-01-16 |  | V |  |  |  | RFC/RFSU
. | 23210 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-01 | Tape to be removed from valve stem | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23211 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-01 | Touch contact with valve wheel of the other line | A | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-13 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23212 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-01 | Rusted screws on valve visor. To be changed to SS | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23213 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-01 | Mastic missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23214 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-01 | Insulation not protected from rain water. Wet insulation to be exchanged for dry one. | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23215 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23216 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07106-01 | Pipe to be reduced. Not enough space for sample collection | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23217 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07106-01 | Cladding overlap oriented up. Not acceptable | B | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23218 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07106-01 | Mastic missing on elbow and valve | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23219 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07106-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23220 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-02 | Guide missing on one side | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23221 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-02 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23222 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-02 | Painted / dirty valve visors to be cleaned out | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23223 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-02 | Rusted screws on valve visor. To be changed to SS | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23224 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-02 | Tape to be removed from valve stem | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23225 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-02 | Paint touch up for support to be done | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23226 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-02 | Paint touch up for valves hand wheel to done | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23227 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-02 | Insulation not protected from rain water. Wet insulation to be exchanged for dry one. | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23228 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-02 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23229 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07104-01 | Valve cannot operate | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23230 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07104-01 | Guides missing | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23231 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07104-01 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23232 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07104-01 | Dirty valve visors to be cleaned out | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23233 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07104-01 | Rusted screws on valve visor. To be changed to SS | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23234 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07104-01 | Paint touch up for support to be done | C | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23235 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07104-01 | Paint touch up for valves hand wheel to done | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23236 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07104-01 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23237 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-03 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23238 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-03 | Dirty valve visors to be cleaned out | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23239 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-03 | Rusted screws on valve visor. To be changed to SS | C | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23240 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-03 | Tape to be removed from valve stem | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-07 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23241 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-03 | Paint touch up for valves hand wheel to done | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23242 | 810.10 | 810-10-34 | 810WT | 810WT-810WW07102-03 | Piping Insulation to be completed | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23243 | 810.10 | 810-10-34 | 810WT | 810WT-810TRBA0003L1-01, 810WT-810TRBA0003L2-01 | Support to be tightened (BG1-AA2) | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23244 | 810.10 | 810-10-34 | 810WT | 810WT-810TRBA0003L1-01, 810WT-810TRBA0003L2-01 | SS flange contaminated by rust from CS nuts | B | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23245 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-01 | Valve handwheel missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23246 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-01 | Rusted bolts (810-TSTR-006) | B | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23247 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-01 | Paint touch up to be done (810-TSTR-006) | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23248 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-01 | Pipeline different shades of color applied. To be unified with rest of pipelines | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23249 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-01 | Piping Insulation missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23250 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-02 | Rusted anchor bolts | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23251 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-02 | Valve symbols void. Drawing to be revised | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-13 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23252 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-02 | Pipeline different shades of color applied. To be unified with rest of pipelines | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23253 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-02 | Piping Insulation missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23254 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-03 | Rusted anchor bolts | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23255 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-03 | Tag plate to be removed | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23256 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-03 | Valve symbols void. Drawing to be revised | B | EM | HEC PI Design | Mr. Maciej Smalira | 2022-09-13 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23257 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-03 | Pipeline different shades of color applied. To be unified with rest of pipelines | C | PA | HEC PA Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23258 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-03 | Plug to be painted | C | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-03-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23259 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00003-03 | Piping Insulation missing | C | IN | HEC IN Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-02-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23260 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00004-01 | Fire fighting connection missing | A | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23261 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00300-01 | Valve handwheel missing | A | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23262 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00200-03 | Touch up paint for support to be done | C | PA | HEC PA Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-02-13 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23263 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00200-04 | Support of sampling line not indicated (PUB-DA8) | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23264 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00200-05 | Pipeline not resting | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23265 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00200-05 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23266 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00200-05 | Pipeline touch contact with handrail. Handrail not fixed | A | ME | HEC ME Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23267 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00300-03 | Pipeline touch contact with other line (instrument air line) | C | CI | HEC CI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-05-17 | Walkdown |  | Changed from Category A |  |  | V |  |  | 2023-02-21 | RFC/RFSU
. | 23268 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00300-04 | C-profile overloaded (existing support bended). Guide in slope position | A | EM | HEC MR Design | Mr. Maciej Smalira | 2022-09-13 | 2023-01-23 | Walkdown |  |  |  | 배관팀 조치 필요. | V |  |  |  | RFC/RFSU
. | 23269 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00300-04 | Pipeline not resting | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23270 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00300-04 | Support not existing (PUB-DA8) | B | PI | HEC PI Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23271 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00300-05 | Pipeline touch contact with handrail | A | ME | HEC ME Construction | Mr. Maciej Smalira | 2022-09-13 | 2023-01-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23272 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00400-04 | C-profile overloaded (existing support bended) | A | EM | HEC MR Design | Mr. Maciej Smalira | 2022-09-13 | 2023-01-23 | Walkdown |  |  |  | 배관팀 조치 필요 | V |  |  |  | RFC/RFSU
. | 23273 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00400-05 | Pipeline not resting | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23274 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00500-04 | C-profile overloaded (existing support bended) | A | EM | HEC MR Design | Mr. Maciej Smalira | 2022-09-13 | 2023-01-23 | Walkdown |  |  |  | 배관팀 조치 필요 | V |  |  |  | RFC/RFSU
. | 23275 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00500-05 | Rusted bolts and nuts to be cleaned | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23276 | 810.12 | 810-12-14 | 860CT | 860CT-860FW00600-05 | Pipeline not resting | B | PI | HEC PI Construction | Mr. Jakub Partyka | 2022-09-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23867 | 810.10 | 810-10-18 | 810-P0006A/B |  | Missing lubrication point cap. | C | ME | HEC ME Construction | Mr. Adrian Antonowicz | 2023-01-04 | 2023-04-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 23868 | 810.10 | 810-10-18 | 810-P0006A/B |  | Rust around vibration sensor mounting surface. Required corrective action and inspection of mounting surface because of very stricltly Vendor requirements to mounting surface. Sensors tag no. 810-VT-8061A/B 810-VT-8062A/B | C | ME | HEC ME Construction | Mr. Adrian Antonowicz | 2023-01-04 |  | Walkdown | [8 empty] | RFC/RFSU
. | 23869 | 810.10 | 810-10-18 | 810-P0006A/B |  | Painted unreadable tag no. for vibration sensor. | C | CI | HEC CI Construction | Mr. Adrian Antonowicz | 2023-01-04 | 2023-02-08 | Walkdown |  |  | 2023-01-21 |  | V |  |  |  | RFC/RFSU
. | 23876 | 810.10 | 810-10-26 | 810-P0007 |  | Rust around vibration sensor mounting surface. Required corrective action and inspection of mounting surface because of very stricltly Vendor requirements to mounting surface. | C | ME | HEC ME Construction | Mr. Adrian Antonowicz | 2023-01-04 |  | Walkdown | [8 empty] | RFC/RFSU
. | 24399 | 810.10 | 810-10-14 |  |  | 300UG-FW-SD-0001: PRESSURE TEST | C | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-05-08 | Walkdown |  | Changed from Category A |  |  | V |  |  | 2023-03-07 | RFC/RFSU
. | 24400 | 810.10 | 810-10-14 |  |  | 300UG-FW-SD-0016_R: PRESSURE TEST | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24401 | 810.10 | 810-10-14 |  |  | 450UG-FW-SD-0002: PRESSURE TEST | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24402 | 810.10 | 810-10-14 |  |  | 450UG-FW-SD-0005: PRESSURE TEST | C | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24403 | 810.10 | 810-10-14 |  |  | B1UG-FW-SD-0004: PRESSURE TEST | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-02-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24404 | 810.10 | 810-10-14 |  |  | B1UG-FW-SD-0009: PRESSURE TEST | C | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-03-16 | Walkdown |  | Changed from Category A |  |  | V |  |  | 2023-03-07 | RFC/RFSU
. | 24405 | 810.10 | 810-10-14 |  |  | B1UG-FW-SD-0015: PRESSURE TEST | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24406 | 810.10 | 810-10-14 |  |  | 200UG-FW-SD-0036: RE-INSTATEMENT | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24407 | 810.10 | 810-10-14 |  |  | 300UG-FW-SD-0001: RE-INSTATEMENT | C | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-05-11 | Walkdown |  | Changed from Category A |  |  | V |  |  | 2023-03-09 | RFC/RFSU
. | 24408 | 810.10 | 810-10-14 |  |  | 300UG-FW-SD-0001-B: RE-INSTATEMENT | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24409 | 810.10 | 810-10-14 |  |  | 300UG-FW-SD-0001-E: RE-INSTATEMENT | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24410 | 810.10 | 810-10-14 |  |  | 300UG-FW-SD-0016_R: RE-INSTATEMENT | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24411 | 810.10 | 810-10-14 |  |  | 300UG-FW-SD-0026: RE-INSTATEMENT | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24412 | 810.10 | 810-10-14 |  |  | 450UG-FW-SD-0002: RE-INSTATEMENT | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24413 | 810.10 | 810-10-14 |  |  | 450UG-FW-SD-0005: RE-INSTATEMENT | C | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24414 | 810.10 | 810-10-14 |  |  | 450UG-FW-SD-0011: RE-INSTATEMENT | C | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24415 | 810.10 | 810-10-14 |  |  | 450UG-FW-SD-0012: RE-INSTATEMENT | C | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24416 | 810.10 | 810-10-14 |  |  | B1UG-FW-SD-0004: RE-INSTATEMENT | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-02-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24417 | 810.10 | 810-10-14 |  |  | B1UG-FW-SD-0009 RE-INSTATEMENT | C | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-03-16 | Walkdown |  | Changed from Category A |  |  | V |  |  | 2023-03-09 | RFC/RFSU
. | 24418 | 810.10 | 810-10-14 |  |  | B1UG-FW-SD-0010-D RE-INSTATEMENT | C | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-05-11 | Walkdown |  | Changed from Category A |  |  | V |  |  | 2023-03-09 | RFC/RFSU
. | 24419 | 810.10 | 810-10-14 |  |  | B1UG-FW-SD-0015 RE-INSTATEMENT | C | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-03-16 | Walkdown |  | Changed from Category A |  |  | V |  |  | 2023-03-09 | RFC/RFSU
. | 24420 | 810.10 | 810-10-14 |  |  | B1UG-FW-SD-0021 RE-INSTATEMENT | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24421 | 810.10 | 810-10-14 |  |  | B1UG-FW-SD-0009-B RE-INSTATEMENT | C | PI | HEC PI Construction | J.W.JEONG | 2023-01-12 | 2023-03-16 | Walkdown |  | Changed from Category A |  |  | V |  |  | 2023-03-09 | RFC/RFSU
. | 24422 | 810.10 | 810-10-14 |  |  | WF-200PR1-FW-0003 WATER FLUSHING | C | COMM | HEC COMM | J.W.JEONG | 2023-01-12 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24423 | 810.10 | 810-10-14 |  |  | WF-600PS-FW-1004 WATER FLUSHING | C | COMM | HEC COMM | J.W.JEONG | 2023-01-12 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24424 | 810.10 | 810-10-14 |  |  | WF-600PS-FW-1005 WATER FLUSHING | C | COMM | HEC COMM | J.W.JEONG | 2023-01-12 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24425 | 810.10 | 810-10-14 |  |  | WF-600PS-FW-1006 WATER FLUSHING | C | COMM | HEC COMM | J.W.JEONG | 2023-01-12 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24426 | 810.10 | 810-10-14 |  |  | WF-600PS-FW-1007 WATER FLUSHING | C | COMM | HEC COMM | J.W.JEONG | 2023-01-12 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24427 | 810.10 | 810-10-14 |  |  | WF-810WT-FW-1001 WATER FLUSHING | C | COMM | HEC COMM | J.W.JEONG | 2023-01-12 | 2023-04-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24428 | 810.10 | 810-10-14 |  | general | Fire hose houses are missing | C | PI | HEC PI Construction | Mr. Piotr Słowik | 2023-01-12 | 2023-03-23 | Walkdown |  | Changed from Category A |  |  | V |  |  | 2023-02-28 | RFC/RFSU
. | 24429 | 810.10 | 810-10-14 |  | general | Fire foam drums missing | C | ME | HEC ME Construction | Mr. Piotr Słowik | 2023-01-12 |  | Walkdown |  | Changed from Category B |  | DA | V |  |  | 2023-03-10 | RFC/RFSU
. | 24430 | 810.10 | 810-10-14 |  | general | Missing hanging tags for PIVs - to be checked during re-walk down | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2023-01-12 | 2023-05-05 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24431 | 810.10 | 810-10-14 |  | general | Missing hanging tags for fire monitors to be checked during re-walk down | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2023-01-12 | 2023-03-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24432 | 810.10 | 810-10-14 |  |  | 200-PIV-003 missing | C | PI | HEC PI Construction | Mr. Piotr Słowik | 2023-01-12 | 2023-04-28 | Walkdown |  | Changed from Category A |  |  | V |  |  | 2023-03-08 | RFC/RFSU
. | 24433 | 810.10 | 810-10-14 |  | general | touch up painting to be done on PIVs and handwheels | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2023-01-12 | 2023-05-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24434 | 810.10 | 810-10-14 |  | general | civil works to be completed | C | CV | HEC CV Construction | Ms. Paulina Bajer | 2023-01-12 | 2023-04-12 | Walkdown | Gusan / Jakon |  |  |  | V |  |  |  | RFC/RFSU
. | 24435 | 810.10 | 810-10-14 |  | general | housekeeping to be done | C | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2023-01-12 | 2023-02-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24436 | 810.10 | 810-10-14 |  | general | Chains missing on fire hydrants | C | PI | HEC PI Construction | Mr. Piotr Słowik | 2023-01-12 | 2023-03-16 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24437 | 810.10 | 810-10-14 |  | 200-MOV-1005 | Valve not installed | A | PI | HEC PI Construction | Mr. Jarosław Korczak | 2023-01-12 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24438 | 810.10 | 810-10-14 |  | 000-HSE-PID-00202 | Fire hydrant next to PIV-0086 to be rotated with 90 degrees | A | PI | HEC PI Construction | Mr. Piotr Słowik | 2023-01-12 | 2023-02-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24439 | 810.10 | 810-10-14 |  | 000-HSE-PID-00202 | Fire hydrant next to PIV-0087 to be rotated with 90 degrees | A | PI | HEC PI Construction | Mr. Piotr Słowik | 2023-01-12 | 2023-02-02 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24440 | 810.10 | 810-10-14 |  | 000-HSE-PID-00202 | PIV-0085, damaged valve | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2023-01-12 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24441 | 810.10 | 810-10-14 |  | 000-HSE-PID-00202 | PIV-0112: guardpost to be installed | A | CV | HEC CV Construction | Ms. Małgorzata Juszczyk | 2023-01-12 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24442 | 810.10 | 810-10-14 |  | general | Fire hydrant to be rotated (DN110 connection to be orientated to the road) e.g. fire hydrant next to PIV-0073 | C | PI | HEC PI Construction | Mr. Bartosz Michalonek | 2023-01-12 | 2023-05-05 | Walkdown |  | Changed from Category A |  |  | V |  |  | 2023-02-28 | RFC/RFSU
. | 24443 | 810.10 | 810-10-14 |  | general | P&IDs to be revised - hydrants and PIVs to be specified on the proper side of the road as per Site conditions | B | EM | HEC SE Design | Mr. Tomasz Ulatowski | 2023-01-12 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24444 | 810.10 | 810-10-14 |  | EGAT-HEC-200-HSE-PID-00201, 202 | piping sealing to be done on walls (Fire Water | C | AR | HEC AR Construction | Mr. Piotr Słowik | 2023-01-12 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24445 | 810.10 | 810-10-14 |  | EGAT-HEC-200-HSE-PID-00201, 202, 203 | LO device missing | C | COMM | HEC COMM | Ms. Małgorzata Juszczyk | 2023-01-12 |  | Walkdown | [8 empty] | RFC/RFSU
. | 24446 | 810.10 | 810-10-14 |  | EGAT-HEC-200-HSE-PID-00201, 202, 203 | rusted visor bolts to be replaced to SS | C | PI | HEC PI Construction | Ms. Paulina Bajer | 2023-01-12 | 2023-05-11 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24447 | 810.10 | 810-10-14 |  | EGAT-HEC-200-HSE-PID-00201 | handwheels to be touch-up painted | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2023-01-12 | 2023-05-10 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24448 | 810.10 | 810-10-14 |  | EGAT-HEC-810-HSE-PID-00202 | Drain valve from TSTR-006 to be provided | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2023-01-12 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24449 | 810.10 | 810-10-14 |  | deluge valve shelters | Insulation incomplete on the valve | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2023-01-12 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24450 | 810.10 | 810-10-14 |  | deluge valve shelters | Piping sealing to be done | B | AR | HEC AR Construction | Ms. Paulina Bajer | 2023-01-12 | 2023-01-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24451 | 810.10 | 810-10-14 |  | EGAT-HEC-000-HSE-PID-00205 | missing fire hydrants next to 300-PIV-0070 to 300-PIV-0074 | C | PI | HEC PI Construction | Mr. Tomasz Ulatowski | 2023-01-12 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24452 | 810.10 | 810-10-14 |  | EGAT-HEC-000-HSE-PID-00204 | Missing fire monitor next to 300-PIV-0028 | A | PI | HEC PI Construction | Mr. Tomasz Ulatowski | 2023-01-12 | 2023-01-31 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 24453 | 810.10 | 810-10-14 |  | general | Fire hydrants elevation to be verified against doc no. HSE-TDS-00201 (unable to check). | C | PI | HEC PI Construction | Mr. Bartosz Michalonek | 2023-01-12 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25350 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00211/221 | sampling points 8118 and 8102: unable to take the sample (pipelines to be shortened) | B | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25351 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00211 | Electrical tracing on LG and LT to be provided | A | EL | HEC EL Construction | Ms. Paulina Bajer | 2023-01-13 | 2023-01-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25352 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00211 | Insulation on LG and LT to be provided | A | IN | HEC IN Construction | Ms. Paulina Bajer | 2023-01-13 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25353 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00211 | Electrical tracing on 810-V0001 to be provided | A | EL | HEC EL Construction | Ms. Paulina Bajer | 2023-01-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25354 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00211/221 | Locking device missing | C | COMM | HEC COMM | Ms. Małgorzata Juszczyk | 2023-01-13 |  | Walkdown | [8 empty] | RFC/RFSU
. | 25355 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00211 | Rusted bolts, flanges | B | PI | HEC PI Construction | Ms. Paulina Bajer | 2023-01-13 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25356 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00211 | Insulation incomplete | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2023-01-13 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25357 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00211 | Temporary hanging tags on instruments to be replaced to permanent | B | CI | HEC CI Construction | Ms. Paulina Bajer | 2023-01-13 | 2023-01-25 | Walkdown |  |  | 2023-01-21 |  | V |  |  |  | RFC/RFSU
. | 25358 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00211/221 | Piping sealing to be done (passing though the wall) | C | AR | HEC AR Construction | Ms. Paulina Bajer | 2023-01-13 | 2023-01-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25359 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00211 | wet wool on line 810-3''-W-00116-MS-2-ET to be replaced with new one | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2023-01-13 | 2023-02-28 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25360 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00211 | Plug missing on drain and vent valve | A | PI | HEC PI Construction | Ms. Paulina Bajer | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25361 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00221 | Insulation to be provided | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2023-01-13 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25362 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00221 | Grease nipple cover missing on both pumps | B | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25363 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00221 | Support to be fixed on pump discharge line | A | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25364 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | EGAT-HEC-810-PRO-PID-00211/221 | Housekeeping to be done (dust to be removed) | B | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25365 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | 810-LG-M-1007 | Hanging Tag Missing | B | CI | HEC CI Construction | Mr. Jakub Maziarz | 2023-01-13 | 2023-01-24 | Walkdown |  |  | 2023-01-21 |  | V |  |  |  | RFC/RFSU
. | 25366 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | 810-LT-1041 | Cable tag missing | B | CI | HEC CI Construction | Mr. Jakub Maziarz | 2023-01-13 | 2023-01-24 | Walkdown |  |  | 2023-01-21 |  | V |  |  |  | RFC/RFSU
. | 25367 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | 810-PV-1041A, 810-PT-1041 | Missing blind plug with Atex | A | CI | HEC CI Construction | Mr. Jakub Maziarz | 2023-01-13 | 2023-01-24 | Walkdown |  |  | 2023-01-21 |  | V |  |  |  | RFC/RFSU
. | 25368 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | 810-PT-1041, 810-LT-1041, 810-LT-1040 | Atex marking missing | A | CI | HEC CI Construction | Mr. Jakub Maziarz | 2023-01-13 | 2023-01-24 | Walkdown |  |  | 2023-01-21 |  | V |  |  |  | RFC/RFSU
. | 25369 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | 810-PT-1036 | Drain plug missing | A | CI | HEC CI Construction | Mr. Jakub Maziarz | 2023-01-13 | 2023-01-24 | Walkdown |  |  | 2023-01-21 |  | V |  |  |  | RFC/RFSU
. | 25370 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | 810-PT-1036 | Stanchion grounding to be done | A | CI | HEC CI Construction | Mr. Jakub Maziarz | 2023-01-13 | 2023-01-24 | Walkdown |  |  | 2023-01-21 |  | V |  |  |  | RFC/RFSU
. | 25371 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | 810-PT-1036 | Grounding to tightened | A | CI | HEC CI Construction | Mr. Jakub Maziarz | 2023-01-13 | 2023-01-24 | Walkdown |  |  | 2023-01-21 |  | V |  |  |  | RFC/RFSU
. | 25372 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | 810-PV-1041A | Atex Marking on positioner missing | A | CI | HEC CI Construction | Mr. Jakub Maziarz | 2023-01-13 | 2023-01-24 | Walkdown |  |  | 2023-01-21 |  | V |  |  |  | RFC/RFSU
. | 25373 | 810.10 | 810-10-28 | Potable Water Storage and Distribution System | 810-PV-1041A | Tubing ro be tightened (not air tight) | A | CI | HEC CI Construction | Mr. Jakub Maziarz | 2023-01-13 | 2023-01-24 | Walkdown |  |  | 2023-01-21 |  | V |  |  |  | RFC/RFSU
. | 25374 | 810.10 | 810-10-28 | Potable Water storage and Distribution System | EGAT-HEC-810-PRO-PID-00221 | For Tag no- 810-MP0011A/B LCS blind plug to be provided | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25375 | 810.10 | 810-10-28 | Potable Water storage and Distribution System | EGAT-HEC-810-PRO-PID-00221 | For Tag no- 810-MP0011A/B LCS earthing cable to be connected. | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25376 | 810.10 | 810-10-28 | Potable Water storage and Distribution System | EGAT-HEC-810-PRO-PID-00221 | Motor skid earthing to be tightned, Motor earthing cable to be connect to motor body. | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25377 | 810.10 | 810-10-28 | Potable Water storage and Distribution System | EGAT-HEC-810-PRO-PID-00221 | Skid and motor cleaning to be done | C | COMM | HEC COMM | Mr. Arkadiusz Tryniszewski | 2023-01-13 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25378 | 810.10 | 810-10-28 | Potable Water storage and Distribution System | EGAT-HEC-810-PRO-PID-00221 | Power cable and earthing cable to be connect on the exhaust fan on the roof. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-13 | 2023-01-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25379 | 810.10 | 810-10-28 | Potable Water storage and Distribution System | EGAT-HEC-810-PRO-PID-00221 | Heat racing cable gland on juction box to be tightned. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25380 | 810.10 | 810-10-28 | Potable Water storage and Distribution System | EGAT-HEC-810-PRO-PID-00221 | Potable water shelter cable pit to be cleaning and sealing to be applied. | C | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-13 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25381 | 810.10 | 810-10-28 | Potable Water storage and Distribution System | EGAT-HEC-810-PRO-PID-00221 | Cable tray main earthing to be provided. | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2023-01-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25382 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | 1000UG-W-SD-0001: Pressure Test | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25383 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | 1000UG-W-SD-0001: Re-instatement | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25384 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | 200RS1-W-0002: Re-instatement | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25385 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | 200UG-W-SD-0001: Re-instatement | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-13 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25386 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | 200UG-W-SD-0002: Re-instatement | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-13 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25387 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | B1UG-W-SD-0001: Re-instatement | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-13 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25388 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | B2UG-W-SD-0001: Re-instatement | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-13 | 2023-01-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25389 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | B2UG-W-SD-0002: Re-instatement | A | PI | HEC PI Construction | J.W.JEONG | 2023-01-13 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25390 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Touch up paint on support (810-2"-IA-00112-MS-2-N) | C | PA | HEC PA Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-02-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25391 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Missing lock pin on handwheel (near PSV-0008A) | A | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25392 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Loose lockin handwheel (near PSV-0008B) | A | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25393 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Housekeeping to be done | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-03-24 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25394 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Missing eye hook | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25395 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Insulation to be fixed | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-03-21 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25396 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Coupling guard to be fixed | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25397 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Oil gauge to te tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25398 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Housekeeping to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25399 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Nut to be tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25400 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Missing eye hook | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25401 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Insulation to be fixed | C | IN | HEC IN Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-04-06 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25402 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Oil gauge to te tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25403 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Housekeeping to be done | B | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25404 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Nut to be tightened | A | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25405 | 810.10 | 810-10-28 | 810-MP0011A |  | Not fixed to foundation pump coupling protection cover | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2023-01-13 | 2023-01-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25406 | 810.10 | 810-10-28 | 810-MP0011B |  | Not fixed grounding connection to control panel support | A | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2023-01-13 | 2023-01-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25407 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Vent line not plugged | B | PI | HEC PI Construction | Mr. Krzysztof Nolbert | 2023-01-13 | 2023-01-20 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25408 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | heat tracing not finished | A | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2023-01-13 | 2023-01-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25409 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Heat tracing junction boxes not grounded | C | EL | HEC EL Construction | Mr. Krzysztof Nolbert | 2023-01-13 | 2023-05-15 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25410 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Rusted fixing elements at flanges | C | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2023-01-13 | 2023-01-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25411 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Not properly fixed nuts at valve hand wheel | A | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2023-01-13 | 2023-01-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25412 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | House keeping ncessary after concrete polishing | C | ME | HEC ME Construction | Mr. Krzysztof Nolbert | 2023-01-13 | 2023-01-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25413 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Wet insulation at outdoor pipeline (not finished insulation jacketing | C | IN | HEC IN Construction | Mr. Krzysztof Nolbert | 2023-01-13 | 2023-02-14 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 25414 | 810.10 | 810-10-28 | Potable Water storage and Distribution System |  | Not finished safety shawers | C | EM | HEC SE Design | Mr. Krzysztof Nolbert | 2023-01-13 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29630 | 810.10 | 810-10-28 | IN_Piping Insulation - AUX | 200FS2-W-0001 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29631 | 810.10 | 810-10-28 | IN_Piping Insulation - AUX | 200FS3-W-1001 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29635 | 810.10 | 810-10-28 | IN_Piping Insulation - AUX | 200RS1-W-0001 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29636 | 810.10 | 810-10-28 | IN_Piping Insulation - AUX | 200RS1-W-0002 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29639 | 810.10 | 810-10-19 | IN_Piping Insulation - AUX | 600PR-SW-1001 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29642 | 810.12 | 810-12-10 | IN_Piping Insulation - AUX | 600PS-FW-1003 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29649 | 810.10 | 810-10-28 | IN_Piping Insulation - AUX | 850WT-W-1001 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 29650 | 810.10 | 810-10-28 | IN_Piping Insulation - AUX | 850WT-W-1002 (IN) | Insulation Final Inspection not done. | C | IN | HEC IN Construction | S.C.Lee | 2023-02-09 | 2023-03-17 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30547 | 810.10 | 810-10-36 | 810-FT9201 | 810-PRO-PID-00021A | Broken glass | C | CI | HEC CI Construction | Mr. Bartosz Łuczak | 2023-02-25 |  | PAC | [8 empty] | RFC/RFSU
. | 30548 | 810.10 | 810-10-40 | 900-6"-WW-00104-B1A1-ET | 970-00051 | misleading indication of valve open/close | C | PI | HEC PI Construction | Mr. Bartosz Łuczak | 2023-02-25 |  | PAC | [8 empty] | RFC/RFSU
. | 30549 | 810.10 | 810-10-10 | 810-X0001-M01 | 810-00101 | loose screws | C | PI | HEC PI Construction | Mr. Bartosz Łuczak | 2023-02-25 | 2023-04-05 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30663 | 810.10 | 810-10-28 |  |  | General comment: Missing green information plates in polish language | C | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2023-03-15 |  | PAC | [8 empty] | RFC/RFSU
. | 30664 | 810.10 | 810-10-28 |  |  | General comment: Missing lines to NY sewer | C | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2023-03-15 |  | PAC | [8 empty] | RFC/RFSU
. | 30665 | 810.10 | 810-10-28 | Unit 600/610 |  | 610-SS-002 not installed! | C | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-04-26 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30666 | 810.10 | 810-10-28 | Unit 600/610 |  | Shower head for 610-SS-001 not installed | C | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-04-26 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30667 | 810.10 | 810-10-28 | Unit 810 |  | No potable water supply to 810-SS-001 | C | COMM | HEC COMM | Ms. Małgorzata Juszczyk | 2023-03-15 |  | PAC | [8 empty] | RFC/RFSU
. | 30668 | 810.10 | 810-10-28 | Unit 810 |  | low water pressure for 810-SS-002 | C | COMM | HEC COMM | Ms. Małgorzata Juszczyk | 2023-03-15 |  | PAC | [8 empty] | RFC/RFSU
. | 30669 | 810.10 | 810-10-28 | Unit 850 |  | no potable water supply to 850-SS-001 | C | COMM | HEC COMM | Ms. Małgorzata Juszczyk | 2023-03-15 |  | PAC | [8 empty] | RFC/RFSU
. | 30670 | 810.10 | 810-10-28 | Unit 850 |  | no potable water supply to 850-SS-002 | C | COMM | HEC COMM | Ms. Małgorzata Juszczyk | 2023-03-15 |  | PAC | [8 empty] | RFC/RFSU
. | 30671 | 810.10 | 810-10-28 | Unit 860 |  | no potable water supply to 850-SS-002 | C | COMM | HEC COMM | Ms. Małgorzata Juszczyk | 2023-03-15 |  | PAC | [8 empty] | RFC/RFSU
. | 30672 | 810.10 | 810-10-28 | Unit 860 |  | 860-SS-001 ET not working | C | EL | HEC EL Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-03-27 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30673 | 810.10 | 810-10-28 | Unit 860 |  | 860-SS-001 Block valve damaged - unable to operate | C | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2023-03-15 |  | PAC | [8 empty] | RFC/RFSU
. | 30674 | 810.10 | 810-10-28 | PDH |  | Lack of access to the 200-SS-006 (scaffolding) | C | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-04-14 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30675 | 810.10 | 810-10-28 | PDH |  | Shower head for 200-SS-006 not installed | C | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-04-14 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30676 | 810.10 | 810-10-28 | PDH |  | 200-SS-007 ET not working | C | EL | HEC EL Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-04-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30677 | 810.10 | 810-10-28 | PDH |  | 200-SS-001 ET not working | C | EL | HEC EL Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-04-20 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30678 | 810.10 | 810-10-28 | PDH |  | 200-SS-001 block valve unable to operate | C | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-03-21 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30679 | 810.10 | 810-10-28 | PDH |  | 200-SS-002 ET not working | C | EL | HEC EL Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-04-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30680 | 810.10 | 810-10-28 | PDH |  | 200-SS-004 ET not working | C | EL | HEC EL Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-04-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30681 | 810.10 | 810-10-28 | PDH |  | 200-SS-003 ET not connected | C | EL | HEC EL Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-04-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30682 | 810.10 | 810-10-28 | PDH |  | 200-SS-003 block valve unable to operate | C | PI | HEC PI Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-03-21 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30683 | 810.10 | 810-10-28 | PDH |  | Shower head for 200-SS-003 not installed | C | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-04-14 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30684 | 810.10 | 810-10-28 | PDH |  | 200-SS-003 missing green information plates | C | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2023-03-15 | 2023-04-14 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31102 | 810.10 | 810-10-36 | 810-X0002-X02A/B | 810-X0002-X02A/B | DCS Op. Can control despite activation of local mode | C | COMM | HEC COMM | Mr. Damian Maciejaszek | 2023-03-17 |  | PAC | [8 empty] | RFC/RFSU
. | 31105 | 810.10 | 810-10-40 | 900-SN-5103 | 900-SN-5103 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31106 | 810.10 | 810-10-20 | 810-SN-9809 | 810-SN-9809 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-05 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31107 | 810.10 | 810-10-20 | 810-SN-9810 | 810-SN-9810 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-05 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31108 | 810.10 | 810-10-20 | 810-SN-9805 | 810-SN-9805 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31109 | 810.10 | 810-10-20 | 810-SN-9806 | 810-SN-9806 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31110 | 810.10 | 810-10-26 | 810-SN-8115 | 810-SN-8115 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31112 | 810.10 | 810-10-10 | 810-SN-9101 | 810-SN-9101 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31113 | 810.10 | 810-10-10 | 810-SN-9102 | 810-SN-9102 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31114 | 810.10 | 810-10-10 | 810-SN-9103 | 810-SN-9103 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31115 | 810.10 | 810-10-10 | 810-SN-9104 | 810-SN-9104 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31116 | 810.10 | 810-10-10 | 810-SN-9105 | 810-SN-9105 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31117 | 810.10 | 810-10-10 | 810-SN-9106 | 810-SN-9106 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31118 | 810.10 | 810-10-10 | 810-SN-9107 | 810-SN-9107 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31119 | 810.10 | 810-10-10 | 810-SN-9108 | 810-SN-9108 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31120 | 810.10 | 810-10-36 | 810-SN-8103 | 810-SN-8103 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31121 | 810.10 | 810-10-36 | 810-SN-9201 | 810-SN-9201 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-04-14 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31122 | 810.10 | 810-10-36 | 810-SN-9202 | 810-SN-9202 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-04-14 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31123 | 810.10 | 810-10-36 | 810-SN-9203 | 810-SN-9203 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-04-14 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31124 | 810.10 | 810-10-36 | 810-SN-9204 | 810-SN-9204 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-04-14 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31125 | 810.10 | 810-10-36 | 810-SN-9205 | 810-SN-9205 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-04-14 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31126 | 810.10 | 810-10-36 | 810-SN-9206 | 810-SN-9206 | Lack of nameplate, flow of water is directly on the electrical heating | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-22 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31127 | 810.10 | 810-10-36 | 810-SN-9207 | 810-SN-9207 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-04 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31128 | 810.10 | 810-10-34 | 810-SN-8107 | 810-SN-8107 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-02 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31129 | 810.10 | 810-10-28 | 810-SN-8102 | 810-SN-8102 | Lack of nameplate, isolation valve is too high | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-22 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31130 | 810.10 | 810-10-28 | 810-SN-8118 | 810-SN-8118 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-02 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31131 | 810.10 | 810-10-18 | 810-SN-8112 | 810-SN-8112 | Lack of nameplate, isolation valve is too high, flow of water is directly on the electrical heating | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-22 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31132 | 810.10 | 810-10-18 | 810-SN-8108 | 810-SN-8108 | Lack of nameplate, isolation valve is too high, flow of water is directly on the electrical heating | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-22 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31133 | 810.10 | 810-10-40 | 900-SN-5102 | 900-SN-5102 | Lack of nameplate | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-03-17 | 2023-05-02 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31136 | 810.10 | 810-10-26 | Unit 810 | 810-PRO-PID-00171 | ET for samping point no. 8114 to be provided | C | EL | HEC EL Construction | Ms. Małgorzata Juszczyk | 2023-03-17 |  | PAC | [8 empty] | RFC/RFSU
. | 31229 | 810.10 | 810-10-20 | 810-X0008-ST01 |  | According to note no 5 to P&ID please fill oil to goose neck | C | ME | HEC ME Construction | Ms. Małgorzata Juszczyk | 2023-03-31 |  | PAC | [8 empty] | RFC/RFSU
. | 31298 | 810.10 | 810-10-18 | 810 | 810-ST0001 | Something is making loud noise inside the tank. Like some hard object is curculating and hitting the Tank walls from inside | C | ME | HEC ME Construction | Mr. Andrzej Przechrzta | 2023-04-06 |  | PAC | [8 empty] | RFC/RFSU
. | 31788 | 810.10 | 810-10-20 | 810-ST0002 | 810-ST0002 | No nitrogen blanket | C | ME | HEC ME Construction | Mr. Jarosław Pykosz | 2023-05-07 |  | PAC | [8 empty] | RFC/RFSU
. | 31791 | 810.10 | 810-10-10 | Backwash sequence DCS | PRE-Backwash step | Sequence is stopping beceause of low water flow 810FIC9161, sequence need to be reset to continue working | C | CI | HEC CI Construction | Mr. Aleksander Rożek | 2023-05-07 |  | PAC | [8 empty] | RFC/RFSU
. | 31856 | 810.10 | 810-10-36 | unit 810 |  | Insulation to be provided on line 810-1''-CH-96004-C1F0-ET | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2023-05-11 |  | PAC | [8 empty] | RFC/RFSU
. | 31858 | 810.10 | 810-10-36 | unit 810 |  | Collission of the ladder to the top of the clarifier chambers with insulation | C | IN | HEC IN Construction | Ms. Paulina Bajer | 2023-05-11 |  | PAC | [8 empty] | RFC/RFSU
. | 31859 | 810.10 | 810-10-36 | unit 810 |  | Incorrect tagging of chemical pipelines in the clarifier area (flocculant, coagulant, chlorinated water, caustic)- all are marked as "WODOROTLENEK SODU" = CAUSTIC), while only two of them regard caustic. | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2023-05-11 | 2023-05-15 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31860 | 810.10 | 810-10-32 | unit 810 |  | Safety gate on the ladder missing | C | ME | HEC ME Construction | Ms. Paulina Bajer | 2023-05-11 | 2023-06-12 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31978 | 810.10 | 810-10-42 | 810 -P0004B/ 810-P0004A |  | Present information that fire pomps number can works interchangeably 810-P0004B disel pump and the electrial pump 810-P0004A | C | ME | HEC ME Construction | Mr. Mariusz Pelc | 2023-05-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32046 | 810.10 | 810-10-28 | AUX area |  | groundung cable laying on the ground - as per attached drawing | C | EL | HEC EL Construction | Mr. Wojciech Chrzanowski | 2023-05-25 | 2023-06-13 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 32124 | 810.10 | 810-10-18 | unit 810 | 810-ST0001 | Gap in between Storage tank 810-ST0001 - crushed grouting arund bottom of the tank - the annular plate. Grouting to be repaired and gaps to be sealed. Pockets around annular plate of tank causing water stagnation and corrosion to be removed. | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-06-01 |  | PAC | [8 empty] | RFC/RFSU
. | 32125 | 810.10 | 810-10-26 | unit 810 | 810-ST0002 | Gap in between Storage tank 810-ST0002 - crushed grouting arund bottom of the tank - the annular plate. Grouting to be repaired and gaps to be sealed. Pockets around annular plate of tank causing water stagnation and corrosion to be removed. | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-06-01 |  | PAC | [8 empty] | RFC/RFSU
. | 32131 | 810.10 | 810-10-26 | unit 810 | 810-ST0002 | Insulation on valve box on sampling line (2" - nozzle SP1 ) is broken | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-06-01 |  | PAC | [8 empty] | RFC/RFSU
. | 32231 | 810.10 | 810-10-32 | unit 810 | 810-X0003-P01B | Drainage line (part made of GRE) is broken. | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-06-05 | 2023-06-15 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 32343 | 810.10 | 810-10-20 | 810-X0008-U01A | PID: 810-00151A 810-PG-9812 810-PG-9811 | PGs seems to be broken. Arrows are off the scale when there is no pressure | C | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2023-06-13 |  | PAC | [8 empty] | RFC/RFSU
. | 32346 | 810.10 | 810-10-28 | Potable water storage | PID: 810-00211 810-TG-1025 | TG (810-TG-1025) is broken | C | CI | HEC CI Construction | Mr. Damian Maciejaszek | 2023-06-13 |  | PAC | [8 empty] | RFC/RFSU
. | 32347 | 810.10 | 810-10-19 | 820-US-003 | 820-US-003 | Leak on the plant water line on utlity station (820-US-003). Pipe is rusty and insulation is damaged | C | PI | HEC PI Construction | Mr. Damian Maciejaszek | 2023-06-13 |  | PAC | [8 empty] | RFC/RFSU
. | 32354 | 810.10 | 810-10-42 | Fire water shelter | 810-P0005A | Pump 810-P0005A (jockey pump) switches on and after few seconds switches off several times per hour | C | ME | HEC ME Construction | Mr. Damian Maciejaszek | 2023-06-13 |  | PAC | [8 empty] | RFC/RFSU
. | 32439 | 810.10 | 810-10-20 | unit 810 | 810-X0008 | Insulation on Caustic Injection Skid for Regeneration (CSKID-5) is broken - cladding is crushed. | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-06-14 |  | PAC | [8 empty] | RFC/RFSU
. | 32440 | 810.10 | 810-10-20 | unit 810 | 810-X0008-BL01A/B | 810-PG-9885, 810-PG-9884 are lying on the ground (not fixed). | C | ME | HEC ME Construction | Mr. Krzysztof Kaliszyk | 2023-06-14 |  | PAC | [8 empty] | RFC/RFSU
. | 32441 | 810.10 | 810-10-40 | 820-PR-001 | 900-4"-WW-00105-B1A1-ET (support SG-C4) | Pipe not resting on support SG-C4 | C | PI | HEC PI Construction | Mr. Krzysztof Kaliszyk | 2023-06-14 |  | PAC | [8 empty] | RFC/RFSU
. | 32447 | 810.10 | 810-10-36 | unit 810 | Clarifier package | Incorrect piping service identification (colour and substance desription) - only caustic is marked in violet at Site, while there are also coagulant nad flocculant lines going to coagulation/flocculation chambers | C | PA | HEC PA Construction | Ms. Paulina Bajer | 2023-06-14 |  | PAC | [8 empty] | RFC/RFSU
. | 32448 | 810.10 | 810-10-28 |  | CCR section | Safety shower no. 200-SS-003 not working | C | PI | HEC PI Construction | Mr. Bartosz Michalonek | 2023-06-14 |  | PAC | [8 empty] | RFC/RFSU
. | EGAT-RFI-CI-CW-00978.01 | 810.10 | 810-10-10 | 810-X10002/3 | Cable tray | Provide additional support | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-03-22 | 2022-07-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01296.01 | 810.10 | 810-10-18 | Aux. Area | 810-FV-1012, 860-FV-1001 | Missing hanging tag to be provided | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-17 | 2022-07-26 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01319.01 | 810.10 | 810-10-28 | Aux. Area | 810-PV-1041A | Missing hanging tag to be provided | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-26 | 2022-09-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01360.01 | 810.10 | 810-10-10 | Auxilliary | 810-LV-1020 | Missing hanging tag to be provided | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-26 | 2022-06-27 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01360.02 | 810.10 | 810-10-10 | Auxilliary | 810-LV-1020 | Valve calibration to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-26 | 2022-08-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01366.01 | 810.10 | 810-10-28 | Aux. Area | Cable Laying | At section N1 and N2 temporary cable tie to be replace as per drawing | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-26 | 2022-10-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01366.02 | 810.10 | 810-10-28 | Aux. Area | Cable Laying | At section N1 and N2 distance of cable tie should be as per drawing | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-26 | 2022-10-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01373.01 | 810.10 | 810-10-26 | Auxiliary area | Thermowell | Torquing to be done | B | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-03 | 2022-09-26 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01388.01 | 810.10 | 810-10-28 | 810-SHT-CC-300 | LT/PT | Torquing to be done | B | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-03 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01390.01 | 810.10 | 810-10-28 | 810-SHT-CC-300 | LG/PG | Torquing to be done | B | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-03 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01392.01 | 810.10 | 810-10-26 | AUX AREA | Instrument Installation | Torquing to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-30 | 2022-09-29 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01420.01 | 810.10 | 810-10-10 | Auxiliary | 810-XV-9117, 810-XV-9118 | Missing hang tag for each valve | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-06-02 | 2022-06-27 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01420.02 | 810.10 | 810-10-10 | Auxiliary | 810-XV-9117,9118,9148,9147,9128,9138,9127,9137 | Solenoid valve should be mounted properly | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-06-02 | 2022-08-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01430.01 | 810.10 | 810-10-10 | Auxiliary | 810-PSV-9101, 810-PSV-9102 | Missing hang tag for each PSV valve | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-06-02 | 2022-06-27 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01447.01 | 810.10 | 810-10-40 | Waste water | EGAT-HEC-970-PRO-PID-00051 | Torquing to be done | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-06 | 2022-12-01 | Construction |  |  | 2022-12-01 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01448.01 | 810.10 | 810-10-28 | Auxiliary | 810-PV-1041A | Missing hang tag for manifold | A | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-03 | 2022-07-01 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01477.01 | 810.10 | 810-10-10 | Raw water building | 810-FT-9120, 9130 | SS tag to be provide | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-06 | 2022-07-29 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01477.02 | 810.10 | 810-10-10 | Raw water building | 810-FT-9140 | Lock screw missing | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-06 | 2022-07-26 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01477.03 | 810.10 | 810-10-10 | Raw water building | 810-FT-9120,9130,9140,9110 | Cleaning and preservation to be done | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-06 | 2022-07-27 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01484.01 | 810.10 | 810-10-20 | Raw water | EGAT-HEC-810-PRO-PID-00101 | 810-AR-569, 568, 570 Polish language phenolic tag wrong spelling to be corrected | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-06 | 2022-11-07 | Construction |  |  | 2022-11-05 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01484.02 | 810.10 | 810-10-20 | Raw water | EGAT-HEC-810-PRO-PID-00101 | 810-AR-569, 568, 570 Main earthing to be provided | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-06-06 | 2023-01-11 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01485.01 | 810.10 | 810-10-18 | Fire water | EGAT-HEC-810-PRO-PID-00101 | 810-TT-1004, TG-1015, PG-1009 Stud bolt torquing to be done | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-06 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01485.02 | 810.10 | 810-10-18 | Fire water | EGAT-HEC-810-PRO-PID-00101 | 810-TT-1004 Transmitter must be properly tighten | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-06 | 2022-11-22 | Construction | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01485.03 | 810.10 | 810-10-18 | Fire water | EGAT-HEC-810-PRO-PID-00101 | 810-TT-1004, TG-1015, PG-1009 Access to be provided | C | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-06-06 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01499.01 | 810.10 | 810-10-10 | Calibration | Magnetic flowmeter | Vendor calibration report to be attach | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-06-10 | 2022-08-17 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01500.01 | 810.10 | 810-10-32 | Calibration | 810-PT-9333 | Set range should be marked up in data sheet as per actual calibration range | A | EM | HEC MR Design | Mr. Tomasz Jozel | 2022-06-11 | 2022-11-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01500.02 | 810.10 | 810-10-20 | Calibration | 810-PT-9833 | Set range should be marked up in data sheet as per actual calibration range | A | EM | HEC MR Design | Mr. Tomasz Jozel | 2022-06-11 | 2022-09-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01507.01 | 810.10 | 810-10-18 | Fire Water AUX Area | EGAT-HEC-600-INC-DWG-00006_4 | At 810-SL-001 Temporary cable to be replaced as per drawing | B | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-07 | 2022-10-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01507.02 | 810.10 | 810-10-18 | Fire Water AUX Area | EGAT-HEC-600-INC-DWG-00006_4 | At 810-SL-001 Distance of Cable tie should be as per drawing | B | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-07 | 2022-10-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01509.01 | 810.10 | 810-10-18 | Fire water | EGAT-HEC-600-INC-DWG-00006_4 | Temperature transmitter elbow to be provide at termination point | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-09 | 2022-09-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01522.01 | 810.10 | 810-10-10 | Sand filter package | 810-PT-9101 | Grouting should be properly clean | A | CI | HEC CI Construction | Neilmar | 2022-06-11 | 2022-07-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01546.01 | 810.10 | 810-10-26 | Auxiliary | 810-TG-1016 | Torquing to be done | C | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01547.01 | 810.10 | 810-10-26 | Auxiliary | Instrument Installation | Temperature transmitter torquing to be done | C | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01547.02 | 810.10 | 810-10-26 | Auxiliary | 810-TT-1006 | LCD display need to be rotate | C | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-11-16 | Construction | 2022-11-13 |  | 2022-11-13 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01547.03 | 810.10 | 810-10-26 | Auxiliary | Remote Indicator | Sunshade to be install | C | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-12-01 | Construction |  |  | 2022-12-01 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01548.01 | 810.10 | 810-10-26 | Auxiliary | 810-FT-1020 | Torquing to be done | A | PI | HEC PI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-09-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01548.02 | 810.10 | 810-10-26 | Auxiliary | 810-FT-1020 | Earthing to be install | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-10-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01552.01 | 810.10 | 810-10-40 | Auxiliary | Instrument Installation | Torquing to be done | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-09-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01552.02 | 810.10 | 810-10-40 | Auxiliary | 810-FT-0511 | Earthing connection must be done | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-09-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01552.03 | 810.10 | 810-10-40 | Auxiliary | 810-LT-0511 | Sunshade to be install | C | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-11-22 | Construction | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01557.01 | 810.10 | 810-10-18 | Calibration | 810-FT-9161 | Nameplate calibration range should be change as per data sheet calibration range | A | EM | HEC MR Design | Mr. Tomasz Jozel | 2022-06-22 | 2022-10-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01558.01 | 810.10 | 810-10-20 | Calibration | 810-FT-9803, 9804, 9805 | Nameplate calibration range should be change as per data sheet calibration range | A | EM | HEC MR Design | Mr. Tomasz Jozel | 2022-06-22 | 2022-10-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01562.01 | 810.10 | 810-10-40 | Auxiliary | 900-FT-5102 | Torquing to be done | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01562.02 | 810.10 | 810-10-40 | Auxiliary | 900-FT-5102 | Earthing connection must be done | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-06-16 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01614.01 | 810.10 | 810-10-20 | Calibration | Flow Transmitter | 810-FT-9802, 9834, 9839, 9840 Nameplate calibration range should be change as per data sheet | A | EM | HEC MR Design | Mr. Michal Cwiklak | 2022-06-25 | 2022-10-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01635.01 | 810.10 | 810-10-18 | 820-PR-01 | 810-LI-1021B | SS Hanging tag missing | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-06-27 | 2022-07-26 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01653.01 | 810.10 | 810-10-18 | Fire water tank | 810-LI-1001B | SS Hanging tag to be provide | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-06-28 | 2022-07-26 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01653.02 | 810.10 | 810-10-18 | Fire water tank | 810-LI-1001B | Between baseplate and concrete foundation applied silicone sealant | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-06-28 | 2022-08-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01653.03 | 810.10 | 810-10-18 | Fire water tank | 810-LT-1001 | Calibration to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-06-28 | 2022-08-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01661.01 | 810.10 | 810-10-10 | Fire water | Cable laying | Temporary cable tie to be replace as per drawing | A | CI | HEC CI Construction | Neilmar | 2022-06-27 | 2022-08-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01661.02 | 810.10 | 810-10-10 | Fire water | Cable laying | Distance of cable tie should be as per drawing | A | CI | HEC CI Construction | Neilmar | 2022-06-27 | 2022-08-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01690.01 | 810.10 | 810-10-10 | Sand filter package | 810-AC-501 | Earthing to be done | A | EL | HEC EL Construction | Mr. Jaroslaw Lugowski | 2022-07-01 | 2022-08-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01690.02 | 810.10 | 810-10-10 | Sand filter package | 810-AC-501 | Terminal block above space heater not reflect in the drawing | A | EM | HEC MR Design | Mr. Jaroslaw Lugowski | 2022-07-01 | 2022-09-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01690.03 | 810.10 | 810-10-10 | Sand filter package | 810-AC-501 | Phenolic tag to be replace | B | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-07-01 | 2022-12-02 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01690.04 | 810.10 | 810-10-10 | Sand filter package | 810-AC-501 | Provide sticker for proper identification | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-07-01 | 2022-07-26 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01764.01 | 810.10 | 810-10-34 | Auxiliary Area | 810-LT-1012, 1013 | Torquing to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-07-11 | 2022-08-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01839.01 | 810.10 | 810-10-20 | Clarifier package | 810-AC-511, 521 | Main earth to be provided | A | EL | HEC EL Construction | Mr. Jaroslaw Lugowski | 2022-07-18 | 2022-11-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01839.02 | 810.10 | 810-10-20 | Clarifier package | 810-AC-511, 521 | TB above space heater not reflect in panel drawing | A | EM | HEC MR Design | Mr. Jaroslaw Lugowski | 2022-07-18 | 2022-09-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01839.03 | 810.10 | 810-10-20 | Clarifier package | 810-AC-511, 521 | Phenolic tag to be replace with polish language description | B | EM | HEC MR Design | Mr. Jaroslaw Lugowski | 2022-07-18 | 2022-11-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01839.04 | 810.10 | 810-10-20 | Clarifier package | 810-AC-521 | Door not properly allign | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-07-18 | 2022-09-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01877.01 | 810.10 | 810-10-10 | Calibration Shop | Pressure Gauge (4ea) | Data sheet model number P252 should be change as per actual model number P258 | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-07-21 | 2022-07-26 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01995.01 | 810.10 | 810-10-10 | Auxiliary | 810-AS-006 | Touch up paint for airline support | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-08-01 | 2022-08-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01995.02 | 810.10 | 810-10-10 | Auxiliary | 810-AS-006 | Provide identification hanging tag for sub header | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-08-01 | 2022-08-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02195.01 | 810.10 | 810-10-18 | Aux Area | 810-AC-501 | Missing Tee for Spare With Blind Need to Provide | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-08-17 | 2023-05-01 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02196.01 | 810.10 | 810-10-18 | Auxiliary | 810-FV-9161 | Missing tee for spare with blind plug need to provide | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-08-19 | 2022-09-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02231.01 | 810.10 | 810-10-20 | Auxiliary | 810-AC-561 | Switch box cable gland to be tighten | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-08-19 | 2022-08-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02231.02 | 810.10 | 810-10-20 | Auxiliary | 810--AC-561 | Wrong tag number of cabinet | B | EM | HEC MR Design | Mr. Michal Cwiklak | 2022-08-19 | 2022-11-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02290.01 | 810.10 | 810-10-18 | 810 Auxiliary | 810-FT-9161 | 1/4 SS tube cup for drain to be provide | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-08-25 | 2022-11-22 | Construction | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02336.01 | 810.10 | 810-10-18 | Cooling water | 860-FT-1001, 1010 | 1/2 nipple to be verify | A | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-09-05 | 2022-11-23 | Construction | 2022-11-23 | 2022-11-23 | 2022-11-23 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02409.01 | 810.10 | 810-10-28 | Fire water treatment | Impulse tubing | Additional support to be provided for 810-PT-1036,1041 | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-05 | 2022-11-21 | Construction | 2022-11-18 | Rejected by PMC.. Support neet to re-weld | 2022-11-18 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02418.01 | 810.10 | 810-10-26 | Raw water treatment | 810-FT-1019, 1018, PT-1034 | 1/4 SS tube for drain to be provide | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-05 | 2022-11-30 | Construction | 2022-11-18 | 2022-11-30 | 2022-11-29 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02418.02 | 810.10 | 810-10-26 | Raw water treatment | 810-LT-1027, 1026 | Sunshade to be provide | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-05 | 2022-09-13 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02418.03 | 810.10 | 810-10-26 | Raw water treatment | 810-LT-1027, 1026 | Torquing to be done | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-05 | 2022-09-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02418.04 | 810.10 | 810-10-26 | Raw water treatment | 810-LT-1027, 1026 | Calibration to be done | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-05 | 2022-10-31 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02419.01 | 810.10 | 810-10-20 | Demi water | Instrument Installation (9ea) | 1/4 SS tube for drain to be provide | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-05 | 2022-11-30 | Construction | 2022-11-18 | 2022-11-30 | 2022-11-29 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02419.02 | 810.10 | 810-10-20 | Demi water | 810-FT-9804 | Touch up paint for the stanchion | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-05 | 2022-09-13 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02419.03 | 810.10 | 810-10-20 | Demi water | 810-TT-9804 | Sunshade to be provide | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-05 | 2022-11-02 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02640.01 | 810.10 | 810-10-36 | Clarifier (AUX) | EGAT-HEC-600-INC-DLP-00001_6 | Sun Shade to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-11-22 | Construction | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02640.02 | 810.10 | 810-10-36 | Clarifier (AUX) | EGAT-HEC-600-INC-DLP-00001_6 | 810-FT-9201, 9211 Stanchion base plate to be clean | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-10-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02640.03 | 810.10 | 810-10-36 | Clarifier (AUX) | EGAT-HEC-600-INC-DLP-00001_6 | Provide Additional Earthing (Instrument) | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-11-22 | Construction | 2022-11-17 | 2022-11-22 | 2022-11-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02640.04 | 810.10 | 810-10-36 | Clarifier (AUX) | EGAT-HEC-600-INC-DLP-00001_6 | Touch up paint of the instrument to be done | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-11-22 | Construction | 2022-11-18 | 2022-11-22 | 2022-11-18 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02641.01 | 810.10 | 810-10-34 | Clarifier (AUX) | EGAT-HEC-600-INC-DLP-00001_6 | Bolt Torquing to be done | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-12-01 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02641.02 | 810.10 | 810-10-34 | Clarifier (AUX) | EGAT-HEC-600-INC-DLP-00001_6 | SS Hanging tag to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-11-22 | Construction | 2022-11-17 | 2022-11-22 | 2022-11-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02641.03 | 810.10 | 810-10-34 | Clarifier (AUX) | EGAT-HEC-600-INC-DLP-00001_6 | Grounding ring to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-11-22 | Construction | 2022-11-17 | 2022-11-22 | 2022-11-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02641.04 | 810.10 | 810-10-34 | Clarifier (AUX) | EGAT-HEC-600-INC-DLP-00001_6 | 810-FE-9334 Rusted bolt to be cleaned | B | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2023-01-17 | Construction |  |  | 2023-01-14 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02641.05 | 810.10 | 810-10-34 | Clarifier (AUX) | EGAT-HEC-600-INC-DLP-00001_6 | 810-FE-9241 Touch up paint to be done | C | CI | CW Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2023-03-10 | Construction |  |  | 2023-03-10 | Need to Re-Submit | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02647.01 | 810.10 | 810-10-32 | Clarifier (AUX) | 810-FT-9334 (TAG) | Sun Shade to be provided | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-11-10 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02647.02 | 810.10 | 810-10-32 | Clarifier (AUX) | 810-FT-9334 (TAG) | Rusted bolt to be replaced | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02651.01 | 810.10 | 810-10-26 | AUX | 840-M0001 | Torquing to be done | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02651.02 | 810.10 | 810-10-26 | AUX | 840-M0001 | Hook up drawing to be revised for stud bolt length | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-09-07 | 2022-10-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02717.01 | 810.10 | 810-10-26 | 840 AUX AREA | 840-FT-1003 (TAG) | SS Hanging tag to be provided | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-13 | 2022-11-10 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02717.02 | 810.10 | 810-10-26 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | 1/4 Drain tube to be provided | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-13 | 2022-11-09 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02717.03 | 810.10 | 810-10-26 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | Grouting form works to be removed and cleaned | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-13 | 2022-11-04 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02717.04 | 810.10 | 810-10-26 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | Grouting form works to be removed and cleaned | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-13 | 2022-11-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02717.05 | 810.10 | 810-10-26 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | Thermostat properly fixed (GEN) | A | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-13 | 2022-11-04 | Construction |  |  | 2022-11-08 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02719.01 | 810.10 | 810-10-40 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | SS Hanging tag to be provided | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-13 | 2022-11-22 | Construction | 2022-11-15 | 2022-11-22 | 2022-11-15 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02719.02 | 810.10 | 810-10-40 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | Cable tray to be provided ( Capillary Tube ) | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-13 | 2022-11-22 | Construction | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02719.03 | 810.10 | 810-10-40 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | Torquing to be done | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-13 | 2022-11-22 | Construction | 2022-11-15 | 2022-11-22 | 2022-11-15 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02719.04 | 810.10 | 810-10-40 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | Sun Shade to be provided | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-13 | 2022-11-22 | Construction | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02719.05 | 810.10 | 810-10-40 | 840 AUX AREA | EGAT-HEC-600-INC-DLP-00001_6 | Drawing Elevation needs to be revised | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-13 | 2022-12-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02727.02 | 810.10 | 810-10-20 | Recycle Water Basin Auxiliary area | 810-XV-9838 | Bolt torque to be done | C | CI | HEC CI Construction | Ariel Lazaro | 2022-09-14 | 2023-05-02 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02755.01 | 810.10 | 810-10-32 | Sand filter package | 810-XV-9361 , 810-XV-9362 , 810-XV-9351 , 810-XV-9352 | Valve elevation to be update in the drawing as per actual valve isntallation | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-15 | 2022-12-08 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02763.01 | 810.10 | 810-10-32 | AUX Area | 810-X0003-P01 A/B | Torquing to be done for TG & PG | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-14 | 2022-11-09 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02763.02 | 810.10 | 810-10-32 | AUX Area | 810-X0003-P01 A/B | Hook up drawing to be revised for stud bolt length | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-14 | 2022-10-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02834.01 | 810.10 | 810-10-19 | 700 Auxillary Area | 700-XV-1001 | Permanent gasket to be provided | A | PI | HEC PI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-19 | 2022-10-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02834.02 | 810.10 | 810-10-19 | 700 Auxillary Area | 700-XV-1001 | Bolt Torquing to be done with permanent stud bolts | A | PI | HEC PI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-19 | 2022-11-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02848.01 | 810.10 | 810-10-40 | Inter connecting CW Area | EGAT-HEC-600-INC-DLP-00001_6 | Earthing Ring to be provided | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-16 | 2022-12-02 | Construction |  |  | 2022-12-01 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02848.02 | 810.10 | 810-10-40 | Inter connecting CW Area | EGAT-HEC-600-INC-DLP-00001_6 | Callibration to be done | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-16 | 2023-01-27 | Construction |  |  | 2023-01-27 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02865.01 | 810.10 | 810-10-14 | Cooling Water AUX Area | 860-FT-1002 | Callibration to be done | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-20 | 2022-12-30 | Construction |  |  | 2022-12-30 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02865.02 | 810.10 | 810-10-14 | Cooling Water AUX Area | 860-FT-1002 | FE sensor not installed | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-20 | 2022-11-21 | Construction | 2022-11-18 |  | 2022-11-18 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02866.01 | 810.10 | 810-10-10 | Fire Water Tank AUX Area | EGAT-HEC-600-INC-DLP-00001_6 | Hook up drawing to be revised (bolt) | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-20 | 2022-10-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02866.02 | 810.10 | 810-10-10 | Fire Water Tank AUX Area | EGAT-HEC-600-INC-DLP-00001_6 | Transmitter hole for mounting bracket plug to be provided | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-09-20 | 2022-10-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02907.01 | 810.10 | 810-10-18 | AUX Area |  | Torquing to be done for TG | A | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-09-21 | 2022-11-17 | Construction | 2022-11-15 | 2022-11-17 | 2022-11-15 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02907.02 | 810.10 | 810-10-18 | AUX Area |  | Hook Up Drawing to be revised for Stud Bolt length | A | CI | HEC CI Construction | Mr. Adam Zbroja | 2022-09-21 | 2022-10-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02966.01 | 810.10 | 810-10-36 | AUX AREA | EGAT-HEC-000-HOK-00001_10 | TORQUING TO BE DONE | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-27 | 2023-05-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02966.02 | 810.10 | 810-10-36 | Aux Area | EGAT-HEC-INC-HOK-00001_10 | Hook up Drawing to be Revised for Stud Bolt Length | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-27 | 2023-05-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02967.01 | 810.10 | 810-10-34 | AUX AREA | EGAT-HEC-000-INC-HOK-00001_10 | TORQUING TO BE DONE | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-27 | 2023-04-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02967.02 | 810.10 | 810-10-34 | Aux Area | EGAT-HEC-000-INC-HOK-00001_10 | Hook up Drawing to be Revised for Stud Bolt Length | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-27 | 2023-05-01 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02967.03 | 810.10 | 810-10-34 | AUX area | EGAT-HEC-000-INC-HOK-00001_10 | Additional support for capillary tube | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-27 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-02967.04 | 810.10 | 810-10-34 | AUX area | EGAT-HEC-000-INC-HOK-00001_10 | Gauges must be readable to operator | C | CI | HEC CI Construction | Mr. Michal Cwiklak | 2022-09-27 | 2023-05-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03747.01 | 810.10 | 810-10-19 | PLANT WATER DISTRIBUTION SYSTEM | 700-FO-1004 | VISUAL INSPECTION DOCUMENT NOT DELIVERED | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-27 | 2023-04-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03809.01 | 810.10 | 810-10-36 | RAW WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | SUN SHADE TO BE PROVIDED | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-10-26 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03809.02 | 810.10 | 810-10-36 | RAW WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | ATEX BLIND PLUG TO BE PROVIDED | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-10-26 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03813.01 | 810.10 | 810-10-12 | AUXILIARY | 810-BPV-9511 | Provide permanent hanging tag | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-27 | 2022-11-18 |  | 2022-11-18 | 2022-11-18 | 2022-11-18 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03831.01 | 810.10 | 810-10-20 | CLARIFIRE | EGAT-HEC-600-INC-DLP-00001_Z0 | EARTING TO BE PROVIDED | A | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-10-26 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03831.02 | 810.10 | 810-10-20 | CLARIFIRE | EGAT-HEC-600-INC-DLP-00001_Z0 | PROVIDE ISOLATION RUBBER FOR STANCHION AND PANEL | B | CI | HEC CI Construction | Mr. Jaroslaw Lugowski | 2022-10-26 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03922.01 | 810.10 | 810-10-20 | CLARIFIER | EGAT-HEC-600-INC-DLP-00001_Z0 | EARTING TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-12-01 |  |  |  | 2022-11-30 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03922.02 | 810.10 | 810-10-20 | CLARIFIER | EGAT-HEC-600-INC-DLP-00001_Z0 | STANCHION ANCHOR BOLT LONG NEED TO CUT | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-30 |  |  |  | 2022-11-30 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03922.03 | 810.10 | 810-10-20 | CLARIFIER | EGAT-HEC-600-INC-DLP-00001_Z0 | PANEL SHAKING ADDITIONAL SUPPORT | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03925.01 | 810.10 | 810-10-20 | 810-SL-003 | EGAT-HEC-600-INC-DLP-00001_Z0 | SS HANGING TAG FOR TAPPING POINT TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-23 |  | 2022-11-23 | 2022-11-23 | 2022-11-23 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03936.01 | 810.10 | 810-10-32 | RAW WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | CABLE ENTRY PROVIDE SEALANT | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03936.02 | 810.10 | 810-10-32 | RAW WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | STANCHION ANCHOR BOLT LONG NEED TO CUT | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03937.01 | 810.10 | 810-10-40 | PR-01 AUX. | EGAT-HEC-600-INC-DLP-00001_Z0 | SS HANGING TAG FOR TAPPING POINT TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-24 |  |  | 2022-11-24 | 2022-11-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03943.01 | 810.10 | 810-10-40 | PR-01 AUX. | EGAT-HEC-600-INC-DPL-00001_Z0 | SS HANGING TAG FOR TAPPING POINT TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-24 |  | 2022-11-24 | 2022-11-24 | 2022-11-24 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03944.01 | 810.10 | 810-10-40 | 810-SL-004 | EGAT-HEC-600-INC-DPL-00001_Z0 | SS HANGING TAG FOR TAPPING POINT TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-23 |  | 2022-11-23 | 2022-11-23 | 2022-11-23 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03953.01 | 810.10 | 810-10-20 | 810-SL-003 | EGAT-HEC-600-INC-DLP-00001_Z0 | SS HANGING TAG FOR TAPPING POINT TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03953.02 | 810.10 | 810-10-20 | 810-SL-003 | EGAT-HEC-600-INC-DLP-00001_Z0 | 810FT9834, PT9833 ADDITIONAL SUPPORT | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-23 |  | 2022-11-23 | 2022-11-23 | 2022-11-23 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03955.01 | 810.10 | 810-10-26 | 810-SL-003 | EGAT-HEC-600-INC-DLP-00001_Z0 | SS HANGING TAG FOR TAPPING POINT TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03956.01 | 810.10 | 810-10-26 | 810-SL003 | EGAT-HEC-600-INC-DLP-00001_Z0 | SS HANGING TAG FOR TAPPING POINT TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-29 | 2022-11-24 |  | 2022-11-24 | 2022-11-24 | 2022-11-24 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03993.01 | 810.10 | 810-10-20 | AUX | EGAT-HEC-600-INC-DWG-00006_Z0 | AT TAG NUMBER 810-JA-522, 810-JA-523, 810-TSH-9323, CABLE DUCT TRAY COVER TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-03 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03993.02 | 810.10 | 810-10-20 | AUX | EGAT-HEC-600-INC-DWG-00006_Z0 | AT TAG NUMBER 810-JA-522, 810-JA-523, 810-TSH-9323, CABLE TAGGING TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-03 | 2022-11-22 |  | 2022-11-21 | 2022-11-22 | 2022-11-21 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04084.01 | 810.10 | 810-10-26 | 810 AUX AREA | 810-PRV-006 | Deformed copper tube need to be replaced | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-03 | 2022-12-29 |  |  |  | 2022-12-02 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04086.01 | 810.10 | 810-10-26 | RAW WATER TREATMENT | EGAT-HEC-600-INC-DLP-00001_Z0 | ALL TT BOLT LENGTH HOOK UP DRAWING TO BE REVISED | C | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-11-03 | 2023-06-15 | Construction | [8 empty] | Construction
. | EGAT-RFI-CI-CW-04086.02 | 810.10 | 810-10-26 | RAW WATER TREATMENT | EGAT-HEC-600-INC-DLP-00001_Z0 | SS HANGING TAG TO BE PROVIDE | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-03 | 2023-06-15 | Construction | [8 empty] | Construction
. | EGAT-RFI-CI-CW-04092.01 | 810.10 | 810-10-32 | NITROGEN AREA | EGAT-HEC-600-INC-DPL-00001_Z0 | SS HANGING TAG FOR TAPPING TO BE PROVIDED | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-03 | 2022-11-28 |  | 2022-11-28 |  | 2022-11-28 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04092.02 | 810.10 | 810-10-32 | NITROGEN AREA | EGAT-HEC-600-INC-DPL-00001_Z0 | PLASTIC CABLE TIE TO BE CHANGED IN SS CABLE TIE | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-03 | 2022-11-28 |  | 2022-11-28 |  | 2022-11-28 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04539.01 | 810.10 | 810-10-40 | PDH | EGAT-HEC-200-INC-DWG-00006_2 | CABLE TAGGING TO BE PROVIDED AT JB (230-PT-0602) | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-24 | 2022-12-09 |  |  |  | 2022-12-02 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04539.02 | 810.10 | 810-10-19 | AUX | EGAT-HEC-200-INC-DWG-00006_2 | CABLE TAGGING TO BE PROVIDED AT INSTRUMENT (850-LT-0511) | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-11-24 | 2022-12-09 |  |  |  | 2022-12-02 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04609.01 | 810.12 | 810-12-14 | COOLING WATER DELUGE | EGAT-HEC-600-INC-DWG-00006_Z0 | CABLE TAGGING TO BE PROVIDED AT INSTRUMENT (860-SOV-1003, 860-PSH-1005) | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-12-19 | 2023-01-03 |  |  |  | 2023-01-03 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04609.02 | 810.12 | 810-12-14 | COOLING WATER DELUGE | EGAT-HEC-600-INC-DWG-00006_Z0 | AT INSTRUMENT GROUNDING TO BE PROVIDED 860-SOV-1003) | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-12-19 | 2023-01-03 |  |  |  | 2023-01-03 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04713.01 | 810.10 | 810-10-42 | AUX AREA | 810-PRV-1009 | WRONG HANGING TAG NEED TO BE REPLACE ON ACTUAL INSTALLED | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-12-07 | 2022-12-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04732.01 | 810.10 | 810-10-19 | PDH AREA | 230-PT-0602 | GROUNDING TO BE PROVIDE STANCHION SIDE | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-12-07 | 2022-12-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04732.02 | 810.10 | 810-10-19 | PDH AREA | 230-PT-0602 | ATEX PLUG TO BE PROVIDE | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-12-07 | 2022-12-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04747.01 | 810.10 | 810-10-40 | 1000-PW-32 WASTE WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | BOLT TORQUING TO BE DONE | A | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-12-07 | 2023-01-03 |  |  |  | 2023-01-03 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04747.02 | 810.10 | 810-10-40 | 1000-PW-32 WASTE WATER | EGAT-HEC-600-INC-DLP-00001_Z0 | SUNSHADE TO BE PROVIDED | B | CI | HEC CI Construction | Ms. Agnieszka Szyndler-Jurszo | 2022-12-07 | 2023-01-10 |  |  |  | 2023-01-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-05585.01 | 810.10 | 810-10-42 | AUXILIARY AREA | 810-PG-2973 | Over-Range Protector (Gauge Saver) missing | A | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2023-01-31 | 2023-02-08 |  |  |  | 2023-02-07 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-05750.01 | 810.10 | 810-10-10 | 810 AUX AREA | 810AT9151, 810AT9886, 810AT9896 | ADDITIONAL SUPPORT AND CABLE TRAY | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2023-01-25 | 2023-02-06 |  |  |  | 2023-02-03 |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00823.01 | 810.10 | 810-10-18 | 810 Unit | EGAT-HEC-900-ELE-DLP-01003_2,01004_0,01005_0,01006_2 | Above Ground Cable Installation inspection carried out for steam generator Cables And Fire Pump LCP MV Cables. | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-07-06 | 2022-08-11 | Construction |  |  |  |  | V | 2022-08-30 |  |  | Construction
. | EGAT-RFI-EL-SB-00823.02 | 810.10 | 810-10-18 | AUX | EGAT-HEC-900-ELE-DLP-01003_2,01004_0,01005_0,01006_2 | Red marked Drawing to be revised and submitted officially. | B | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-10-08 | 2022-07-29 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00824.01 | 810.10 | 810-10-18 | 810 Unit | EGAT-HEC-900-ELE-DLP-01003_2,01004_0,01005_0,01006_2 | Above Ground Cable Installation inspection carried out for steam generator Cables And Fire Pump LCP MV Cables. | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-07-06 | 2022-08-11 | Construction |  |  |  |  | V | 2022-08-30 |  |  | Construction
. | EGAT-RFI-EL-SB-00824.02 | 810.10 | 810-10-18 | AUX | EGAT-HEC-900-ELE-DLP-01003_2,01004_0,01005_0,01006_2 | Red marked Drawing to be revised and submitted officially. | B | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-10-08 | 2023-01-17 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00825.01 | 810.10 | 810-10-18 | 810 Unit | EGAT-HEC-900-ELE-DLP-01003_2,01004_0,01005_0,01006_2 | Above Ground Cable Installation inspection carried out for steam generator Cables And Fire Pump LCP MV Cables. | A | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-07-06 | 2022-08-11 | Construction |  |  |  |  | V | 2022-08-30 |  |  | Construction
. | EGAT-RFI-EL-SB-00825.02 | 810.10 | 810-10-18 | AUX | EGAT-HEC-900-ELE-DLP-01003_2,01004_0,01005_0,01006_2 | Red marked Drawing to be revised and submitted officially. | B | EL | HEC EL Construction | Mr. Szymon Woyke | 2021-10-08 | 2023-01-17 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02012.01 | 810.10 | 810-10-20 | Aux Unit-810 | EGAT-HEC-900-ELE-DLP-01004 | Provide installation details of height of Junction box (810-X0008-MP01A/B) | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-03-29 | 2023-01-11 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02117.01 | 810.10 | 810-10-40 | PDH | EGAT-HEC-200-ELE-DLP-01002_3 & EGAT-HEC-900-ELE-DLP-01028_5 | Backfilling should not be done up to 2 meters from wall for the purpose of duct sealing. | B | EL | HEC EL Construction | Mr. Arkadiusz Tryniszewski | 2022-04-06 | 2023-01-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05947.01 | 810.10 | 810-10-20 | AUX/810 | Lightning & Accessories | Copper tape to be cleaned of plaster paint | C | EL | Shinbo Electrical Subcon. | Mr. Arkadiusz Tryniszewski | 2023-01-11 | 2023-03-21 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02248 | 810.10 | 810-10-28 | PDH | 810-P0011A | One scaffolding post was on pump foundation, needs to remove | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-22 | 2022-10-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02249 | 810.10 | 810-10-28 | PDH | 810-P0011B | One scaffolding post was on pump foundation, needs to remove | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-22 | 2022-10-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02265.1 | 810.10 | 810-10-10 | 810 | 810-X0001-U01A | Sand filter in polish translation at the nameplate to be corrected | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-07-05 | 2023-06-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02265.2 | 810.10 | 810-10-10 | 810 | 810-X0001-U01A | Housekeeping of the equipment is required specially on the top platform and top portion of the equipment body | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-07-05 | 2023-06-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02265.3 | 810.10 | 810-10-10 | 810 | 810-X0001-U01A | Touch-up paint on gratings, grating support, handrils and equipment body | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-07-05 | 2023-06-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02265.4 | 810.10 | 810-10-10 | 810 | 810-X0001-U01A | Gratings to be align and elips to be tightened | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-07-05 | 2023-06-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02290.1 | 810.10 | 810-10-20 | PDH | 810-X0008-ST01/P03AB | Stud bolts to be protected with molecote | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2022-11-15 | Construction | [8 empty] | Construction
. | EGAT-RFI-ME-DA-02290.2 | 810.10 | 810-10-20 | PDH | 810-X0008-ST01/P03AB | Insulation damage to repair | C | IN | HEC IN Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2022-12-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02290.3 | 810.10 | 810-10-20 | PDH | 810-X0008-ST01/P03AB | Remove scaffolding on the skid | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2022-10-12 | Construction | [8 empty] | Construction
. | EGAT-RFI-ME-DA-02290.4 | 810.10 | 810-10-20 | PDH | 810-X0008-ST01/P03AB | Housekeeping in the area | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2022-11-17 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02291.1 | 810.10 | 810-10-20 | PDH | 810-X0008-ST02/P04AB | Stud bolts to be protected with molecote | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2022-11-15 | Construction | [8 empty] | Construction
. | EGAT-RFI-ME-DA-02291.2 | 810.10 | 810-10-20 | PDH | 810-X0008-ST02/P04AB | Insulation damage to repair | C | IN | HEC IN Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2022-12-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02291.3 | 810.10 | 810-10-20 | PDH | 810-X0008-ST02/P04AB | Remove scaffolding on the skid | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2022-10-12 | Construction | [8 empty] | Construction
. | EGAT-RFI-ME-DA-02291.4 | 810.10 | 810-10-20 | PDH | 810-X0008-ST02/P04AB | Housekeeping in the area | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-25 | 2022-11-17 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02304.1 | 810.10 | 810-10-10 | PDH | 810-X0001-U01A | Touch up on damage paint | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-09-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02304.2 | 810.10 | 810-10-10 | PDH | 810-X0001-U01A | Gratings to be aligned and clip tighten | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-09-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02304.3 | 810.10 | 810-10-10 | PDH | 810-X0001-U01A | Housekeeping on top platform | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-09-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02305.1 | 810.10 | 810-10-10 | PDH | 810-X0001-U01B | Touch up on damage paint | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-09-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02305.2 | 810.10 | 810-10-10 | PDH | 810-X0001-U01B | Gratings to be aligned and clip tighten | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-09-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02305.3 | 810.10 | 810-10-10 | PDH | 810-X0001-U01B | Housekeeping on top platform | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-09-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02306.1 | 810.10 | 810-10-10 | PDH | 810-X0001-U01C | Touch up on damage paint | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-09-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02306.2 | 810.10 | 810-10-10 | PDH | 810-X0001-U01C | Gratings to be aligned and clip tighten | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-09-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02306.3 | 810.10 | 810-10-10 | PDH | 810-X0001-U01C | Housekeeping on top platform | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-09-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02307.1 | 810.10 | 810-10-10 | PDH | 810-X0001-U01D | Touch up on damage paint | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-09-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02307.2 | 810.10 | 810-10-10 | PDH | 810-X0001-U01D | Gratings to be aligned and clip tighten | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-09-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02307.3 | 810.10 | 810-10-10 | PDH | 810-X0001-U01D | Housekeeping on top platform | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-08-23 | 2022-09-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02335 | 810.10 | 810-10-32 | PDH | 810-X0003-P01A | Heat tracing to install | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-08-30 | 2023-01-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02336 | 810.10 | 810-10-32 | PDH | 810-X0003-P01B | Heat tracing to install | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-08-30 | 2023-01-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02346 | 810.10 | 810-10-36 | PDH | 810-X0002-ST01/P03ABC | Nameplate to install | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-01 | 2023-04-06 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02347.1 | 810.10 | 810-10-32 | PDH | 810-X0003-ST01/P02ABC | Tank nameplate missing | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-01 | 2022-12-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02347.2 | 810.10 | 810-10-32 | PDH | 810-X0003-ST01/P02ABC | Pump nameplate missing | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-01 | 2022-12-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02347.3 | 810.10 | 810-10-32 | PDH | 810-X0003-ST01/P02ABC | Calibration pot valves handwheel (BA-93104 and BA-93107) orientation to be reviewed by engineering | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-01 | 2023-01-30 | Construction |  |  |  | (EM) 이미 Close되었던 Punch로, Access 가능합니다. FE Comment | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02347.4 | 810.10 | 810-10-32 | PDH | 810-X0003-ST01/P02ABC | Pipe support PS-10 section 3 of framework clashes the pipe line 810-3/4"-SW-93116-B1A1-N | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-01 | 2023-01-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02347.5 | 810.10 | 810-10-32 | PDH | 810-X0003-ST01/P02ABC | Grouting on control box | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-09-01 | 2023-01-11 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02451.1 | 810.10 | 810-10-20 | 810 | 810-X0008-U01A | Scaffolding to remove | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-26 | 2022-10-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02451.2 | 810.10 | 810-10-20 | 810 | 810-X0008-U01A | Touch up damage paint | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-26 | 2022-10-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02451.3 | 810.10 | 810-10-20 | 810 | 810-X0008-U01A | PSV tag missing (Piping) | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-26 | 2023-01-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02452.1 | 810.10 | 810-10-20 | 810 | 810-X0008-U01B | Scaffolding to remove | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-26 | 2022-10-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02452.2 | 810.10 | 810-10-20 | 810 | 810-X0008-U01B | Touch up damage paint | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-26 | 2022-10-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02453.1 | 810.10 | 810-10-20 | 810 | 810-X0008-VSKID-2A/B | Touch up paint analyzer box stand (Instrument) | C | CI | HEC CI Construction | Mr. Uladzimir Belavus | 2022-09-26 | 2022-11-09 | Construction |  |  | 2022-11-05 |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02453.2 | 810.10 | 810-10-20 | 810 | 810-X0008-VSKID-2A/B | Clamp rubber to put in good place of analyzer box stand (Instrument) | C | CI | HEC CI Construction | Mr. Uladzimir Belavus | 2022-09-26 | 2022-11-09 | Construction |  |  | 2022-11-09 |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02453.3 | 810.10 | 810-10-20 | 810 | 810-X0008-VSKID-2A/B | Provide the skid nameplate | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-26 | 2022-10-04 | Construction | [8 empty] | Construction
. | EGAT-RFI-ME-DA-02453.4 | 810.10 | 810-10-20 | 810 | 810-X0008-VSKID-2A/B | Housekeeping in the area | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-26 | 2022-10-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02457 | 810.10 | 810-10-36 | 810 | 810-X0002-P02A | Grouting on Local Control Panel to be done (Electrical) | B | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-09-23 | 2023-01-11 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02480.1 | 810.10 | 810-10-42 | 810 | 810-P0004B-ST | Provide nameplate of the tank | C | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-30 | 2023-03-02 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02480.2 | 810.10 | 810-10-42 | 810 | 810-P0004B-ST | Instrument connection to be completed | B | CI | HEC CI Construction | Mr. Uladzimir Belavus | 2022-09-30 | 2022-11-30 | Construction |  |  | 2022-11-30 |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02481.1 | 810.10 | 810-10-28 | PDH | 810-V0001 | No provision for gratings to be installed | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-30 | 2022-12-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02481.2 | 810.10 | 810-10-28 | PDH | 810-V0001 | Need gratings additional supports to avoid sagging | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-30 | 2022-12-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02481.3 | 810.10 | 810-10-28 | PDH | 810-V0001 | Touch up damage paint on platform | B | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-09-30 | 2022-12-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02529.01 | 810.10 | 810-10-18 | 810 | V-KHP-M28-810-ST0001-00001 REV. Z1 | Cathodic protection to be applied first after water filling of the tank. Inspection/information to be provided to PMC | C | ME | HEC ME Construction | Mr. Tomasz Trakul | 2023-06-23 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02529.02 | 810.10 | 810-10-18 | 810 | V-KHP-M28-810-ST0001-00001 REV. Z1 | Punch "D" acc to MC Procedure for corrosion at supports on horizontal parts, to be rectifield during turnover | C | ME | HEC ME Construction | Mr. Tomasz Trakul | 2023-06-23 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02596 | 810.10 | 810-10-32 | 810 | 810-X0003-X01A | Repair on internal bottom concrete and painting | A | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-11-14 | 2022-11-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02597 | 810.10 | 810-10-32 | 810 | 810-X0003-X01B | Repair on internal bottom concrete and painting | A | ME | HEC ME Construction | Mr. Uladzimir Belavus | 2022-11-14 | 2022-11-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02632 | 810.10 | 810-10-36 | 810 | 810-X0002-P01A | Heat tracing to install on pressure gauge pipe | A | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-12-09 | 2023-01-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-ME-DA-02633 | 810.10 | 810-10-36 | 810 | 810-X0002-P01B | Heat tracing to install on pressure gauge pipe | A | EL | HEC EL Construction | Mr. Uladzimir Belavus | 2022-12-09 | 2023-01-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | PICS.200FS1-W-0002.01 | 810.10 | 810-10-28 |  |  | Insulation not finished | C | IN | HEC IN Construction | Mr. Tomasz Trakul | 2022-11-28 | 2023-04-06 | Construction |  |  |  |  | V |  |  |  | RFC/RFSU
. | PICS.200PR1-FW-0003.01 | 810.10 | 810-10-14 |  |  | Insulation not finished | C | IN | HEC IN Construction | Mr. Tomasz Trakul | 2022-11-14 | 2023-04-06 | Construction |  |  |  |  | V |  |  |  | RFC/RFSU
. | PICS.810-10-14.01 | 810.10 | 810-10-14 |  | B1UG-FW-SD-0015, 450UG-FW-SD-0005-A | On PIV paint damaged portion touch up to be done | C | PI | HEC PI Construction | Vineesh Pushpakaran | 2022-10-01 | 2023-03-16 | Construction |  |  |  |  | V |  |  |  | RFC/RFSU

## AUX 4
AUX 4
No. | Punch No | System | Subsystem | Location / Area | Tag/Drawing/Line/Cable No. | Punch Description | Punch Category | Discipline | Action by | Originator | Issued Date | Closed Date | Punch Type | Note | Remarks | Submit to Owner | Punch Comment | File | RFI No | Report No.(Old) | Target Date | Scope of Punch
. | 27660 | 800.00 | 1304-12-17 | Guard House - Aux (3C) (1000-GH-48) | General | Lack of SAT inspection | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27661 | 800.00 | 1304-12-17 | Guard House - Aux (3C) (1000-GH-48) | General | Lack of Final Inspection - HVAC/Plumbng | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27662 | 800.00 | 1304-12-17 | Guard House - Aux (3C) (1000-GH-48) | General | Lack of Final Inspection - Fire Protection | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27663 | 800.00 | 1304-12-17 | Guard House - Aux (3C) (1000-GH-48) | General / PW installation | Lack of PW Inside installation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-03-30 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27664 | 800.00 | 1304-12-17 | Guard House - Aux (3C) (1000-GH-48) | General / SD installation | Lack of SD Inside installation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-03-30 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27665 | 800.00 | 1304-12-17 | Guard House - Aux (3C) (1000-GH-48) | General / Air condition | Lack of Air condition installation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-05-08 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27666 | 800.00 | 1304-12-17 | Guard House - Aux (3C) (1000-GH-48) | General / Ventilation system | Lack of ventilation system | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-03-30 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27667 | 800.00 | 1304-12-17 | Guard House - Aux (3C) (1000-GH-48) | General / SD installation | Lack of HVAC equipment | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-06-19 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28109 | 800.00 | 1304-12-17 | Guard House - Aux (3C) (1000-GH-48) |  | The building is underconstruction. No AR works has been finished. | C | AR | HEC AR Construction | Mr. Andrzej Wójcikiewicz | 2023-01-26 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28169 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-900-ELE-DLP-01030,EGAT-HEC-1000-ELE-DLP-04007,05008 | Normal and Emergency Lighting fixtures, Cable tray Installation to be complete and official inspection to be carried out. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28170 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-900-ELE-DLP-01030,EGAT-HEC-1000-ELE-DLP-04007,05008 | Tag no- 48-PDP-001, 002,003 and 48-ELP-001 Panel Installation to be done, | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 | 2023-05-16 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28171 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-900-ELE-DLP-01030,EGAT-HEC-1000-ELE-DLP-04007,05008 | Cable pulling and Cable termination to be done and official inspection to be carried out. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28172 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-900-ELE-DLP-01030,EGAT-HEC-1000-ELE-DLP-04007,05008 | Socket Outlet, Escape Lighting, Exit Lighting, Canopy lighting to be installed and officially inspection to be carried out. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28173 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-900-ELE-DLP-01030,EGAT-HEC-1000-ELE-DLP-04007,05008 | Lighting (48-ELP-001/12) on the roof to be installed and oficial inspection to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28174 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-900-ELE-DLP-01030,EGAT-HEC-1000-ELE-DLP-04007,05008 | Earthing for the Door frame, Monkey ladder, HVAC Fans(1000-GH48-ACCU-0001A/B, 0002, 0003,0004,0005&0006) to be connected and oficial inspection to be carried out. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28175 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-900-ELE-DLP-01030,EGAT-HEC-1000-ELE-DLP-04007,05008 | Lightning protection bare copper tape and lightning air terminal to be installed. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 | 2023-05-16 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28176 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-900-ELE-DLP-01030,EGAT-HEC-1000-ELE-DLP-04007,05008 | Earth rod with Test well for lightning protection to be installed . | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 | 2023-05-16 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28177 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-900-ELE-DLP-01030,EGAT-HEC-1000-ELE-DLP-04007,05008 | Earthing resistance test to be done protocol to be submitted. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28178 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-900-ELE-DLP-01030,EGAT-HEC-1000-ELE-DLP-04007,05008 | Illumination test to be done and protocol to be submitted. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28179 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-900-ELE-DLP-06007 | Smoke detectors, Fire Beacon, Remote Indicator,Power suppl unit, Manual call point, Alarm Pushbutton and Transponder I/O module box to be installed and oficially Inspection to be carried out. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28180 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-900-ELE-DLP-06007 | Fire alarm Cable pulling and termination to be done and oficial inspection to be carried out. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28181 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-900-ELE-DLP-06007 | Fire Alarm Sat to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28182 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-1000-INC-DLP-00214 | Telecommunication system installation to be done and official inspection to be carried out. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 | 2023-06-16 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28183 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-1000-INC-DLP-00214 | Telcommunication SAT to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28184 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-1000-INC-DLP-00314 | PAGA System installation to be done and official inspection to be carried out. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 | 2023-06-16 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28185 | 800.00 | 1304-12-17 | Guard House (1000-GH-48) | EGAT-HEC-1000-INC-DLP-00314 | PAGA SAT to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-27 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | EGAT-RFI-AR-GS-06561.01 | 800.00 | 1304-12-17 | 1000-GH-48 | Slab BS1 | Electrical conduits need to be removed from beam RW1 | C | EL | HEC EL Construction | Mr. Wojciech Grabowski | 2022-08-26 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-GS-06561 |  |  | Construction
. | EGAT-RFI-AR-GS-07626.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Correct the slope near the north wall | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-24 |  | Construction | [5 empty] | EGAT-RFI-AR-GS-07626 |  |  | Construction
. | EGAT-RFI-AR-GS-07646.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Top column to be repaired | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-03-06 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07813.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Add plaster under facade elements | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-11 | 2023-04-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-07813.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Finish facade by ground | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-11 | 2023-04-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-07813.03 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Windows opening to be checked after plastic cover removal | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-11 | 2023-04-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-07818.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Part of walls assembled with 2 layers | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-04-28 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07818.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Rigips approval required | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-04-28 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07819.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Rigips opinion required approval | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-04-28 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07820.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | A part of walls assembled with 2 layers | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-04-28 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07820.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Rigips approval rewuired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-04-28 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07822.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | First layer of gympsum boards need approval from vendor | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-04-28 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07828.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Skirting to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-04-17 | 2023-06-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-07971.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Scratches and touch ups | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07971.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Dooors need to be adjusted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07971.03 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Hinges to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07971.04 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Seals need to be improved | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07971.05 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Doors dents | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07971.06 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Surface pointing imperfections on the frame | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07972.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Room 3- touch ups done | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-07972.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Room 4- doors and frame painted with epoxy | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08010.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Tapes to be removed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 | 2023-06-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08010.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Electrical equipment should be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 | 2023-06-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08010.03 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Cable hole should be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 | 2023-06-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08013.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Cables and equipment should be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 | 2023-06-16 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08014.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Cables and equipment should be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 | 2023-06-16 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08014.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Hydraulic connections don't fit well | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 | 2023-06-16 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08016.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Unused electrical holes to be covered | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-20 | 2023-06-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08018.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Panel boards ans A/C equipment to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08019.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Ceiling should be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08020.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Panel boeards and A/C equipment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08021.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Panels to be cleaned, profiles to be adjusted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-09 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08022.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Panels to be cleaned, profiles to be adjusted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-09 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08024.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Panels and profiles to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-20 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08025.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Panels to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-17 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08025.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Protiles to be adjusted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-17 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08027.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Doors to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-20 | 2023-06-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08027.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Doors handle cover to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-20 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08027.03 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Plastic cover to be removed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-20 | 2023-06-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08038.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Windows to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08038.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Scratch on the window between rooms 2 & 1 | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08038.03 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Windows to be adjusted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 | 2023-06-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08039.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Paint coat damage | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-07 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08039.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Plastic cover to be removed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-07 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08039.03 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Frame top bolt to be adjusted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-07 | 2023-06-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08071.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Sealant to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-31 | 2023-06-01 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08075.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Tape to be removed, to be cleaned, sealant to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-01 | 2023-06-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08087.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Tiles to be exchanged above third doors | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-07 | 2023-06-16 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08095.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Sealant to be improved | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-31 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08096.0 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Verticaal chaamfering to be done | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-09 | 2023-06-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08096.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | To finished behind cable support foundation-east side | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-09 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08097.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Dilatation between building and stoops to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-31 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08133.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Windows to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08133.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Seal to be adjusted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08133.03 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Windows to be adjusted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08135.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Windows to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08135.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Seals to be adjusted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08135.03 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Windows to be adjusted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-13 | 2023-06-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08136.01 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Frame scratched | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-15 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08136.02 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Glass scratched | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-15 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-GS-08136.03 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Window to be adjusted | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-15 | 2023-06-20 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-GS-08136.04 | 800.00 | 1304-12-17 | 1000-GH-48 | - | Corrossion on frame | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-15 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-CI-CW-05426.01 | 800.00 | 1304-12-17 | STORAGE BUILDING AND GUARD HOUSE | EGAT-HEC-300-INC-DWG-00007_Z0 | AFTER TERMINATION COMPLETE CONTINUITY AND IR TEST TO BE DONE (55) | C | CI | CW Construction | Mr. Paweł Rogoziński | 2023-01-31 | 2023-04-12 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-05426.02 | 800.00 | 1304-12-17 | STORAGE BUILDING AND GUARD HOUSE | EGAT-HEC-300-INC-DWG-00007_Z0 | AFTER TERMINATION COMPLETE CONTINUITY AND IR TEST TO BE DONE (55) | C | CI | CW Construction | Mr. Paweł Rogoziński | 2023-01-31 | 2023-04-12 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-05905.01 | 800.00 | 1304-12-17 | Aux Guard house building | EGAT-HEC -600-INC-TDS-00052_Z0 | Alarm pre | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2023-03-08 | 2023-04-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04971.01 | 800.00 | 1304-12-17 | 1000-GH-44-PPL | EGAT-HEC-400-ELE-DWG-00006_4 | Drawing should be updated in the next revision | C | EL | HEC EL Design | Mr. Adam Siewiorek | 2022-10-27 | 2023-05-16 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07146.01 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-ELE-DLP-06007_Z0 | Fire Alarm Devivce Tag should be Provide (Fire Beaco, Horn, et..) | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07146.02 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-ELE-DLP-06007_Z0 | Missing 1000-GH-IP-0005 Should be install and complete cable Connection. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07146.03 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-ELE-DLP-06007_Z0 | CNBOP Sticker should be install for Fire Device. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07146.04 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-ELE-DLP-06007_Z0 | SAT should be done. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07147.01 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-ELE-DLP-06007_Z0 | Missing Cable Tag should be provide | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07147.02 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-ELE-DLP-06007_Z0 | Paint remove from the Cable and Clean. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07147.03 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-ELE-DLP-06007_Z0 | Reming Cable Connection should be complete | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07149.01 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-ELE-DLP-05008_Z0 | Earthing Connection should be provide for Lighting Cable Tray. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-06-20 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07149.02 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-ELE-DLP-05008_Z0 | CNBOP Lighting Junction box blind plugs to be install. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-06-20 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07149.03 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-ELE-DLP-05008_Z0 | Lighting Switch screw end plugs should be provided. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-06-20 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07151.01 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-INC-DLP-50214_Z0 | Security Cabinet Roof should change or repair. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07151.02 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-INC-DLP-50214_Z0 | Fuse or Others Device tag should be provide inside the Cabinet. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07151.03 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-INC-DLP-50214_Z0 | Missing Device should be nstall inside the Cabinet. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07151.04 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-INC-DLP-50214_Z0 | Inside the Cabinet cleaning must be done before SAT. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07151.05 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-INC-DLP-50214_Z0 | Cable Tag should be provide for Outside Camera. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-22 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07151.06 | 800.00 | 1304-12-17 | Guard House-48 | EGAT-HEC-1000-INC-DLP-50214_Z0 | Permanent Tag should be provide for Security Device. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07154.01 | 800.00 | 1304-12-17 | Guard House - 48 | EGAT-HEC-1000-INC-DLP-00214 & 00314_Z0 | Data outlet mounting be checked, proper Screw should be Install. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-14 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07154.02 | 800.00 | 1304-12-17 | Guard House - 48 | EGAT-HEC-1000-INC-DLP-00214 & 00314_Z0 | 48-SP-002 should be Install | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-14 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07154.03 | 800.00 | 1304-12-17 | Guard House - 48 | EGAT-HEC-1000-INC-DLP-00214 & 00314_Z0 | 48-DO-001 around of dta outlet gap shall be coverd. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-14 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07154.04 | 800.00 | 1304-12-17 | Guard House - 48 | EGAT-HEC-1000-INC-DLP-00214 & 00314_Z0 | 48-DO-001 should be relocated to place good access. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-14 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07157.01 | 800.00 | 1304-12-17 | Guard House - 48 | EGAT-HEC-1000-ELE-DLP-05008_Z0, EGAT-HEC-900-ELE-DLP-01030_Z0 | Missing Cable Tag should be provide near the wall inside the pit. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-06-20 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07157.02 | 800.00 | 1304-12-17 | Guard House - 48 | EGAT-HEC-1000-ELE-DLP-05008_Z0, EGAT-HEC-900-ELE-DLP-01030_Z0 | Cable Tray Route marker should be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-06-20 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07157.03 | 800.00 | 1304-12-17 | Guard House - 48 | EGAT-HEC-1000-ELE-DLP-05008_Z0, EGAT-HEC-900-ELE-DLP-01030_Z0 | Cable Tray Earthing connection should be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-06-20 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07157.04 | 800.00 | 1304-12-17 | Guard House - 48 | EGAT-HEC-1000-ELE-DLP-05008_Z0, EGAT-HEC-900-ELE-DLP-01030_Z0 | Grommet should be provide every Sharp Edge for cable tray. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-06-20 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01100.01 | 800.00 | 1304-12-17 | 1000-GH-48 | UG PW Pipe Installation | To be provided bolting report of PW connection | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01100 |  |  | Construction
. | EGAT-RFI-HV-JW-01100.02 | 800.00 | 1304-12-17 | 1000-GH-48 | UG PW Pipe Installation | To be provided wrapping report of PW connection | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2022-11-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01100 |  |  | Construction
. | EGAT-RFI-HV-JW-01477.01 | 800.00 | 1304-12-17 | 1000-GH-48 | Pipe Insulation & Jacketing | Execute passages of the installtion throught the walls | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-04-28 | 2023-05-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01478.01 | 800.00 | 1304-12-17 | 1000-GH-48 | Hvac Piping work | Execute passages of the installation throught the walls | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-04-28 | 2023-05-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01529.01 | 800.00 | 1304-12-17 | AUX | 1000-GH-48 | Lack of tags on radiators | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-06-20 |  | Construction | [8 empty] | Construction
. | 04-PMC-HEC-E-0598.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Roof Jaketing (Refer to photo attahced) | Jacketing damaged - dented in the upper part at the entrance to the shaft | C | HV | HEC HV Design | Ms. Daria Pliszka | 2023-02-13 | 2023-04-20 | [5 empty] | V |  |  |  | Construction
. | 28024 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | No one room is finished. No possibility to check an accordance with drawing, specification, etc. The walkdown must be repeated. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28025 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | Floor lining is mostly covered, no possibility to check. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-05-12 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28026 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Electric rooms, control room | In electric rooms works a raised floor is damaged in some areas. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28027 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | All openings must be filled/covered (with proper fireproofing where required). | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28028 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | Expansion joints/gaps between columns or columns and walls must be properly finished. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-06-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28029 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | The walkway and the plinth around the building is not done. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28030 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | The cracks on the facades must be repaired. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28031 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | All facades, doors, windows, floor, ceiling, roof etc. must be cleaned. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 |  | Walkdown | [8 empty] | RFC/RFSU
. | 28032 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | Corners must be properly finished, cracks must be repaired. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28033 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | Door bucks must be properly finished. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28034 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | Missing thresholds, inproper finishing. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28035 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | All suspended ceilings required completion, adjustment and cleaning. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28036 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | Wall cracks must be repaired. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28037 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | Damages caused by other branches works must be fixed. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28038 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | Damages window and doors handles/locks must be removed. Doors must be adjusted. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28039 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Technical rooms | Damages must be repaired, finishing must be improved. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28040 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | Floor lining damaged because of bad doors adjustment must be exchanged. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28041 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | Damaged windows boards must be exchanged. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28042 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Shower rooms | Damaged walls have to be fixed. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28043 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Smoking room | Opening in the wall to fill. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-03-09 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28044 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Facades | Missing canopy. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-04-18 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28045 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Facades | Incorrect finishing of the downspout supports. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28046 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Roof | Damaged flashing must be exchanged. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28047 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Roof | The flashing being access to the roof must be protected by grating or at least anti-slip pad. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28048 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Roof | Instead of gluing such a large number of small patches, one larger sheet of membrane should be glued. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-03-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28049 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Roof | Doghouses flashing shall be improved. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28050 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Roof | The safety rope system lost its functionality because it was covered with HVAC supports. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28051 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Roof | Water pools - the profile or slope of the flashings must be corrected. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28052 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Battery room | Room finishing must be improved. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-25 | 2023-05-12 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28053 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | Lack of SAT inspection | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-06-19 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28054 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | Lack of Final Inspection - HVAC/Plumbng | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28055 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | Lack of Final Inspection - Fire Protection | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28056 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General All installation | Lack of identification and flow direction marking in line with the procedure - installation and equipment | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-05-09 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28057 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | HVAC Room PW | shut-off valve installed before the pressure safety valve x2 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 28058 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | HVAC Room IA | damaged casing of hvac control panel | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-05-22 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 28059 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | HVAC Room PW | the water discharge from the pressure safety valves and the anti-contamination valve is made of a small diameter and should be open | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-02-01 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28060 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General remark / SD | lack of sanitary equipment or is not completed | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-02-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28061 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General All installation | Lack of name stickers on HVAC equipment (local control panel) | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-03-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28062 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General All installation | dirt and damages on Insulation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-05-08 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 28063 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General ventilation | Lack of supports for flex duct | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 28064 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Room 45 / ventilation | air difusser demaged (to be replaced) | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 28065 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Room 35, 42 / electric heater | the door of the shower cubicle hits the electric heater | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 |  | Walkdown | [8 empty] | RFC/RFSU
. | 28066 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Room 40 / PW | to thighten wash basin | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-02-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28067 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | WH not electricity connections | C | EL | HEC EL Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28068 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Room 35 | EH not on the same hight | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-02-01 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 28069 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Room 39 | Lack of intake louver | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-02-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28070 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General | the method of installing shower trays in the showers - unacceptable | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28071 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General / Clean Agent system | Lack of fan door test | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-04-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28072 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Room 08 Clean Agent system | Present documents authorizing the use of the duct used in the Pressure relief damper installation in room no. 08 | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28073 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Elevations / Clean Agent system | Pressure relief damper outside is cover by rain pipe | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-04-04 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28074 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | General RL/RG equipment | Lack of ground wire | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-05-08 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28075 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | Illumination test to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-05-08 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28076 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | Loop impedance test to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-05-30 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28077 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | Earthing continuity and resistance test to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28078 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | All Lighting switches, Socket outlets and Lighting fixtures to be cleaned. | C | EL | HEC HV Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28079 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | Gas Becon & Sounder earthing cable to be connected. | C | CI | HEC CI Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-03-21 | Walkdown |  |  | 2023-03-17 | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28080 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | Cable tray on wall opening area fire sealing to be done where ever it is required. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28081 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | 13/2 room Lighting switch tag number is missing. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28082 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | 1000-CCR21-ELP-008 HVAC frame broken | C | HV | HEC HV Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-02-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28083 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | Socket outlet & switches frame to be remove and Plastering works to be complete by architectular | C | AR | HEC AR Construction | Mr. Adam Siewiorek | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28084 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | 14/1 Hand dryer location to be change beside the shink due to cable is short. | C | HV | HEC HV Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-02-02 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28085 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | 15/1 In toilet urinal sensor to be install and connect the cable. | A | HV | HEC HV Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 28086 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | Cable ladder and tray earth bonding and main earthing cable to be connect for all above ceiling and below Race ways. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-05-04 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28087 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | Conduit pipe earthing to be provided. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-05-16 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28088 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | In corridor one socket outlet plastering works to be complete by architectular. | C | AR | HEC AR Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-05-02 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28089 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | In all rooms below raise floor to be cleaned. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-05-04 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28090 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | In Shift leader room raise floor supports are rusted around 5cm to be verify in all rooms and replace the supports. | C | AR | HEC AR Construction | Mr. Adam Siewiorek | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28091 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | In raise floor cable tray wall opening fire sealing works to be done if required. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-05-05 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28092 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | 21/PDP/004/08/01 Socket outlet to be fix in locker room toilet. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-04-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28093 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | In Handicap toilet (W)-2 room 1 light is mising as per drawing EGAT-HEC-1000-ELE-DLP-05005_rev-Z0, Lighting switch to be installed and official inspection to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28094 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | In women drying room 21-ELP-001/12/05 lighting fixture to be installed. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-04-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28095 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | Women locker room lighting is different from drawing to be verify and official inspection to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-05-18 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28096 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | All of Electrical reminaing inspections according to ITP to be carried out. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28097 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | All out side door earthing to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-03-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28098 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | Monkey ladder earthing to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-04-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28099 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | Canopy lighting fixtures to be installed. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-03-27 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28100 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | 1000-PO-001B Repair panel to be installed and cable termination to be complete and official inspection to be carried out. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-04-21 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28101 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-900-ELE-DLP-01016,EGAT-HEC-1000-ELE-DGA-00003,DLP-04003,05005 | Outdoor lighting to be install on the building and cable termination to be complete. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28102 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-1000-INC-DLP-00211 | TEL/LAN Socket to be installed and cable termination to be completed | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28103 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-1000-INC-DLP-00211,EGAT-HEC-1000-INC-DLP-00311 | Telecommunication SAT to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28104 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-1000-INC-DLP-50211 | Security System to be installed, cable termination to be done and SAT to be complete | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28105 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-1000-INC-DLP-50211 | Security system SAT to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28106 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-1000-ELE-DLP-06003 | Fire alarm device to be install. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 | 2023-04-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 28107 | 800.00 | 1304-12-19 | CCB Building (1000-CCR-21) | EGAT-HEC-1000-ELE-DLP-06003 | Fire alarm device to be installed and sat to be performed. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-25 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 30513 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Furniture / Refer to photo in 04-PDHP-HEC-E-1521 | General comment: missing plugs for the screw holes in the cabinets | C | AR | HEC AR Construction | Ms. Małgorzata Juszczyk | 2023-03-01 |  | RFSU | [8 empty] | RFC/RFSU
. | 30516 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Sink / Refer to photo in 04-PDHP-HEC-E-1521 | General comment: Unconnected sinks to the sewage system and water connection to the tap | C | HV | HEC HV Construction | Ms. Małgorzata Juszczyk | 2023-03-01 | 2023-03-16 | RFSU |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30517 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Wall / Refer to photo in 04-PDHP-HEC-E-1521 | General comment: Many unfinished items in the rooms | C | AR | HEC AR Construction | Ms. Małgorzata Juszczyk | 2023-03-01 |  | RFSU | [8 empty] | RFC/RFSU
. | 30518 | 800.00 | 1304-12-19 | Central Control Building (1000-CCR-21) | Partition wall | Missing partition wall in room no 16 | C | AR | HEC AR Construction | Ms. Małgorzata Juszczyk | 2023-03-01 | 2023-06-23 | RFSU |  |  |  |  | V |  |  |  | RFC/RFSU
. | 30519 | 800.00 | 1304-12-19 |  | - | General comment: Housekeeping to be done | C | AR | HEC AR Construction | Ms. Małgorzata Juszczyk | 2023-03-01 |  | RFSU | [8 empty] | RFC/RFSU
. | 30658 | 800.00 | 1304-12-19 | 1000-CCR-21 | - | Water below the uprised floor room 31 | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-14 | 2023-06-15 | RFSU |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31302 | 800.00 | 1304-12-19 | CCB - Room 36 | EGAT-HEC-1000-ARC-DWG-00002 | Lack of electrical power in all sockets on ground level. Socket NO: 21-PDP-001/12/01 21-PDP-001/12/02 21-PDP-001/12/03 | C | EL | HEC EL Construction | Mr. Kamil Ciesielski | 2023-04-09 | 2023-04-13 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31303 | 800.00 | 1304-12-19 | CCB - Room 10, 8, 16, | EGAT-HEC-1000-ARC-DWG-00001 | Electrical failure in sockets - from time to time, usually during nights | C | EL | HEC EL Construction | Mr. Kamil Ciesielski | 2023-04-09 | 2023-04-13 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31796 | 800.00 | 1304-12-19 | Locker Room | Locker Room | Temperature is much below 24 °C | C | HV | HEC HV Construction | Mr. Aleksander Rożek | 2023-05-07 | 2023-06-01 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31797 | 800.00 | 1304-12-19 | Conrol Room | Conrol Room | humidity below 40% (usual is about 10-30%) | C | HV | HEC HV Construction | Mr. Aleksander Rożek | 2023-05-07 | 2023-06-01 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31985 | 800.00 | 1304-12-19 | CCB 1000-CCR-21 room 15 (toilet) |  | Leaking urinal in toilet nr 15 in CCB | C | AR | HEC AR Construction | Mr. Sławomir Dyrda | 2023-05-19 | 2023-06-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 32496 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL WINDOWS : Room No. 45, 44, 43, 27, 26, 25, 24, 23, 22, 21, 20, 19, 18, 17,10, 08 | windows need to be adjusted / external sill shall be repaired / internal sill shall be repaired (r. 8,10,24,45) / windows touch up painting (r.10.19,20,21,27,45) / Damages window and doors handles/locks must be removed. Doors must be adjusted / Damaged windows boards must be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32497 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL | windows need to be adjusted / external sill shall be repaired / internal sill shall be repaired (r. 8,10,24,45) / windows touch up painting (r.10.19,20,21,27,45) / Damages window and doors handles/locks must be removed. Doors must be adjusted / Damaged windows boards must be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32498 | 800.00 | 1304-12-19 | 1000-CCR-21 | ROOF/Axis A-C/1-13 | Flashing - damaged parts must be replaced, doghouses to improve, water pools profile/slope corrected, the flashing being access to the roof must be protected by grating or at least anti-slip pad / Fix and clean membrane / missing pad HV/EL equipment / statement of repaired roof sheating / The safety rope system lost its functionality because it was covered with HVAC supports | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32499 | 800.00 | 1304-12-19 | 1000-CCR-21 | FACADES | Cracks on the facades must be repaired / incorrect finishing of the downspout supports | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32501 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL - TILE INSTALLATION, ROOM No. 28, 52 | Clean out required proper installation elevation / To clean after fugue finishing / Tiles require cleaning (28,52) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32502 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL - WALLS/ROOM No. 36 | Corners must be properly finished, cracks on corners and walls must be repaired / damaged wall behind door (36) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32503 | 800.00 | 1304-12-19 | 1000-CCR-21 | ROOM NO. 5 | Anchor installation top part / Dirty/scratched walls | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32504 | 800.00 | 1304-12-19 | 1000-CCR-21 | WALLS - ROOM NO. 6 | damaged/scratched walls | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32505 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL - CONTROL ROOM NO. 10 | regulation of raised floor and cleaning under riased floor / regulation and damage fixing of suspended ceiling | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32506 | 800.00 | 1304-12-19 | 1000-CCR-21 | WALLS - ROOM NO. 16 | damaged/scratched walls / missing partition wall | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32507 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL - RACK ROOM NO. 31 | damages of suspended ceiling / regulation of suspended ceiling / regulation of raised floor / cleaning under raised floor / to install push bars and handle | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32508 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL - ENGINEERING ROOM NO. 33 | Raised floor - cleaning (panel, under panels), levelling / To fix installation holes on epoxy paintr | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32509 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL - ROOM NO. 34 | tiles required cleaning / partition wall require cleaning / damage walls need to be fixed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32510 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL - ROOM NO. 37 | tiles need to be replaced - on wall 10 pcs / partition wall require cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32511 | 800.00 | 1304-12-19 | 1000-CCR-21 | TILES - ROOM NO. 38 | tiles need to be replaced - 10 pcs on wall and 4 pcs on floor | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32512 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL - ROOM NO. 41 | tiles required cleaning / partition wall require cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32513 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL - ROOM NO. 42 | tiles required cleaning / partition wall require cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32599 | 800.00 | 1304-12-19 | CCR-21 |  | CCR-21 telecom room (other buildings and rooms where similar solution were issued) lack of automatic switching between units in stand-by mode and duty mode, alarms in DCS not available, unable to control units from HVAC control panel | C | HV | HEC HV Construction | Mr. Karol Pytel | 2023-06-16 |  | PAC | [8 empty] | RFC/RFSU
. | 32639 | 800.00 | 1304-12-19 | 1000-CCR-21 | DOORS - ROOMS 5,7,12,13S,14S,15N,16N,24 | door frame and leaf touch up room | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32640 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL - DOORS | to clean doors | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32641 | 800.00 | 1304-12-19 | 1000-CCR-21 | DOORS - ROOM 33 | scratch on door frame and leaf | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32642 | 800.00 | 1304-12-19 | 1000-CCR-21 | DOORS - ROOM 35 | scratch on door frame and leaf | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32643 | 800.00 | 1304-12-19 | 1000-CCR-21 | DOORS - ROOM 37 | scratch on door frame and leaf | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32644 | 800.00 | 1304-12-19 | 1000-CCR-21 | DOORS - ROOM 39 | scratch on door frame and leaf | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32645 | 800.00 | 1304-12-19 | 1000-CCR-21 | DOORS - ROOM 40 | scratch on door frame and leaf | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32646 | 800.00 | 1304-12-19 | 1000-CCR-21 | DOORS - ROOM 46 | scratch on door frame and leaf | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32647 | 800.00 | 1304-12-19 | 1000-CCR-21 | DOORS - ROOM 48 | scratch on door frame and leaf / damaged active door leaf | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32648 | 800.00 | 1304-12-19 | 1000-CCR-21 | DOORS - ROOMS 31,36,41,42,44,45 | scratch on door frame and leaf | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32649 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL - WINDOWS | windows need to be adjusted (r.8,12,17-27,43)/ windows touch up painting (r.10.19,20,21,27,45) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32650 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL - WINDOWS | external sill shall be repaired (8,10,17-27,43-45) / internal sill shall be repaired (r. 8,10,24,45) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32651 | 800.00 | 1304-12-19 | 1000-CCR-21 | GENERAL - WINDOWS | Damages window and doors handles/locks must be removed. Doors must be adjusted / Damaged windows boards must be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32652 | 800.00 | 1304-12-19 | 1000-CCR-21 | RAISED FLOOR - 11,30,32,48 | Adjustment, cleaning, damaged panels to replace | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | EGAT-RFI-AR-UB-05056.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Control Room No. 10 | Damages of suspended ceiling | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-22 | 2023-06-23 | Construction | 2022-04-22 |  |  |  | V | EGAT-RFI-AR-UB-05056 |  |  | Construction
. | EGAT-RFI-AR-UB-05056.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Control Room No. 10 | Regulation of suspended ceiling | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-22 | 2023-06-23 | Construction | 2022-04-22 |  |  |  | V | EGAT-RFI-AR-UB-05056 |  |  | Construction
. | EGAT-RFI-AR-UB-05059.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Control Room No. 10 | Regulation of raised floor | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-22 | 2023-06-15 | Construction | 2022-04-22 |  |  |  | V | EGAT-RFI-AR-UB-05059 |  |  | Construction
. | EGAT-RFI-AR-UB-05059.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Control Room No. 10 | Skirting has to be installed | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-22 | 2022-11-25 | Construction | 2022-04-22 |  |  |  | V | EGAT-RFI-AR-UB-05059 |  |  | Construction
. | EGAT-RFI-AR-UB-05059.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Control Room No. 10 | Cleaning under raised floor | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-22 | 2023-06-23 | Construction | 2022-04-22 |  |  |  | V | EGAT-RFI-AR-UB-05059 |  |  | Construction
. | EGAT-RFI-AR-UB-05061.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Rack Room No. 31 | Regulation of raised floor | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-22 | 2023-06-23 | Construction | 2022-04-22 |  |  |  | V | EGAT-RFI-AR-UB-05061 |  |  | Construction
. | EGAT-RFI-AR-UB-05061.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Rack Room No. 31 | Skirting has to be installed | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-22 | 2022-11-25 | Construction | 2022-04-22 |  |  |  | V | EGAT-RFI-AR-UB-05061 |  |  | Construction
. | EGAT-RFI-AR-UB-05061.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Rack Room No. 31 | Cleaning under raised floor | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-22 | 2023-06-23 | Construction | 2022-04-22 |  |  |  | V | EGAT-RFI-AR-UB-05061 |  |  | Construction
. | EGAT-RFI-AR-UB-05065.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Rack Room No. 31 | Damages of suspended ceiling | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-22 | 2023-06-23 | Construction | 2022-04-22 |  |  |  | V | EGAT-RFI-AR-UB-05065 |  |  | Construction
. | EGAT-RFI-AR-UB-05065.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Rack Room No. 31 | Regulation of suspended ceiling | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-22 | 2023-06-23 | Construction | 2022-04-22 |  |  |  | V | EGAT-RFI-AR-UB-05065 |  |  | Construction
. | EGAT-RFI-AR-UB-05067.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Battery Room No. 49/ Rack Room No. 31 | Damage of plaster nearby door | A | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-22 | 2022-07-27 | Construction | 2022-04-22 |  |  |  | V | EGAT-RFI-AR-UB-05067 |  |  | Construction
. | EGAT-RFI-AR-UB-05067.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Battery Room No. 49/ Rack Room No. 31 | Finishing of plaster on gypsum wall | A | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-22 | 2022-05-10 | Construction | 2022-04-22 |  |  |  | V | EGAT-RFI-AR-UB-05067 |  |  | Construction
. | EGAT-RFI-AR-UB-05067.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Battery Room No. 49/ Rack Room No. 31 | Spot plastering improvement necessary | A | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-22 | 2022-05-11 | Construction | 2022-04-22 |  |  |  | V | EGAT-RFI-AR-UB-05067 |  |  | Construction
. | EGAT-RFI-AR-UB-05088.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | To fix installation holes on epoxy paint | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05088 |  |  | Construction
. | EGAT-RFI-AR-UB-05088.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | To clean under raised floor | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05088 |  |  | Construction
. | EGAT-RFI-AR-UB-05088.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | To clean raised floor | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05088 |  |  | Construction
. | EGAT-RFI-AR-UB-05088.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | Levelling of raised floor to fix | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-06-23 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05088 |  |  | Construction
. | EGAT-RFI-AR-UB-05088.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | Skirting to do | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05088 |  |  | Construction
. | EGAT-RFI-AR-UB-05089.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | To install panel nearby electrical tray | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-06-15 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05089 |  |  | Construction
. | EGAT-RFI-AR-UB-05089.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | Damaged frame nearby electrical tray | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-06-15 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05089 |  |  | Construction
. | EGAT-RFI-AR-UB-05089.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | Levelling of suspended ceiling to fix | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-06-15 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05089 |  |  | Construction
. | EGAT-RFI-AR-UB-05171.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 6 | Dirty/scratched walls | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05171 |  |  | Construction
. | EGAT-RFI-AR-UB-05171.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 6 | Damaged wall behind door | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05171 |  |  | Construction
. | EGAT-RFI-AR-UB-05171.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 5 | Dirty/scratched walls | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05171 |  |  | Construction
. | EGAT-RFI-AR-UB-05171.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 14 | Acryl finishing | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05171 |  |  | Construction
. | EGAT-RFI-AR-UB-05171.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 15 | Acryl finishing | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05171 |  |  | Construction
. | EGAT-RFI-AR-UB-05171.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 16 | Dirty/scratched walls | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-06-19 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05171 |  |  | Construction
. | EGAT-RFI-AR-UB-05171.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 42 | Corners to paint | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05171 |  |  | Construction
. | EGAT-RFI-AR-UB-05171.08 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 36 | Damaged wall behind door | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05171 |  |  | Construction
. | EGAT-RFI-AR-UB-05171.09 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | Lack of dilatation joints | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-02 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05171 |  |  | Construction
. | EGAT-RFI-AR-UB-05311.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | To fix membrane | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-07-05 | 2023-06-23 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05311 |  |  | Construction
. | EGAT-RFI-AR-UB-05311.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | Missing pad for HV/EL equipment | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-07-05 | 2023-06-23 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05311 |  |  | Construction
. | EGAT-RFI-AR-UB-05424.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | Acryl finishing | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-08-04 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05424 |  |  | Construction
. | EGAT-RFI-AR-UB-05424.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | Dirty/ scratched surface | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-08-04 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05424 |  |  | Construction
. | EGAT-RFI-AR-UB-05605.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | Plinth to be done | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05605 |  |  | Construction
. | EGAT-RFI-AR-UB-05605.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Axis 7-8/A | To clean nearby dilatation | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-06-01 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05605 |  |  | Construction
. | EGAT-RFI-AR-UB-05605.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Axis 8-15 | To correct plastering around windows-deviation | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2022-11-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05605 |  |  | Construction
. | EGAT-RFI-AR-UB-05605.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Axis B-C/1 | To celan | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-06-01 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05605 |  |  | Construction
. | EGAT-RFI-AR-UB-05605.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | Axis B-C/1 | To fix after support | C | EL | HEC EL Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05605 |  |  | Construction
. | EGAT-RFI-AR-UB-05605.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | Axis A/4A-13 | Leak/dirt nearby | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-06-01 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05605 |  |  | Construction
. | EGAT-RFI-AR-UB-05605.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | Axis A/13 | To fix after piping installation | C | ME | HEC ME Construction | Piotr Zygmunt | 2022-10-13 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05605 |  |  | Construction
. | EGAT-RFI-AR-UB-05674.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | axis: A/1-15;A-C/1;C/4A-15 | To do plinth | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05690.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | To remove tape | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-20 | 2022-12-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05690 |  |  | Construction
. | EGAT-RFI-AR-UB-05690.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 1 | To install panel - 2 pcs. | C | EL | HEC EL Construction | Piotr Zygmunt | 2022-10-20 | 2023-04-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05690 |  |  | Construction
. | EGAT-RFI-AR-UB-05690.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 9 | To install panel - 2 pcs. | C | EL | HEC EL Construction | Piotr Zygmunt | 2022-10-20 | 2023-04-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05690 |  |  | Construction
. | EGAT-RFI-AR-UB-05690.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 8 | To install panel - 9 pcs. | C | EL | HEC EL Construction | Piotr Zygmunt | 2022-10-20 | 2023-04-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05690 |  |  | Construction
. | EGAT-RFI-AR-UB-05690.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 8 | To regulate HV equipment | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-10-20 | 2023-01-11 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05690 |  |  | Construction
. | EGAT-RFI-AR-UB-05690.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 16 | To regulate HV equipment | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-10-20 | 2023-01-11 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05690 |  |  | Construction
. | EGAT-RFI-AR-UB-05690.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 6 | To regulate HV equipment | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-10-20 | 2023-01-11 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05690 |  |  | Construction
. | EGAT-RFI-AR-UB-05690.08 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 13 | To regulate HV equipment | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-10-20 | 2023-01-11 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05690 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 50 | To clean profiles | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-24 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 17 | To clean profiles | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-24 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 21 | To clean profiles | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-24 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 23 | To clean profiles | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-24 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 50 | To install panel - 1 pcs. | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 17 | To regulate profile | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 18 | To regulate profile | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.08 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 20 | To regulate profile | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.09 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 21 | To regulate profile | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.10 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 22 | To regulate profile | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.11 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 23 | To regulate profile | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.12 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 24 | To regulate profile | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.13 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 25 | To regulate profile | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.14 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 26 | To regulate profile | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.15 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 27 | To regulate profile | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.16 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 3 | To regulate profile | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.17 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 17 | To install panel - 3 pcs. | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.18 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 17 | To regulate panel | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.19 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 18 | To regulate panel | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.20 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 19 | To regulate panel | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.21 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 20 | To regulate panel | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.22 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 21 | To regulate panel | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2023-02-22 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  | SCAN CAT | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.23 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 22 | To regulate panel | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2023-02-22 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  | SCAN CAT | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.24 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 23 | To regulate panel | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.25 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 24 | To regulate panel | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.26 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 26 | To regulate panel | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.27 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 3 | To regulate panel | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.28 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 18 | To fix wall profile - 3 pcs. | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2023-03-21 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  | SCAN CAT | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.29 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 18 | Levelling | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.30 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 19 | Levelling | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.31 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 19 | HV equipment regulation | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2023-02-22 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  | SCAN CAT | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.32 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 21 | HV equipment regulation | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2023-02-22 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  | SCAN CAT | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.33 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 22 | HV equipment regulation | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2023-02-22 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  | SCAN CAT | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.34 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 25 | HV equipment regulation | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2023-02-22 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  | SCAN CAT | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.35 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 21 | To fix wall profile - 1 pcs. | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2023-02-22 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  | SCAN CAT | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.36 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 23 | To install panel - 2 pcs. | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.37 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 24 | To remove tapes | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.38 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 25 | To remove tapes | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.39 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 26 | To remove tapes | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.40 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 27 | To remove tapes | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.41 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 3 | To remove tapes | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.42 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 24 | To fix wall profile/wall nearby window | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2023-02-22 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  | SCAN CAT | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.43 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 27 | Panel to clean | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.44 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 3 | To reinstall dirty/ damaged panel | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-02 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.45 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 3 | To regulate lamp | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2022-11-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.46 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 3 | To fix wall profile/wall | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2023-03-21 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  | SCAN CAT | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05764.47 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 3 | To install panel | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-02 | 2023-03-21 | Construction |  | 'Punch Category' changed C -> B (2022-11-09) evidence attached |  | SCAN CAT | V | EGAT-RFI-AR-UB-05764 |  |  | Construction
. | EGAT-RFI-AR-UB-05776.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 45 | To clean profiles | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 48 | To clean profiles | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 35 | To clean profiles | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 51 | To clean profiles | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 42 | To clean profiles | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 52 | to clean profiles | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 39 | To clean profiles | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.08 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 28 | To clean profiles | B | AR | HEC CV Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.09 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 29 | To clean profiles | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.10 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 43 | To regulate profile | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.11 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 44 | To regulate profile | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-12-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.12 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 45 | To regulate profile | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.13 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 35 | To regulate profile | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.14 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 42 | To regulate panel | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2023-02-22 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.15 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 47 | To fix profile | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.16 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 35 | To fix profile | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.17 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 51 | To fix profile | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.18 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 48 | Levelling | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.19 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 35 | Levelling | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.20 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 43 | HV equipment regulations | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2023-02-22 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.21 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 46 | HV equipment regulation | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2023-02-22 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.22 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 51 | To fix wall profile 2pcs | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.23 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 28 | To fix wall profile 2 pcs | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2023-03-21 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.24 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 29 | To fix wall profile | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2023-03-21 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.25 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 28 | To install panel 1pc | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2023-02-22 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.26 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 29 | To install panel 4pcs | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2023-03-21 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.27 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 36 | To remove tapes | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.28 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 29 | To remove types | B | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2022-11-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.29 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 47 | To fix profile/wall | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2023-02-22 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05776.30 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 29 | To fix profile/wall | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-07 | 2023-03-21 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 29 | Wall profile to reinstall nearby | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-03-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 43 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 44 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 45 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 46 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 47 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 48 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.08 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 42 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.09 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 52 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.10 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 36 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.11 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 39 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.12 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 35 | Acryl finishing of wall profile | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2021-03-10 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.13 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 51 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.14 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 28 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.15 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 29 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-01-25 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.16 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 29 | To regulate profile - line | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-06-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05777.17 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 29 | Nearby door to fix wall/profile | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-09 | 2023-03-10 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05778.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 17 | Wall profile to clean/reinstall room | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2023-03-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05778.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 25 | Wall profile to clean/reinstall | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2023-03-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05778.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 17 | Panel to regulate | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2023-03-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05778.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 19 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2023-01-13 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05778.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 21 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2023-01-13 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05778.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 22 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2023-01-13 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05778.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 23 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2023-01-13 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05778.08 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 24 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2023-01-13 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05778.09 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 25 | Acryl finihsing wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2023-01-13 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05778.10 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 26 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2023-01-13 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05778.11 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 27 | Acryl finishing of wall profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2023-01-13 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05870.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | Cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 43 | To install screw on lock | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-03-16 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 43 | Door closer to regulate | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-03-16 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 46 | Door closer to regulate | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-03-16 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 47 | Door closer to regulate | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-03-16 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 35 | Door closer to regulate | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-03-16 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 44 | Door closer - to install protection element | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-03-29 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.08 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 44 | Scratch on door leaf | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.09 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 45 | Scratch on door leaf | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.10 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 46 | Scratch on door leaf | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.11 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 48 | Scratch on door leaf | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.12 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 40 | Scratch on door leaf | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.13 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 37 | Scratch on door leaf | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.14 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 35 | Scratch on door leaf | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.15 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 33 | Scratch on door leaf | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.16 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | Door stopper to install | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-03-16 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.17 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 46 | Scratch on door frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.18 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 48 | Scratch on door frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.19 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 42 | Scratch on door frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.20 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 41 | Scratch on door frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.21 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 40 | Scratch on door frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.22 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 39 | Scratch on door frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.23 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 36 | Scratch on door frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.24 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 37 | Scratch on door frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.25 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 35 | Scratch on door frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.26 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 33 | Scratch on door frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.27 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 31 | Scratch on door frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.28 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 48 | Damaged active door leaf | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.29 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 42 | To remove tape from doors | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.30 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 41 | To remove tape from doors | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.31 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 39 | To remove tape from doors | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.32 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 39 | To remove foil | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.33 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 39 | Door leaf to regulate | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.34 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 36 | Lack of gasket | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-03-29 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.35 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 38 | Lack of part of door frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.36 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 35 | To install ventilated louver frame | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-06-15 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.37 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 31 | To install handle | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-06-23 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05870.38 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 31 | To install push bar | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-06 | 2023-06-23 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05870 |  |  | Construction
. | EGAT-RFI-AR-UB-05874.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 16 | Scratch | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-13 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05874 |  |  | Construction
. | EGAT-RFI-AR-UB-05874.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Corridor No. 3 nearby Room No. 16 | Scratch | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-13 | 2023-06-19 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05874 |  |  | Construction
. | EGAT-RFI-AR-UB-05874.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 6 | Damage nearby door | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-13 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05874 |  |  | Construction
. | EGAT-RFI-AR-UB-05886.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | To clean after fugue finishing | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-19 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05886 |  |  | Construction
. | EGAT-RFI-AR-UB-05886.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 2 | Joint finishing of threshold | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-19 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05886 |  |  | Construction
. | EGAT-RFI-AR-UB-05890.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 5 | Anchor installation top part | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-27 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05890.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 5, 14N | Foil to remove | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-27 | 2023-06-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05890.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | To clean doors | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-27 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05890.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 5, 7, 13S, 14S, 15N | Door leaf touch-up | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-27 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05890.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 5, 16N, 7, 12, 15N 24 | Door frame touch-up | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-27 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05890.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | - | To install protection of door closer | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-27 | 2023-03-29 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05890.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 12, 17 | Gasket to install | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-27 | 2023-03-16 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05890.08 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 13S, 16S, 17, 20, 24, 26 | Door closer to regulate | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-27 | 2023-03-16 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05890.09 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | Door stoper to install | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-27 | 2023-03-16 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05890.10 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 14S, 14N | Door closer to install | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-27 | 2022-03-16 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05890.11 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 15S | Door to regulate | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-27 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05890.12 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 18 | Damage | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-27 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05890.13 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room 27 | Lock protection to regulate | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2022-12-27 | 2023-03-16 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05899.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 28 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-23 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05899 |  |  | Construction
. | EGAT-RFI-AR-UB-05899.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 37 | Tile need to be replaced - on wall - 10 pcs | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-23 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05899 |  |  | Construction
. | EGAT-RFI-AR-UB-05899.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 38 | Tile need to be replaced - on wall - 10 pcs | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-23 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05899 |  |  | Construction
. | EGAT-RFI-AR-UB-05899.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 38 | Tile need to be replaced - on floor - 4 pcs | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-23 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05899 |  |  | Construction
. | EGAT-RFI-AR-UB-05899.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 41 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-23 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05899 |  |  | Construction
. | EGAT-RFI-AR-UB-05899.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 42 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-23 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05899 |  |  | Construction
. | EGAT-RFI-AR-UB-05899.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 52 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-23 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05899 |  |  | Construction
. | EGAT-RFI-AR-UB-05899.08 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 34 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-23 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05899 |  |  | Construction
. | EGAT-RFI-AR-UB-05899.09 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | Clean out required proper installation elevation | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-23 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05899 |  |  | Construction
. | EGAT-RFI-AR-UB-05958.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Axis A-C/1-13 | Membrane required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-07 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05958 |  |  | Construction
. | EGAT-RFI-AR-UB-05958.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Axis A-C/1-13 | Rust dust need to be remove from membrane | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-07 | 2023-06-15 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05958 |  |  | Construction
. | EGAT-RFI-AR-UB-05958.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Axis A-C/1-13 | Subconctractor's statement of repairs in roof sheating (membrane) for facility 1000-CCR-21 | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-07 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05958 |  |  | Construction
. | EGAT-RFI-AR-UB-05961.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 43 | Skirting and pcv floor required repairing | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-08 | 2023-03-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05961 |  |  | Construction
. | EGAT-RFI-AR-UB-05961.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 45 | Sealant between floor and skirting shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-08 | 2023-03-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05961 |  |  | Construction
. | EGAT-RFI-AR-UB-05961.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 24 | Skirting ought to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-08 | 2023-03-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05961 |  |  | Construction
. | EGAT-RFI-AR-UB-05992.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 47 | Sealant between floor and skirting shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-03-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05992 |  |  | Construction
. | EGAT-RFI-AR-UB-06046.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 14 | Scratches on mirror to be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-24 | 2023-06-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06051.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | General | No possibility to check quality of glass of outdoor | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-24 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06051.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 45, 27, 21, 20, 19, 10 | Window requisite touch up painting | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-24 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06051.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 45, 24, 10, 08 | Internal window sill shall be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-24 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06051.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 45, 44, 43, 27, 26, 25, 24, 23, 22, 21, 20, 19, 18, 17,10, 08 | External window sill shall be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-24 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06051.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 43, 27, 26, 25, 24, 23, 21, 20, 19, 18, 17, 12, 08 | Window need to be adjusted | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-24 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06052.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 15 | Partition walls require cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-09 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06052.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 34 | Partition walls require cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-09 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06052.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 37 | Partition walls require cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-09 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06052.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 41 | Partition walls require cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-09 | 2023-06-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06052.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 34 | Doors need to be adjusted | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-09 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06083.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 11; 30; 32; 48 | Raised floor adjutment shall be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-24 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06083.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 11; 30; 32; 48 | Floor cleaning is needed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-24 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06083.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Room No. 11; 30; 32; 48 | Damaged panels require replacement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-24 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-CI-CW-01209.01 | 800.00 | 1304-12-19 | 1000-CR-21 | Panel Installation | Additional inspection required after all architectural works | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-28 | 2022-06-22 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01210.01 | 800.00 | 1304-12-19 | 1000-CR-21 | Panel installation | Additional inspection required after all architectural works | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-28 | 2022-06-22 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03928.01 | 800.00 | 1304-12-19 | CCR-21, Laboratory PP Area | 3EA | Name plate devices to be provide | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-31 | 2023-01-10 |  |  |  | 2023-01-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03928.02 | 800.00 | 1304-12-19 | CCR-21, Laboratory PP Area | 3EA | Hand Switch Earthing cable need to be provide | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-31 | 2023-02-07 |  |  |  | 2023-02-06 | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03934.01 | 800.00 | 1304-12-19 | CCR-21, Laboratory & Workshop PP Area |  | Name plate devices to be provide | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-31 | 2022-12-28 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03934.02 | 800.00 | 1304-12-19 | Laboratory PP Area | 1000-TGD-7937 | Name plate devices must be visible | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-31 | 2023-01-10 |  |  |  | 2023-01-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04833.01 | 800.00 | 1304-12-19 | CCR-21 WORKSHOP | 1000-JGD-046, 1000-JGD-047, 1000-JGD-048 | INSTRUMENT JB GROUNDING TO BE PROVIDE | C | EL | HEC EL Construction | Mr. Paweł Rogoziński | 2022-12-12 | 2023-04-03 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-05453.01 | 800.00 | 1304-12-19 | Calibration | Gas Detector 14ea | Alarm and pre alarm are not mentioned in calibration report | C | CI | CW Office | Mr. Paweł Rogoziński | 2023-02-17 | 2023-04-03 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00871.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-DLP-05005_2 | Should be install on tag of Cable tray, normal, emergency & power cable lay-out | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-10-06 | 2023-04-26 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-00871.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-DLP-05005_2 | Emergengency lighting Cable tray provide vendor fittings. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-10-06 | 2023-04-25 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01102.01 | 800.00 | 1304-12-19 | 1000-SS-05 | EGAT-HEC-1000-ELE-SCH-00001 | Cable tag should be clarified from design team about earthing cable & size | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-17 | 2022-02-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01102.02 | 800.00 | 1304-12-19 | 1000-SS-05 | EGAT-HEC-1000-ELE-SCH-00001 | LV & Control cable clamp should be provided for step up cable. (below the panel) | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-17 | 2022-01-05 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01102 |  |  | Construction
. | EGAT-RFI-EL-SB-01106.01 | 800.00 | 1304-12-19 | 1000-SS-05 | EGAT-HEC-1000-ELE-SCH-00001 | Cable tag should be clarified from design team about earthing cable & size | B | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-17 | 2022-02-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01106.02 | 800.00 | 1304-12-19 | 1000-SS-05 | EGAT-HEC-1000-ELE-SCH-00001 | LV & Control cable clamp should be provided for step up cable. (below the panel) | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2021-11-17 | 2022-01-05 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-01106 |  |  | Construction
. | EGAT-RFI-EL-SB-01197.02 | 800.00 | 1304-12-19 | 1000-SS-02 | 02-DP-001 | 16.2 Some non compliance found in EGAT-HEC-000-ELE-CAL-00005_Relay coordination_Rev.2 Attachment-4. MCC setting table. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 | 2022-04-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01197.07 | 800.00 | 1304-12-19 | 1000-SS-02 | 02-DP-001 | 16.3 Interface test with ECMS not complete | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-01-26 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02105.01 | 800.00 | 1304-12-19 | CCR | EGAT-HEC-1000-ELE-DLP-05505_3 | Bolts are to be install to the bottom of the emergency tray every 'T' & 'L' Type of support. | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-04-07 | 2022-05-30 | Construction |  |  |  |  | V | EGAT-RFI-EL-SB-02105 |  |  | Construction
. | EGAT-RFI-EL-SB-02105.02 | 800.00 | 1304-12-19 | CCR | EGAT-HEC-1000-ELE-DLP-05005_3 | Earthing connection should be provide for cable tray. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-04-07 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02404.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-DLP-04003_1 | Between the copper tape & roof sheet bolting properly | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-10 | 2023-05-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02404.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-DLP-04003_1 | Provide black selicon properly | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-10 | 2023-04-11 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02404.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-DLP-04003_1 | The bolts of the lighting arrester should be tightness | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-10 | 2023-04-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02443.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-DLP-05005_4, EGAT-HEC-900-ELE-DLP-03023_1 | Earthing connection should be provided for cable tray | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-05-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02443.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-DLP-05005_4, EGAT-HEC-900-ELE-DLP-03023_1 | Cable tag should be provided for cable tray | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-05-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02501.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-300-ELE-DLP-05006_5 | Cable tray support should be provided 1.5 meters | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-19 | 2023-05-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02501.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-300-ELE-DLP-05006_5 | Earthing connection should be provided for cable tray | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-19 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02501.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-300-ELE-DLP-05006_5 | Cable tag should be provided for cable tray | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-19 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02533.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-DGA-00003_2 | Battery rack & battery junction box provide name tag | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-04-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02534.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-DGA-00003_2 | The battery MCCB box has to be cleaned properly | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-05-02 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02536.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-SCH-00002_1 | Cable needs to be tagged on each cable tray | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02536.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-SCH-00002_1 | Whenever remove the temporary cable and install a permanent cable need to be inspection. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-05-12 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02537.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-SCH-00002_1 | Cable needs to be tagged on each cable tray | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02538.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-SCH-00002_1 | Panel Q24 check the earthing cable lug or nut-bolt should be proper install. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-04-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02538.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-SCH-00002_1 | Panel Q6/Q2 Earthing cable should be connected. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-04-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02538.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-SCH-00002_1 | Whenever remove the temporary cable and install a permanent cable need to be inspected. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-04-25 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02538.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-SCH-00002_1 | LP.21-UPDP-1-1B Cable tag check and replace | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-04-25 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02629.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-DLP-05005_4 | The fittings of all lights in the control room are to be installed in one line. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-06-04 | 2023-05-22 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02629.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-DLP-05005_4 | All lights in the rack room provide to be tagged | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-06-04 | 2023-04-11 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02629.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-DLP-05005_4 | Two fittings have to be installed in the right place in the shift control room | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-06-04 | 2023-05-22 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03210.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-300-ELE-DLP-05005_3 | Tie a flexible conduit from the tray to the lighting fixture | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-07-14 | 2023-05-09 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03313.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-000-INC-DWG-00001_4 | Earthing connection should be provided | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-16 | 2023-04-21 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03313.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-000-INC-DWG-00001_4 | Please provide screw for recorder & power supply rack | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-16 | 2023-05-12 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03313.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-000-INC-DWG-00001_4 | 21-SEC-002 Panel to be cleaned | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-16 | 2023-04-03 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03313.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-000-INC-DWG-00001_4 | 21-SEC-003 & 004 Roof should be changed | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-16 | 2023-04-03 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03314.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-000-INC-DWG-00001_4 | Earthing connection should be provided | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-16 | 2023-04-21 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03314.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-000-INC-DWG-00001_4 | 21-PA-001 & 002 Missing equipment should be provided | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-16 | 2023-04-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03314.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-000-INC-DWG-00001_4 | Change the route of the cable and fix it from the other side | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-16 | 2023-05-12 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03350.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EGAT-HEC-1000-ELE-DGA-00003_2 | Earthing connection should be provided | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-16 | 2023-06-13 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04261.01 | 800.00 | 1304-12-19 | CCR-21 | EGAT-HEC-1000-ELE-DLP-06003_3 | Metal clamp should be installed to the CNBOP cable tray | C | EL |  | Mr. Adam Siewiorek | 2022-09-23 | 2023-04-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04261.02 | 800.00 | 1304-12-19 | CCR-21 | EGAT-HEC-1000-ELE-DLP-06003_3 | A fire barrier should be installed in the wall onboth sides | C | EL |  | Mr. Adam Siewiorek | 2022-09-23 | 2023-05-25 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04261.03 | 800.00 | 1304-12-19 | CCR-21 | EGAT-HEC-1000-ELE-DLP-06003_3 | CNBOP cable tray should be install for fire alarm cable crossing | C | EL |  | Mr. Adam Siewiorek | 2022-09-23 | 2023-05-09 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04261.05 | 800.00 | 1304-12-19 | CCR-21 | EGAT-HEC-1000-ELE-DLP-06003_3 | Abort switch for prottection glass cover should be provided. 1000-AS-9101, 1000-AS-9102 & 1000-AS-9103 | C | EL |  | Mr. Adam Siewiorek | 2022-09-23 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04261.06 | 800.00 | 1304-12-19 | CCR-21 | EGAT-HEC-1000-ELE-DLP-06003_3 | Cable tag should be provided for the both side of the wall | C | EL |  | Mr. Adam Siewiorek | 2022-09-23 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04261.07 | 800.00 | 1304-12-19 | CCR-21 | EGAT-HEC-1000-ELE-DLP-06003_3 | Submit the ipdated vendor documents | C | EL |  | Mr. Adam Siewiorek | 2022-09-23 | 2023-04-20 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06961.01 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | FACP unlocking code is not working properly. (Block-A) | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.02 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Tag numbers missing for FH/FB outdoor. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 | 2023-06-14 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06961.03 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | FH, FB, MAC tg numbers missing in the Battery room. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06961.04 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Tag numbers and logical numbers | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.05 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Problem with reset and sounder buttons | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.06 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Bumpers in all cabinets (1000-CCR-FACP-0001/1R,2R,3R,4R) to be repaired/tightened. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06961.07 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | All faults to be cleared from FACP | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.08 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Cause & Effect matrix to be updated [e.g. there is no access void in air lock 2, sensor 6299 doesn't exist. In dining room (type-1)-2 there are 4 detectors, so ''preceding 3 tags'', ''2003'' are mistakes in matrix table]. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.09 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | GEMOS not operating. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.10 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Loop cable of GH-48 and was not connected. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.11 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Fuse value (7.5A) for batteries to be checked/confirmed.(FACP CPU Batteries) | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.12 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Additional SD(CV) to be installed in Drying Room(W) (52). | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.13 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Additional SD(CV) to be installed in Air lock-2.(1000-SD-6096 hs been installed in corridor instead of Aorlock-2) | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.14 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Remote Indicator for 1000-SD-6096 to be moved from air lock-2 to corridor. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.15 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | HVAC cabinet 1000-CCR21-HCP-0001-FAS not connected. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.16 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Access void sensors locations to be visually signed (e.g. by red dot with tag no). | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.17 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Duct smoke decetors shall have tags or red dots on the ceiling to indicate it's position. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.18 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Reseting problem with zone 3117- reset button not working. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.19 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | ACS not connected/To be tested with FAS | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.20 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | FH sound Level Measurments to be performed. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.21 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Logical tags are missing in the documentation (Fire Alarm Layout). | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.22 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | 1000-HD-6001 installation not be corrected. (Dining room (13) | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 | 2023-06-06 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06961.23 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | 1000-HD-6001 - for HD here T1 and T2 times shell be programmed and concidence with SDs.(Dining room (13) | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.24 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | 1000-SD-6111,6092,6085,6019,6194,6089 - can not reset - disabled by hand - to be cleared | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.25 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | 1000-FH-6002 - can not be disabled from FACP. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.26 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | 1000-SD-6087,6094,6081,6164,6168 gets fault after testing and reseting - to be cleared | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06961.27 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | 1000-SD-6195 and 6196 tag displayed wrong (6195 instead of 6196, 6196 instead of 6195). (Shift leader room) | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06961.28 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | Sticker tags for remote indicators to be changed to correct (corresponding with proper SD numbers): 1000-SD-6185-RI, 1000-SD-6186-RI, 1000-SD-6141-RI, 1000-SD-6142-RI. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06961.29 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | 1000-SD-6082-RI, 6081-RI, 6200-RI remote indicators to be placed under the sensor (or possibly close). | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 | 2023-06-06 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06961.30 | 800.00 | 1304-12-19 | CR-21 Building | EGAT-HEC-1000-ELE-DLP-06003(1~5) | 1000-SD-6178- position of the SD (CV) to be visually signed on the ceiling. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07104.01 | 800.00 | 1304-12-19 | Laboratory, Workshop & Central Control Building. | EGAT-HEC-1000-INC-DLP-50211_Z0B, 50212_Z0B, 50213_Z0B | Provide Discription of the call Bottom for The 21-INT-014 | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-15 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07104.02 | 800.00 | 1304-12-19 | Laboratory, Workshop & Central Control Building. | EGAT-HEC-1000-INC-DLP-50211_Z0B, 50212_Z0B, 50213_Z0B | 21-Cas-016,017 Tag should be provide | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-15 | 2023-06-23 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07104.03 | 800.00 | 1304-12-19 | Laboratory, Workshop & Central Control Building. | EGAT-HEC-1000-INC-DLP-50211_Z0B, 50212_Z0B, 50213_Z0B | 21-CRD-016B Should be fixed. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-15 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07104.04 | 800.00 | 1304-12-19 | Laboratory, Workshop & Central Control Building. | EGAT-HEC-1000-INC-DLP-50211_Z0B, 50212_Z0B, 50213_Z0B | Clean the all Divises of security system in CCR Building. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-15 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07104.05 | 800.00 | 1304-12-19 | Laboratory, Workshop & Central Control Building. | EGAT-HEC-1000-INC-DLP-50211_Z0B, 50212_Z0B, 50213_Z0B | 21-IDS-011A Tag should be provide. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-15 | 2023-06-23 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07104.06 | 800.00 | 1304-12-19 | Laboratory, Workshop & Central Control Building. | EGAT-HEC-1000-INC-DLP-50211_Z0B, 50212_Z0B, 50213_Z0B | 42-CAS-015 Tag should be provide. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-15 | 2023-06-23 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07104.07 | 800.00 | 1304-12-19 | Laboratory, Workshop & Central Control Building. | EGAT-HEC-1000-INC-DLP-50211_Z0B, 50212_Z0B, 50213_Z0B | Missing Plate for 42-EML-0111B Should be provide. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-15 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07104.08 | 800.00 | 1304-12-19 | Laboratory, Workshop & Central Control Building. | EGAT-HEC-1000-INC-DLP-50211_Z0B, 50212_Z0B, 50213_Z0B | Drawing should be upated and all ACS system Devise should be Install in safe jone. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-15 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07104.09 | 800.00 | 1304-12-19 | Laboratory, Workshop & Central Control Building. | EGAT-HEC-1000-INC-DLP-50211_Z0B, 50212_Z0B, 50213_Z0B | 42-EEL-012A should be Installed in side the gate. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-15 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07104.10 | 800.00 | 1304-12-19 | Laboratory, Workshop & Central Control Building. | EGAT-HEC-1000-INC-DLP-50211_Z0B, 50212_Z0B, 50213_Z0B | 42-CRD-011B, 11A and 15B Should be moved to other place. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-15 | 2023-06-23 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07104.11 | 800.00 | 1304-12-19 | Laboratory, Workshop & Central Control Building. | EGAT-HEC-1000-INC-DLP-50211_Z0B, 50212_Z0B, 50213_Z0B | 42-CAS-011 Should be Installed. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-15 | 2023-06-23 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07104.12 | 800.00 | 1304-12-19 | Laboratory, Workshop & Central Control Building. | EGAT-HEC-1000-INC-DLP-50211_Z0B, 50212_Z0B, 50213_Z0B | 41-CRD-011 and should be Fixed. | C | EL | HEC EL Construction | Mr. Michal Cwiklak | 2023-06-15 | 2023-06-23 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-00593.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | UG PW Pipe Installation | To be provided wrapping report of connection PW | A | HV | HEC PI Construction | Mr. Jerzy Wegner | 2022-04-20 | 2022-06-21 | Construction | 2022-04-21 | PI Sungdo to be action |  |  | V | EGAT-RFI-HV-JW-00593 |  |  | Construction
. | EGAT-RFI-HV-JW-00718.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | IG pipe Installation | To be sealed pipe going thru fire rated wall acc. to approval | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-04 | 2023-02-16 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00718 |  |  | Construction
. | EGAT-RFI-HV-JW-00724.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be sealed ducts going thru walls acc. to detal. | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2023-01-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00724 |  |  | Construction
. | EGAT-RFI-HV-JW-00724.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be corrected crooced ductwork - Room 18 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-08-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00724 |  |  | Construction
. | EGAT-RFI-HV-JW-00724.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be corrected ducts laying on ED installation - Corridor/ Air Lock | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-08-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00724 |  |  | Construction
. | EGAT-RFI-HV-JW-00724.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be corrected collision duct with insulation - 13 Room | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-08-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00724 |  |  | Construction
. | EGAT-RFI-HV-JW-00724.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be corrected collision duct with profile of cable tray - 5 Room | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-08-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00724 |  |  | Construction
. | EGAT-RFI-HV-JW-00724.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be leveled duct - 7 Room | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-08-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00724 |  |  | Construction
. | EGAT-RFI-HV-JW-00724.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be assembled flexible ducts indicated during inspection | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-12-14 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00724 |  |  | Construction
. | EGAT-RFI-HV-JW-00724.08 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be installed rubber for uninsulated ducts | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-12-28 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00724 |  |  | Construction
. | EGAT-RFI-HV-JW-00724.09 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be corrected crooked duct - 41/42 Room | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-08-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00724 |  |  | Construction
. | EGAT-RFI-HV-JW-00724.10 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be leveled duct - 32 Room | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-08-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00724 |  |  | Construction
. | EGAT-RFI-HV-JW-00724.11 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be corrected ducts laying on cable tray - 31 Room | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-08-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00724 |  |  | Construction
. | EGAT-RFI-HV-JW-00724.12 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be adjusted ED duct to ceiling tile | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2023-01-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00724 |  |  | Construction
. | EGAT-RFI-HV-JW-00725.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Support Installation | To be adjusted, regulated, leveled supports and theraded rods | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-12-28 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00725 |  |  | Construction
. | EGAT-RFI-HV-JW-00725.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Support Installation | To be added support in a few places indicated during inspection | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-08-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00725 |  |  | Construction
. | EGAT-RFI-HV-JW-00725.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Support Installation | To be moved support from flange connection - 23 Room | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-09-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00725 |  |  | Construction
. | EGAT-RFI-HV-JW-00725.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Support Installation | To be provided calculation of supported ducts with cable tray | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-09-08 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00725 |  |  | Construction
. | EGAT-RFI-HV-JW-00726.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be removed sharp edges and mesh | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2023-02-15 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00726 |  |  | Construction
. | EGAT-RFI-HV-JW-00726.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Installation | To be removed colision duct with cable tray | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-12-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00726 |  |  | Construction
. | EGAT-RFI-HV-JW-00727.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Support Installation | To be added support for EA ducts | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-12-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00727 |  |  | Construction
. | EGAT-RFI-HV-JW-00754.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | RL/RG Pipe Installation | To be sealed pipes going thru partition in fire rated walls acc. to approval | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-08 | 2023-01-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00754 |  |  | Construction
. | EGAT-RFI-HV-JW-00754.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | RL/RG Pipe Installation | To be sealed pipes going thru partition in non fire rated walls acc. to detail | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-08 | 2022-12-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00754 |  |  | Construction
. | EGAT-RFI-HV-JW-00754.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | RL/RG Pipe Installation | To be corrected crooked cable tray - corridor | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-08 | 2022-08-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00754 |  |  | Construction
. | EGAT-RFI-HV-JW-00754.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | RL/RG Pipe Installation | To be adjusted, leveled supports, traeded rods | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-08 | 2022-08-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00754 |  |  | Construction
. | EGAT-RFI-HV-JW-00754.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | RL/RG Pipe Installation | To be removed sharp edges on cable tray | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-08 | 2022-08-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00754 |  |  | Construction
. | EGAT-RFI-HV-JW-00754.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | RL/RG Pipe Installation | To be corrected arrangment of pipes and cables | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-08 | 2022-08-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00754 |  |  | Construction
. | EGAT-RFI-HV-JW-00754.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | RL/RG Pipe Installation | To be provided statement of using nitrogen | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-08 | 2022-07-07 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00754 |  |  | Construction
. | EGAT-RFI-HV-JW-00776.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct accessory Installation | To be installed access doors acc. to PN-EN | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-16 | 2023-03-08 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00778 |  |  | Construction
. | EGAT-RFI-HV-JW-00776.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct accessory Installation | To be installed VD before AHU 001A & 0001B | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-16 | 2022-07-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00778 |  |  | Construction
. | EGAT-RFI-HV-JW-00776.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct accessory Installation | To be installed actuators on dampers | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-16 | 2022-08-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00778 |  |  | Construction
. | EGAT-RFI-HV-JW-00776.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct accessory Installation | To be installed MT and TT sensors | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-16 | 2022-08-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00778 |  |  | Construction
. | EGAT-RFI-HV-JW-00870.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | RL/RG Insulation | To be corrected tapes on installation | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-08-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00870 |  |  | Construction
. | EGAT-RFI-HV-JW-00870.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | RL/RG Insulation | To be sealed opens for RL/RG Installation going thru fire rated walls acc. to approval | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-02-16 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00870 |  |  | Construction
. | EGAT-RFI-HV-JW-00870.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | RL/RG Insulation | To be sealed opens for RL/RG installation acc. To detail | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-01-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00870 |  |  | Construction
. | EGAT-RFI-HV-JW-00872.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | EHG Installation | To be clarifield model nr with vendor document due of inconsistent - all units | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-08-04 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00872 |  |  | Construction
. | EGAT-RFI-HV-JW-00872.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | EHG Installation | To be adjusted and leveled to suspended ceiling - all units | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-08-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00872 |  |  | Construction
. | EGAT-RFI-HV-JW-00872.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | EHG Installation | To be removed colision of lamp with EHG - Room No. 10 | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00872 |  |  | Construction
. | EGAT-RFI-HV-JW-00872.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | EHG Installation | To be protected units from dust, mortar etc. - all units | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-08-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00872 |  |  | Construction
. | EGAT-RFI-HV-JW-00872.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | EHG Installation | To be fixed profile above unit - Room No. 5 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-08-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00872 |  |  | Construction
. | EGAT-RFI-HV-JW-00873.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | SAC Installation | To be installed display on unit 02B | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-03 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00873 |  |  | Construction
. | EGAT-RFI-HV-JW-00873.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | SAC Installation | To be clarified model nr with vendor document due of inconsistent - Room No. 7 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-03 | 2023-01-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00873 |  |  | Construction
. | EGAT-RFI-HV-JW-00873.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | SAC Installation | No access to the control panel sac. 0002A/0002B | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-03 | 2023-05-22 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00873 |  |  | Construction
. | EGAT-RFI-HV-JW-00874.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Fan Installation | To be installed PDS and impulse tubes - all fans | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00874 |  |  | Construction
. | EGAT-RFI-HV-JW-00874.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Fan Installation | To be adjusted fan in axe to ductwork - cylinder Room | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-01-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00874 |  |  | Construction
. | EGAT-RFI-HV-JW-00874.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Fan Installation | To be fixed flexible connection - all fans | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-02-03 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00874 |  |  | Construction
. | EGAT-RFI-HV-JW-01010.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | UG PW Pipe Installation | To be provided wrapping report of connection | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-17 | 2022-09-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01010 |  |  | Construction
. | EGAT-RFI-HV-JW-01010.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | UG PW Pipe Installation | To be provided bolting report of connection | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-17 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01010 |  |  | Construction
. | EGAT-RFI-HV-JW-01050.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | IG Pipe Installation | To be provided as-built dwg including changed location of orange junction boxes | C | EL | HEC EL Construction | Mr. Jerzy Wegner | 2022-09-22 |  | Construction |  | 'Discipline' changed HV -> EL (Shinbo) (2022-09-26) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-01050 |  |  | Construction
. | EGAT-RFI-HV-JW-01050.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | IG Pipe Installation | To be installed missing washers for holding cylinders | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-22 | 2022-09-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01050 |  |  | Construction
. | EGAT-RFI-HV-JW-01050.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | IG Pipe Installation | To be installed the identification and flow direction marking | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-22 | 2023-05-09 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01050 |  |  | Construction
. | EGAT-RFI-HV-JW-01079.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct jacketing installation | To be corrected sealing of joints | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-04 | 2022-10-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01079 |  |  | Construction
. | EGAT-RFI-HV-JW-01132.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | ED Pipe Insulation | To be cleaned insulation on ED installation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-20 | 2023-03-02 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01132 |  |  | Construction
. | EGAT-RFI-HV-JW-01132.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | ED Pipe Insulation | To be removed mechanical damages | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-20 | 2022-12-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01132 |  |  | Construction
. | EGAT-RFI-HV-JW-01132.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | ED Pipe Insulation | To be installed sleeves on installation | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-20 | 2022-12-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01132 |  |  | Construction
. | EGAT-RFI-HV-JW-01132.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | ED Pipe Insulation | To be removed rods of suspended ceiling in colision with ED installation | C | AR | HEC AR Construction | Mr. Jerzy Wegner | 2022-10-20 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01132 |  |  | Construction
. | EGAT-RFI-HV-JW-01161.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Control Panel Installation | To be corrected mechanical touch-up paint damages on HVAC panel | C | HV | HEC HV Construction | Mr. Jaroslaw Lugowski | 2022-11-01 | 2023-06-03 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01161 |  |  | Construction
. | EGAT-RFI-HV-JW-01161.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Control Panel Installation | To be provided documents for HVAC panel | C | HV | HEC HV Construction | Mr. Jaroslaw Lugowski | 2022-11-01 | 2023-01-09 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01161 |  |  | Construction
. | EGAT-RFI-HV-JW-01161.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Control Panel Installation | To be connected earthing cable in HVAC panel | C | EL | HEC EL Construction | Mr. Jaroslaw Lugowski | 2022-11-01 | 2023-04-11 | Construction |  | 'Discipline' changed HV -> EL (2022-11-25) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-01161 |  |  | Construction
. | EGAT-RFI-HV-JW-01162.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Control Work - Cabling | To be sealed installation going thru a partition acc. to detail | C | HV | HEC HV Construction | Mr. Jaroslaw Lugowski | 2022-11-01 | 2023-02-20 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01162 |  |  | Construction
. | EGAT-RFI-HV-JW-01162.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Control Work - Cabling | To be sealed installation going thru a partition acc. to approval | C | HV | HEC HV Construction | Mr. Jaroslaw Lugowski | 2022-11-01 | 2023-05-12 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01162 |  |  | Construction
. | EGAT-RFI-HV-JW-01162.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Control Work - Cabling | To be added tags next to equipment and next to walls - some locations | C | HV | HEC HV Construction | Mr. Jaroslaw Lugowski | 2022-11-01 | 2023-02-20 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01162 |  |  | Construction
. | EGAT-RFI-HV-JW-01162.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Control Work - Cabling | To be extended flexible conduit for cable from remote control to A/C | C | HV | HEC HV Construction | Mr. Jaroslaw Lugowski | 2022-11-01 | 2023-02-07 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01162 |  |  | Construction
. | EGAT-RFI-HV-JW-01162.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Control Work - Cabling | To be assembled stickers on equipment | C | HV | HEC HV Construction | Mr. Jaroslaw Lugowski | 2022-11-01 | 2023-02-20 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01162 |  |  | Construction
. | EGAT-RFI-HV-JW-01163.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Control Work - Cabling | To be corrected assembly of cable glands - small connection to ACCU | C | HV | HEC HV Construction | Mr. Jaroslaw Lugowski | 2022-11-01 | 2023-02-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01163 |  |  | Construction
. | EGAT-RFI-HV-JW-01163.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Control Work - Cabling | To be corrected earthing connection in communication kit in AHU | C | EL | HEC EL Construction | Mr. Jaroslaw Lugowski | 2022-11-01 | 2023-05-08 | Construction |  | 'Discipline' changed HV -> EL (2022-11-25) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-01163 |  |  | Construction
. | EGAT-RFI-HV-JW-01163.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Control Work - Cabling | To be assembled tag plate on equipment | C | HV | HEC HV Construction | Mr. Jaroslaw Lugowski | 2022-11-01 | 2023-03-16 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01163 |  |  | Construction
. | EGAT-RFI-HV-JW-01163.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Control Work - Cabling | To be corrected connection of power cable to ACCU | C | EL | HEC EL Construction | Mr. Jaroslaw Lugowski | 2022-11-01 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01163 |  |  | Construction
. | EGAT-RFI-HV-JW-01194.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Insulation | To be removed mechinal damages on insulation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-07 | 2023-02-23 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01195.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | 1000-CCR-21 | To be installed stickers on VD | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2022-12-27 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01195.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | 1000-CCR-21 | To be installed VD due to lack of access 25 room | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-01-10 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01195.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | 1000-CCR-21 | To be installed support due of lack of regulation of VD 26 room | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-01-10 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01195.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | 1000-CCR-21 | To be sealed MFD according to approval | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-06-26 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01195.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | 1000-CCR-21 | To be installed VD on SA ducts 35 room | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-01-10 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01195.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | 1000-CCR-21 | To be reinstalled rods of suspending ceiling due of collision with duct works | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01195.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | 1000-CCR-21 | To be installedaccess doors according to PN/EN | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-02-23 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01195.08 | 800.00 | 1304-12-19 | 1000-CCR-21 | 1000-CCR-21 | To be sealed duct going thourgh a partition according to detail | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-01-04 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01195.09 | 800.00 | 1304-12-19 | 1000-CCR-21 | 1000-CCR-21 | To be installed VDon duct 10 room | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-01-10 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01195.10 | 800.00 | 1304-12-19 | 1000-CCR-21 | 1000-CCR-21 | To be corrected installation of MFD 33 room | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01213.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | PW Pipe Installation | To be provided as-built drawing | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-23 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01213 |  |  | Construction
. | EGAT-RFI-HV-JW-01213.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | PW Pipe Installation | To be removed traces of corrosion from clamps and valve | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-23 | 2023-02-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01213 |  |  | Construction
. | EGAT-RFI-HV-JW-01213.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | PW Pipe Installation | To be relocated strainer before AHU | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-23 | 2023-03-29 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01213 |  |  | Construction
. | EGAT-RFI-HV-JW-01236.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Vent Pipe Installation | To be provided as-built dwg of vent pipe detail | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-16 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01236 |  |  | Construction
. | EGAT-RFI-HV-JW-01267.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Equipment Installation | To be removed traces of corrosion inside AHU | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01267 |  |  | Construction
. | EGAT-RFI-HV-JW-01267.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Equipment Installation | To be touch up painting of mechanical damages - AHU | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01267 |  |  | Construction
. | EGAT-RFI-HV-JW-01267.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Equipment Installation | To be removed transportation protection from fans - AHU-CFU-0001 | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 | 2023-03-02 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01267 |  |  | Construction
. | EGAT-RFI-HV-JW-01267.04 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Equipment Installation | To be installed gasket in window of AHU panel - AHU-0001B | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 | 2023-02-10 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01267 |  |  | Construction
. | EGAT-RFI-HV-JW-01267.05 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Equipment Installation | To be corrected lamels on condencer of ACCU units | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01267 |  |  | Construction
. | EGAT-RFI-HV-JW-01267.06 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Equipment Installation | To be touch up painting on ACCU units | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01267 |  |  | Construction
. | EGAT-RFI-HV-JW-01267.07 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Equipment Installation | To be removed races of corrosion from fan | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01267 |  |  | Construction
. | EGAT-RFI-HV-JW-01267.08 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Equipment Installation | To be removed transportation protection from fans | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 | 2023-02-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01267 |  |  | Construction
. | EGAT-RFI-HV-JW-01305.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Accessory Installation | To be cleaned actuator of MFD | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-21 | 2023-02-07 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01305 |  |  | Construction
. | EGAT-RFI-HV-JW-01315.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | HVAC Equipment Installation | To be installed ERD in room 52 dry room | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-23 | 2023-01-10 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01315 |  |  | Construction
. | EGAT-RFI-HV-JW-01316.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Fire Fighting Equipment Installation | To be provided validity of fire extinguishers | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-23 | 2023-01-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01316 |  |  | Construction
. | EGAT-RFI-HV-JW-01316.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Fire Fighting Equipment Installation | To be installed fire extinguisher in room 4e | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-23 | 2023-03-02 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01316 |  |  | Construction
. | EGAT-RFI-HV-JW-01316.03 | 800.00 | 1304-12-19 | 1000-CCR-21 | Fire Fighting Equipment Installation | To be fixed pin in hinge of box - 2e corridor | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-23 | 2023-01-03 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01316 |  |  | Construction
. | EGAT-RFI-HV-JW-01323.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Support Installation | To be added support for duct installation | C | HV | HEC HV Construction | Tomasz Ulatowski | 2022-12-30 | 2023-03-30 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01323 |  |  | Construction
. | EGAT-RFI-HV-JW-01324.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Accessory Installation | To be intalled access doors according to PN/EN | B | HV | HEC HV Construction | Tomasz Ulatowski | 2022-12-30 | 2023-01-10 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01324 |  |  | Construction
. | EGAT-RFI-HV-JW-01324.02 | 800.00 | 1304-12-19 | 1000-CCR-21 | Duct Accessory Installation | To be installed stckers on UD | B | HV | HEC HV Construction | Tomasz Ulatowski | 2022-12-30 | 2023-01-02 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01349.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | PW Pipe Insulation | Jacketing should be done | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-05-22 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01349 |  |  | Construction
. | EGAT-RFI-HV-JW-01358.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | PW Pipe Installation | Difficult access to the PW systems - height servis | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-06 | 2023-03-28 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01358 |  |  | Construction
. | EGAT-RFI-HV-JW-01360.01 | 800.00 | 1304-12-19 | 1000-CCR-21 | PW Pipe Installation | Places with damages insulation - repair | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-06 | 2023-03-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01360 |  |  | Construction
. | EGAT-RFI-SS-MK-01371.01 | 800.00 | 1304-12-19 | AUX | 1000-CCR-21 | No support for ladder at ground level | C | SS | HEC SS Construction | Mr. Andrzej Misiek | 2022-06-03 | 2023-05-24 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-SS-MK-01371 |  |  | Construction
. | EGAT-RFI-SS-MK-01371.02 | 800.00 | 1304-12-19 | AUX | 1000-CCR-21 | U-Ditch gratings and handrail in axis 13-14/C excluded from inspection | C | SS | HEC SS Construction | Mr. Andrzej Misiek | 2022-06-03 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-SS-MK-01371 |  |  | Construction
. | EGAT-RFI-SS-MK-01371.03 | 800.00 | 1304-12-19 | AUX | 1000-CCR-21 | Ladder 11/C closing not secure of slipping | A | SS | HEC SS Construction | Mr. Andrzej Misiek | 2022-06-03 | 2022-09-12 | Construction |  |  |  |  | V | EGAT-RFI-SS-MK-01371 |  |  | Construction
. | EGAT-RFI-SS-MK-01371.04 | 800.00 | 1304-12-19 | AUX | 1000-CCR-21 | Rusted grating were found 3-10/C | B | SS | HEC SS Construction | Mr. Andrzej Misiek | 2022-06-03 | 2022-09-12 | Construction |  |  |  |  | V | EGAT-RFI-SS-MK-01371 |  |  | Construction
. | 00-PDHP-HEC-L-2178.01 | 800.00 | 1304-12-20 | 1000-LB-41 / Roof | 1000LB-41-AHU-0001 | Material Inspection and FAT reports to be provided for the parts which replaced due to fire | C | HV | HEC HV Construction | Mr. Karol Pytel | 2023-02-25 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | 00-PDHP-HEC-L-2178.02 | 800.00 | 1304-12-20 | 1000-LB-41 / Roof | 1000LB-41-AHU-0001 | Potential Equipment defects to be fixed | C | HV | HEC HV Construction | Mr. Karol Pytel | 2023-02-25 | 2023-03-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | 26966 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | General | Lack of SAT inspection | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26967 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | General | Lack of Final Inspection - HVAC/Plumbng | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26968 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | General | Lack of Final Inspection - Fire Protection | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26969 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | General / Ventilation system | Ventilation system was tunrned on without SAT inspection | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26970 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | General / All installation | Lack of identification and flow direction marking in line with the procedure - installation and equipment | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-05-09 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26971 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | General / Laboratory equipment/installation (Vendor) | Lack of inspection of connection to laboratory equipment (ventilation, gas etc. - Vendors scope) | C | COMM | HEC COMM | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26972 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 27 / Air condition installation | Damaged chousing of air condition controler | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-02-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26973 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 27 / Vent | Supports for vent are dirty and lack of cups | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-01-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26974 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 27 / ED pipe | Tape of insulation is peel of | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-01-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26975 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | General / Ventilation system | Sharp edges and screw at difusers - at the leg hight | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-01-25 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26976 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | General / SD installation | Connection of SD installation (Vendor scope) to the sinks - material are not chemical proof | C | COMM | HEC COMM | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26977 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | General / Ventilation system | Cleaning of ducts should be provided (inside) | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26978 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | General / Ventilation system | Dirty difusers | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-02-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26979 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 28 / Ventilation system | Exhaust difuser covered by the desk | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-05-30 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26980 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 29, 33 / Ventilation system | Tighten the screw - SAC, CTH | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-01-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26981 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 29, 33 / Ventilation system | Touch-up should be corrected - SAC | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-05-16 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26982 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 29 / Ventilation system | Supply diffusers box - SAC is leaky | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-06-01 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26983 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 29 / Ventilation system | Diffusers should be regulated | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-05-18 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26984 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 30 / Heating system | Heater control covered by fume cupboard | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-02-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26985 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 34 / PW, WWS, WWR installation | Lack of insulation of water heater | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-03-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26986 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 34 / PW, WWS, WWR installation | Lack of inspection of water heater | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-03-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26987 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 34 / PW, WWS, WWR installation | Rust on water heater | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-02-01 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26988 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 34 / PW, WWS, WWR installation | Lack of protection for system (diaphragm vessel or other) | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-02-01 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26989 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Outside / ED installation | Unglued elbow, dirty elbow | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-01-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26990 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 38 / Ventilation system | Rust on Fan. Tighten the screw. | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-05-18 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26991 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 38 / Ventilation system | Type of Fan for clarification - EX | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-02-01 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26992 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Toilets / General | Pissed floors in the toilets and urinals | C | AR | HEC AR Construction | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26993 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Toilets / PW installation | Lack of urinal button | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-01-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26994 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Toilets / Sanitary equipment | Lack of silicone - sanitary equipment - urinals and showers | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-02-01 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26995 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Room 15 / Sanitary equipment | Lack of sink and wasbasin | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-05-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26996 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Bathrooms / Sanitary equipment | Shower heater are not complete | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-01-27 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26997 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Roof / Control cable | Corrected the supports for control cables - sensors | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-02-22 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26998 | 800.00 | 1304-12-20 | Laboratory AUX 4 Building (1000-LB-41) | Roof / Duct Jacketing | Corrected the silicone - there is patrially lack of silicone | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-02-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26999 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Roof / Ventilation system | Dameged louver on duct exhaust after fan (duct louver) | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-05-16 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27000 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Roof / AHU | AHU-0001 - dirty inside; rust; touch up should be provided | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27001 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Roof / AHU | AHU-0001 - traces of most likely burns/overheating are visible on the heater. Noticeable burning smell. | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27002 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Roof / AHU | Lack of AHU-0002 | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27003 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Roof / Ventilation system | Exhaust duct concave | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-04-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27004 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Roof / Ventilation system | Exhaust duct - damaged surface | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-03-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27005 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Roof / Control Cable | Lack of one of cable tray cover | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-02-22 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27006 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Roof / RL/RG | Installation, insulation, leakage test inspection should be repeted - AHU-002 | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27007 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Roof / PW installation | Installation, insulation, leakage test inspection should be repeated - AHU-002 | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27008 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Roof / Instrument Cable | Installation inspection should be repeated - AHU-002 | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27009 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Roof / ED installation | Installation inspection should be repeated - AHU-002 | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27010 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Roof / Air condition installation | Iced ACCU | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2023-01-19 | 2023-03-28 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27011 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | Switch in Toilet to be clarify beside 41-PDP-003/008/01 socket outlet. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-19 | 2023-05-09 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27012 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | Final Inspection of the cable to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27013 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | Sensor for urinals to be provided. | A | HV | HEC HV Construction | Mr. Adam Siewiorek | 2023-01-19 | 2023-01-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 27014 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | Socket outlet, LTG Switches and lighting fixtures to be cleaned | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-19 | 2023-04-04 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27015 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | Loop Impedance protocol to be submitted. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-19 | 2023-05-09 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27016 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | Floor box outlet installation , cable termination to be complete. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-19 | 2023-05-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27017 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | Cable tray on wall opening area fire sealing to be done where ever it is required. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-19 | 2023-04-13 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27018 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | Fire alarm device to be installed and sat to be performed. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27019 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | 41-ELP-001/08/SW02/d switch to be fix properly | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-19 | 2023-04-05 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27020 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | Coiled cables in laboratoryto be termiante to the equipments after installations. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27021 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | In Laboratory Processing room 3 Phase socket outlet- 2nos and 1 phase socket outlet -4pcs,cable terminations to be complete and official inspection to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-19 | 2023-05-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27022 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | Door earthing to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-19 | 2023-03-24 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27023 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | Conduit pipe earthing to be done in HVAC room. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-19 | 2023-04-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27024 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | EGAT-HEC-900-ELE-DLP-01017,EGAT-HEC-1000-ELE-DGA-00003, DLP-04004, DLP-05006 | In electrical room and HVAC room Lighting and PDP panel support metal plate to be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-19 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27025 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | All gas alarm horn (sounder) dual tone | There is discrepancy between site (1 horn: GH/TGH) and EGAT-HEC-300-INC-DWG-00007 (2 horns: GH & TGH).e.g. 1000-GH/TGH-7901 vs 1000-GH-7901 & 1000-TGH-7901 | C | CI | CW Construction | Mr. Mariusz Celmer | 2022-01-19 | 2023-03-27 | Walkdown |  |  | 2023-03-01 | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27026 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Tags on description | There is discrepancy between site and EGAT-HEC-300-INC-DWG-00007 (visual and audible alarm appliance shall be located at 2.3m above the floor): 1000-GB-7910, 1000-GH-7910, 1000-TGB-7910, 1000-TGH-7910, 1000-GB-7912, 1000-GH-7912, 1000-TGB-7912, 1000-TGH-7912, 1000-GB-7913, 1000-GH-7913, 1000-TGB-7913, 1000-TGH-7913, 1000-GB-7916, 1000-GH-7916, 1000-TGB-7916, 1000-TGH-7916 | C | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27027 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | 1000-HS-7902A/T, 1000-HS-7901A/T | Nameplates with pushbuttons description missing. | C | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-01-19 | 2023-03-01 | Walkdown |  |  | 2023-02-28 | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27028 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | 1000-GD-7901, 1000-TGD-7901, 1000-TGD-7910 | Mounting screws shall be tightened. | C | CI | CW Construction | Mr. Mariusz Celmer | 2022-01-19 | 2023-03-27 | Walkdown |  |  | 2023-03-01 | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27029 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Tags on description | Full TAG NO shall be visible on nameplate.: 1000-GH-7905, 1000-TGH-7905, 1000-GB-7905, 1000-TGB-7905, 1000-GH-7915, 1000-TGH-7915, 1000-GB-7915, 1000-TGB-7915 | C | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-01-19 | 2023-03-01 | Walkdown |  |  | 2023-02-28 | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27030 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | 1000-GH-7903, 1000-TGH-7903, 1000-GB-7903, 1000-TGB-7903 | Mounting holes in the wall shall be properly masked. | C | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-01-19 | 2023-03-20 | Walkdown |  |  | 2023-03-18 | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27031 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | 1000-TGD-7920, 1000-TGD-7921, 1000-TGD-7922, 1000-TGD-7938 | Blind plug shall be verified. | C | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-01-19 | 2023-02-21 | Walkdown |  |  | 2023-02-18 | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27032 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | 1000-TGD-7920, 1000-TGD-7925, 1000-TGD-7926, 1000-TGD-7932 | Detector warning status shall be verified. | C | CI | CW Construction | Mr. Mariusz Celmer | 2022-01-19 | 2023-03-24 | Walkdown |  |  | 2023-03-01 | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27033 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Tags on description | Blind plug shall be tightened: 1000-TGD-7923, 1000-TGD-7924, 1000-TGD-7925, 1000-TGD-7926, 1000-TGD-7927, 1000-TGD-7928, 1000-TGD-7930, 1000-TGD-7931, 1000-TGD-7932, 1000-TGD-7933, 1000-TGD-7934, 1000-TGD-7935 | C | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-01-19 | 2023-05-09 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27034 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | 1000-TGD-7926 | Cable gland shall be tightened. | C | CI | CW Construction | Mr. Mariusz Celmer | 2022-01-19 | 2023-03-02 | Walkdown |  |  | 2023-02-28 | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27035 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | All devices | Missing SAT report | C | COMM | HEC COMM | Mr. Mariusz Celmer | 2022-01-19 |  | Walkdown | for Lab. Equipment |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27251 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | The door needs to be adjusted, clean up, finishing and repair (a lot of scratches). General. | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27252 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | Need to be repair the entrance threshold | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27253 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | Touch up painting the walls. Need to be repaired damage on the walls. General. | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27254 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | need to finish, clean up, regular and repair the ceiling. General. | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 | 2023-03-24 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27255 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | Need to finish expansion joints. General. | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27256 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | Need to clean up the floor and remove unnecessary equipment. General. | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27257 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | Need to be improved the corners. General. | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27258 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | Need to be improve joints on the floor. General. | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27259 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | missing finish between floor and wall. General | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 | 2023-03-29 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27260 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | Need to repaint windowsill and full in the space under the windowsill. General | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 | 2023-03-29 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27261 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | need to be improved finishing. General. | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27262 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | need to be clean up and touch up painting window frame. General. | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27263 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | room no. 30 / Refer to photo in 04-PDHP-HEC-E-1393 | the handle is missing | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27264 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | need to be repair and improved external wall finish. | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27265 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | the doors are damaged, need to be repaired or exchange | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27266 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | Refer to photo in 04-PDHP-HEC-E-1393 | Canopy is not finish. | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 | 2023-03-29 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 27267 | 800.00 | 1304-12-20 | Laboratory Building (1000-LB-41) | ROOM NO. 39 / Refer to photo in 04-PDHP-HEC-E-1393 | Need to be improve the surface and finishing floor. | C | AR | HEC AR Construction | Ms. Karolina Drozdek | 2023-01-23 | 2023-03-29 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 31269 | 800.00 | 1304-12-20 | 1000-LB-41 |  | GDS: gas cylinder Level Sensor to be relocated from Room 28 to Room 30 (GC room) | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-04-04 | 2023-06-09 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31270 | 800.00 | 1304-12-20 | 1000-LB-41 |  | Lack of a washbasin in a dining room | C | HV | HEC HV Construction | Ms. Inga Żmuda-Trzebiatowska | 2023-04-04 | 2023-05-30 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31271 | 800.00 | 1304-12-20 | 1000-LB-41 |  | Drain from the sink not connected in the dining room | C | HV | HEC HV Construction | Ms. Inga Żmuda-Trzebiatowska | 2023-04-04 | 2023-05-11 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31523 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Touch-up painting on door (frame, leaf) | C | AR | HEC AR Construction | Mr. Bartosz Skórzewski | 2023-04-28 |  | PAC | [8 empty] | RFC/RFSU
. | 31564 | 800.00 | 1304-12-20 |  |  | Low temperature in 1000-LB-41 (16 deg.C) | C | HV | HEC HV Construction | Ms. Inga Żmuda-Trzebiatowska | 2023-04-28 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31629 | 800.00 | 1304-12-20 | Intake room 31 |  | Shelves in room 31 are made from wrong wood-related material (beaverboard). They have to be metal. | C | COMM | HEC COMM | Mr. Szymon Kugler | 2023-04-28 | 2023-06-09 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31630 | 800.00 | 1304-12-20 | PDH EQ | LE-008 / AAS | No air compressor for AAS | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-06-26 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31631 | 800.00 | 1304-12-20 | PDH EQ | LE-010 / UV VIS | We need cuvettes: 10 mm, 40/50 mm and 10 ml for the determination of orthophosphate, silica and sulphate. The 10 ml cuvettes are provided when performing the analysis according to the instrument manual, while the 10 mm and 40/50 mm cuvettes are required for the analysis according to the standard. No reagents for the determination of silica and sulphates according to Polish methods - HACH methods with reagents are not allowed according to the low regulation. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31632 | 800.00 | 1304-12-20 | PDH EQ | LE-011 / Elemental Analyzer for CHNSO | Mr. Lee was informed that another incoming gas scrubber should be installed in the apparatus. Since the quartz tube turned out to be cracked, the Service Engineer replaced it with a spare one, but then our stock was used up. UOP 864 Sulfur in organic and inorganic materials is not possible to perform on a dedicated channel for sulfur, only on a dedicated one for coal. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31633 | 800.00 | 1304-12-20 | PDH EQ | LE-012 / Combustion Ion Chromatograph | The analyser has not been started, and no MSDS for standards. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31634 | 800.00 | 1304-12-20 | PDH EQ | LE-013 / TS/TN analyzer | Purchased calibration standards not conforming to ASTM D6667 were used. They should be adjusted for the sulfur level present in the samples. Curve 1: 0+5+10 mg/kg; Curve 2: 0+10+50+100 mg/kg; Curve 3: 0+50+100+200 mg/kg. Probably too low pressure in the cylinders with standards prevented proper injection of standards, which are incorrect anyway. No quick connector provided to connect sample cylinder and calibration standard cylinder to GI-250 Gas Injector | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31635 | 800.00 | 1304-12-20 | PDH EQ | LE-013 / TS/TN analyzer | UOP 936 No equipment for gas sample preparation - extraction. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31636 | 800.00 | 1304-12-20 | PDH EQ | LE-014 and 015 / Copper strip corrosion | Lack of copper plates with a certificate confirming the copper alloy composition required by ASTM D1838 and ASTM D130. Lack of instructions for water baths in Polish. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31637 | 800.00 | 1304-12-20 | PDH EQ | LE-016 / Viscosity meter | The wrong capillary size is fitted in the viscometer (0.2 and 0.02), as Solvent Solvesso 150 has a viscosity at 40oC of about 1cSt, and the flow time required by the standard must be in the range (200÷1000) s. 1=0,02-t t=50s | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31638 | 800.00 | 1304-12-20 | PDH EQ | LE-019 / pH | To test the pH of low conductivity waters we need a special pH electrode for pure waters, for example demi water. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-06-07 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31639 | 800.00 | 1304-12-20 | PDH EQ | LE-020 / Conductivity meter | Since the ASTM D1125 standard has been withdrawn without replacement, we initially adopt the PN-EN 27888 standard, but officially submit it after verification. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31640 | 800.00 | 1304-12-20 | PDH EQ | LE021 / Titrators | UOP 212 / H2S in propane / No scrubbing installation - sample preparation for analysis. Several reagents and MSDS are missing. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31641 | 800.00 | 1304-12-20 | PDH EQ | LE-021 / Moisture KF / ASTM E203 / | We did not receive a dosing microsyringe of the appropriate capacity with a long needle. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31642 | 800.00 | 1304-12-20 | PDH EQ | LE-022 / Free CO2 | There are no glass funnels to transfer the solutions to the washers/dispenser and no suitable spoons/spatulas needed to measure dry reagents. The sample was dosed with a standard disposable syringe available in stock - the standard requires the sample to be dosed with a calibrated syringe - none. Two lamps and fuses included in NANO15 are missing. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31643 | 800.00 | 1304-12-20 | PDH EQ | LE-023 / TOC Analyzer | Short expiry date of the organic carbon standard; No reagent p.a. to organic carbon | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31644 | 800.00 | 1304-12-20 | PDH EQ | LE-025 / PN-EN 25663 Nitrogen according to Kjeldahl | Due to the failure to provide safety data sheets for some reagents (e.g. catalytic mixture, boric acid mixture with indicators) and the Polish version of the apparatus manual, we were forced to limit ourselves to the role of observers. Please complete the appropriate reagents with the MSDS. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31645 | 800.00 | 1304-12-20 | PDH EQ | LE-031 / BOD | The training was carried out according to the Hach Standard Method instrument manual and not according to ISO 5815-1, the BODTrak II instrument itself can be used to determine BOD5 using the respirometric method (APHA 5210D) and not the electrochemical method which is our target method | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31646 | 800.00 | 1304-12-20 | PDH EQ | LE-034 / Dew point meter | No stable connection of the sample to the analyser. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31647 | 800.00 | 1304-12-20 | PDH EQ | LE-042 / Analytical balance Sartorius MCE 225S-i | I reported that the weight readings on the scales were very unstable when weighing the evaporation vessels. Reducing the air blowing in the weighing room only helped partially. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31648 | 800.00 | 1304-12-20 | PDH EQ | LE-044 / Hydrogen generator | Problem with hydrogen pressure drops in the GDS when operating more than 8-9 FID detectors. The generator is insufficient when all FID detectors are operating at once. Insufficient connection of the hydrogen generator to the GDS - it is necessary to replace the pipe with a steel one. Lack of polish manual. Lack of buffer tank (8l). | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31649 | 800.00 | 1304-12-20 | PDH EQ | Water destilator | Issue with electrical cable | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31650 | 800.00 | 1304-12-20 | PDH EQ | LE-048 | Demi water not working | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-12 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31651 | 800.00 | 1304-12-20 | PDH EQ | LE-051 / ICP MS | The instrument has not been activated | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31652 | 800.00 | 1304-12-20 | PDH EQ | LE-053 / Total Mercury Analyzer | Defective countertop socket - reported to Mr Lee. One package of Mercury collector tube N-160 (5 pcs/pack) and one package of Mercury collector tube (N-100) (5 pcs/pack) are missing. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31653 | 800.00 | 1304-12-20 | PDH EQ | Ion meter | No reagents for S2- (standard) | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-06-21 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31654 | 800.00 | 1304-12-20 | PDH EQ |  | Please provide overdue manuals, MSDS sheets and analytical certificates for reagents and standards - without these documents in Polish we cannot perform analyses, we can only be observers, therefore no acceptance of the equipment will be made | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31655 | 800.00 | 1304-12-20 | PDH EQ |  | When can we expect another training visit of Service Engineers: Metrohm for titrators, Agilent to GC , Nittiseiko for mercury analyzer | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31656 | 800.00 | 1304-12-20 | PDH EQ |  | Gas cylinders without training | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31657 | 800.00 | 1304-12-20 | PDH EQ |  | No equipment to pressurize the gas cylinder by adding high purity nitrogen to the UOP936 method among others. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31658 | 800.00 | 1304-12-20 | PDH EQ |  | No sample dispensing station for GC and other instruments with direct gas sample dispensing. For gaseous samples, it is important to maintain a constant pressure during dosing, so a pressure gauge and a flowmeter are necessary - when analyzing gaseous samples, it was impossible to maintain a constant gas flow. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31659 | 800.00 | 1304-12-20 | PDH EQ |  | GC/Sample dispensing connections and quick disconnects must be made of stainless steel. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-06-09 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31660 | 800.00 | 1304-12-20 | PDH EQ |  | All equipment for dispensing samples from the Sulfinert cylinder required by the standard must also be of Sulfinert design (tubes, pressure gauge, quick connects). | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-06-09 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31661 | 800.00 | 1304-12-20 | PDH EQ |  | No sample dispensing station for GC and other instruments with direct gas sample dispensing. For gaseous samples, it is important to maintain a constant pressure during dosing, so a pressure gauge and a flowmeter are necessary - when analyzing gaseous samples, it was impossible to maintain a constant gas flow. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31662 | 800.00 | 1304-12-20 | PP EQ |  | PPG 5 1. not provided required pressure regulator and stainless steel tubing to connect from one side quick connect sample cylindera and from the other to ventillation 2. Lack of dry nitrogen cylinder used as reference gas | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31663 | 800.00 | 1304-12-20 | PP EQ |  | PPG 6 1. not provided required pressure regulators and stainless steel tubing according schematic included in method 2. Lack of dry nitrogen cylinder used as reference gas | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31664 | 800.00 | 1304-12-20 | PP EQ |  | PPG 202 1. scale 25 kg capacity not available 2. extruder not connected to water and power supply 3. breaker plates and screen assembly compliance with the method requirements has not been verified 4. date of vendor arrival not given | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31665 | 800.00 | 1304-12-20 | PP EQ |  | PPG 203 1. scale 25 kg capacity not available 2. extruder not connected to water and power supply 3. breaker plates and screen assembly compliance with the method requirements has not been verified 4. date of vendor arrival not given | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31666 | 800.00 | 1304-12-20 | PP EQ |  | PPG 300 1. Lack of plastic bags 25x30 cm 2. Lack of stranding equipment /water bath with guide rollers and pelletizer 3. list of reqiured additives has not been verified | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31667 | 800.00 | 1304-12-20 | PP EQ |  | ASTM D5227 PPG 400 - not started. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31668 | 800.00 | 1304-12-20 | PP EQ |  | PPG 401 1. Lack of boiling stones | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31669 | 800.00 | 1304-12-20 | PP EQ |  | PPG 403 - not started. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31670 | 800.00 | 1304-12-20 | PP EQ |  | PPG 408 1. smal amount of aluminium foil and mylar film 2. method not implememnted - vendor arrival date not confirmed 3. calibration standard for Na not provided 4. water cooler platens in the press not connected to the chiller | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-06-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31671 | 800.00 | 1304-12-20 | PP EQ |  | PPG-410 1. required certified reference material to check correctness of measurement 2. Lack of high melt flow die plugs 3. Lack of anti-static bags for resin stabilizing 4. No possibiity to connect to LIMS 5. Not provided tungsen carbide orifices | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31672 | 800.00 | 1304-12-20 | PP EQ |  | PPG 415 1. set for analysis not completed and not placed under the fume hood | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-06-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31673 | 800.00 | 1304-12-20 | PP EQ |  | PPG 404/417/430 1. Lack of specimen molds 150x150mm with specimen cavity 75x75mm thickness 0.25mm and 20 mil, 10 mil, 5 mil, 3 mil. 2. No chillers available to cool water cooled platens PM-010 3. Lack of aluminium backing plates 25x25 cm thickness 3 mm lightly sand-blasted on one side - 2 pieces 4. Lack of brushed aluminium foil chemically clean 0,1 mm thickness and 30 cm wide 5. Lack of vessel large enough to contain the backing plates | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31674 | 800.00 | 1304-12-20 |  |  | PPG 501 1. script for calculations results according the method not provided 2. no possibility to connect to LIMS - another script needed 3. discrepancies between OCS specification in MR and NANO documentation and delivered equipment | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31675 | 800.00 | 1304-12-20 | PP EQ |  | PPG 504 1. Lack of Sample Holder: frame 100 x 100 mm opening | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-06-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31676 | 800.00 | 1304-12-20 | PP EQ |  | PPG 701 1. instrument not connected to instrument air and power supply 2. Lack of frame chase 50mm x 50 mm x 3 mm 3. lack of aluminium can with lid 4. service arrival date not given | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31677 | 800.00 | 1304-12-20 | PP EQ |  | PPG 703 1. inappropriate grips mounted - specimen slides out of the grips. Should be mounted steel rough surface grips. 2. the software in Polish is not yet available | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-06-26 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31678 | 800.00 | 1304-12-20 | PP EQ |  | PPG 707 - no device in the laboratory - expected delivery date June | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-06-26 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31679 | 800.00 | 1304-12-20 | PP EQ |  | PPG 709 1. injection mold for preaparing sample should be provided - it should be diameter 68 mm and thickness 3 mm 2. no training provided | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31680 | 800.00 | 1304-12-20 | PP EQ |  | PPG 711 1. no specimen cutter 2. no appropriate liquide to bath (for example poly(ethylene glycol), glycerin, silicon oil 3. thermometer not avaliable 4. no timer avaliable 5. unsuitable power plug in the bath | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31681 | 800.00 | 1304-12-20 | PP EQ |  | PPG 712 1. Film strip cutter is not provided - no possibility to prepare good quality samples | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31682 | 800.00 | 1304-12-20 | PP EQ |  | PPG 713 1. no proper injection mold fo preparing samples - it should be diameter 68 mm and thickness 3 mm 2. training not provided | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31683 | 800.00 | 1304-12-20 | PP EQ |  | PPG 720 - injection molding machine not running, incompatible nozzle and mold - no training possible - service will return in May | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-12 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31684 | 800.00 | 1304-12-20 | PP EQ |  | PPG 801 1. lack of a suitable polyethylene funnel with a volume of 1 liter 2. not available folded filter paper 3. lack of heavy walled filtering flasks with neoprene adapter 28x16 mm 4. Lack of 200 ml glass pipete, class A 5. required filter absorbing oil mounted on vacuum pump - without a filter there is a risk of hot oil splashing and fumes escaping 6. Confirm used cross section of new cable. It shall be connected directly to motor terminal box, without splicing of cable. This method is unaceptable from electrical point of view. 7. flow meter on vacuum pump nitrogen supply line required | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-17 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31685 | 800.00 | 1304-12-20 | PP EQ |  | PPG 802 1. lack of 200 ml pipete 2. vacuum oven not equipped in second valve for introducing air bleed 3. lack of flow meter at the inputs gases to the vacuum oven 4. Willey mill not strated yet - not connected to power supply and not settled on the table - can not prepare sample 5. no glass beads 6. drying tube not avaliable 7. there is only one vacuum oven avaliable and during the analysis is performed it is not possible to determine of PPG 801 (XS solubles) which is required in schedule every 4 hours - second oven should be provided | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-06-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31686 | 800.00 | 1304-12-20 | PP EQ |  | PPG 803 / PPG 806 / PPG 807 / PPG 808 1. instrument is not connected to the nitrogen and power supply 2. flow meters are reqiured for nitrorgen and oxygen supply 3. oxygen line is not provided to instrument 4. date of service arrival is not announced 5. Gas switching apparatus with flow control (operating at flow rate of 50 ce/min (nitrogen and oxygen)) 6. Indium mentioned in NANO 6 pos. 147 not delivered | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31687 | 800.00 | 1304-12-20 | PP EQ |  | PPG 806- not started | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31688 | 800.00 | 1304-12-20 | PP EQ |  | PPG 807- not started | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31689 | 800.00 | 1304-12-20 | PP EQ |  | PPG 808- not started | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-19 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31690 | 800.00 | 1304-12-20 | PP EQ |  | PPG 809 1. instrument is not connected to compressed air and power suplly 2. date of service arrival is not announced | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31691 | 800.00 | 1304-12-20 | PP EQ |  | PPG 901 chillers not avaliable, no training provided | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-30 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31692 | 800.00 | 1304-12-20 | PP EQ |  | PPG 902 - no agreed reagent, substitute used for training purposes no possibility to prepare the sample - the injection molding machine is not started | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-17 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31693 | 800.00 | 1304-12-20 | PP EQ |  | PPG 903 1. no training | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-30 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31694 | 800.00 | 1304-12-20 | PP EQ |  | PPG 904 - not started. Injection molding machine not running, incompatible nozzle and mold - no training possible - service will return in May | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 | 2023-05-12 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31695 | 800.00 | 1304-12-20 |  | LE-001 Refinery Gas Analyzer | Licence expire (only 6 month license) | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-18 | 2023-06-21 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31696 | 800.00 | 1304-12-20 |  | LE-002 GC with Methanator and FID | UOP899 1. method not implemented by Agilent Engineer 2. training not provided 3. we need a standard with all the components required by the method | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-18 |  | PAC | [8 empty] | RFC/RFSU
. | 31697 | 800.00 | 1304-12-20 |  | LE-003 GC for Boiling range distribution | ASTM D2887 1. solvent CS2 is not available 2. training - only partially 3. method implemented by Agilent Engineer - partially 4. software activation is required (30 days license) | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-18 |  | PAC | [8 empty] | RFC/RFSU
. | 31698 | 800.00 | 1304-12-20 |  | LE-004 GC with FID & Cryogenic cooling | UOP899 1. method implemented by Agilent Engineer - partially 2. we need a standard with all the components required by the method | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-18 |  | PAC | [8 empty] | RFC/RFSU
. | 31699 | 800.00 | 1304-12-20 |  | LE-005 GC for determination of Oxygenates | UOP 960 and UOP 980 1. calibration methods created but peak identification issue 2. we need single standards for each component separately (for both methods) 3. training not provided | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-18 |  | PAC | [8 empty] | RFC/RFSU
. | 31700 | 800.00 | 1304-12-20 |  | LE-006 GC with FID | UOP899 1. method not implemented by Agilent Engineer 2. training not provided 3. we need a standard with all the components required by the method UOP 373 & ASTM D2163 1. standards not delivered 2. method not implemented by Agilent Engineer 3. training not provided | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-18 |  | PAC | [8 empty] | RFC/RFSU
. | 31701 | 800.00 | 1304-12-20 |  | LE-027 GC & Extraction Apparatus | ASTM D2504 1. method implemented by Agilent Engineer - partially 2. training not provided 3. in the current configuration there is no possibility for determination of hydrogen at 5 ppm level (transferred to LE-001) - We need a standard with a low concentration (5 ppm hydrogen) to check this | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-18 |  | PAC | [8 empty] | RFC/RFSU
. | 31702 | 800.00 | 1304-12-20 |  | LE-052 GC/MS with PC and On-board Vaporizer Wasson ECE-Agilent 8890/5977 Custom | Wrong tubing used for connecting the pressure regulator on the gas tank and GC-MS: with accordance to the UOP 1023 the tubing and accessories contacting with LPG e.g. (quick connectors, pressure regulator) must be made from sulfinert-treated stainless steel, not standard steel. Missing UOP 1022 calibration standard, containing arsine and phosphine at the 10 ppm level in helium (the calibration of the GC-MS for arsine and phosphine could not be performed; the sampling port of GC-MS analyzer was not ready: the port ought to be equipped with appropriate quick connector, compatible with the fitting mounted on the sample cylinder, sample cylinder was not provided during the trainig, no Polish manual for the GC-MS | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-18 |  | PAC | [8 empty] | RFC/RFSU
. | 31703 | 800.00 | 1304-12-20 |  | PO-019 Gas Chromatograph Capillary column Continuation | PPG 423 1. different size column instaled 2.service engineer does not implement calculations according method | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31704 | 800.00 | 1304-12-20 |  | PO-020 Gas Chromatograph Capillary column Continuation | PPG 424 and 432 1. used unsiutable solvent i calibration solutions. Need to be change to compatibile with method 2. delivered 5 concentration levels while the method PPG432 mentions 7 3. Lack of thermometer and barometer to record room conditions 4. Lack of decapper to 20 mm vials | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31705 | 800.00 | 1304-12-20 |  | PO-021-2(A) Gas Chromatograph Capillary column Continuation | PPG 429 and PPG 427 1. training not provided | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31706 | 800.00 | 1304-12-20 |  | PO-021-2(B) Gas Chromatograph Capillary column Continuation | PPG428 1. standards not delivered 2. method not implemented by Agilent Engineer 3. training not provided ISO 9377-2 1. method implemented by Agilent Engineer - partially 2. issue with lifted baseline at the site of tetracontan. Unable to complete the analysis 2. training not provided | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-04 |  | PAC | [8 empty] | RFC/RFSU
. | 31861 | 800.00 | 1304-12-20 | 1000-LB-42 |  | Some floor tiles in Laboratory Building need to be replaced | C | AR | HEC AR Construction | Ms. Inga Żmuda-Trzebiatowska | 2023-05-11 |  | PAC | [8 empty] | RFC/RFSU
. | 31926 | 800.00 | 1304-12-20 | PP EQ | PO-025 HDT-300 Vicat | 1. No possibility to connect to LIMS 2. the installed nitrogen valve must be removed and the cover must be installed | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-15 | 2023-06-26 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31927 | 800.00 | 1304-12-20 | PP EQ |  | No direct connections of devices to LIMS - according to the agreed list | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-16 |  | PAC | [8 empty] | RFC/RFSU
. | 31928 | 800.00 | 1304-12-20 | PP EQ |  | Nitrogen and air valves mounted under the ceiling. No intermediate closure available within reach. In the event of a leak in the system, it is impossible to react quickly and shut off the gas. | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-16 | 2023-06-01 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31929 | 800.00 | 1304-12-20 | PP EQ | LE-046 | Glassware washing machineve unsuitable power plug - instruments not connected to the power supply and sets are not complete | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-16 |  | PAC | [8 empty] | RFC/RFSU
. | 31930 | 800.00 | 1304-12-20 | PP EQ | PM-010 Hydraulic Press PM-012 Injection Molder PO-040 | no water filter installed on the cooling water supply - poor water quality causes the deposition of impurities and limescale and leads to a decrease in cooling efficiency and, as a consequence, may lead to equipment damage | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-16 |  | PAC | [8 empty] | RFC/RFSU
. | 31931 | 800.00 | 1304-12-20 | PP EQ | PM-015 Light Box Viewing System | PPG 503 1. no timer is avaliable | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-15 | 2023-05-23 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31932 | 800.00 | 1304-12-20 | PP EQ | PM-012 Injection Molder | ISO molds to injection moulder do not provided | C | COMM | HEC COMM | Ms. Inga Żmuda-Trzebiatowska | 2023-05-15 |  | PAC | [8 empty] | RFC/RFSU
. | 31979 | 800.00 | 1304-12-20 | AUX 4 | 1000-LB-41 | Room 33 air conditioner (constant temperature and humidity unit) diffuser is damaged and need to be painted | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-05-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32464 | 800.00 | 1304-12-20 | 1000-LB-41 | General / Axis A-D/1-9 | membrane - cleaning and removing rust dust / Subcontractor's statement of repairs in roof sheating (membrane) / fix membrane, missing pad for HV/EL equipment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32465 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 13 | fix instalation of tiles / silicone finishing | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32466 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 19 | fouge and tiles required cleaning or improvement | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32467 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 20 | fouge and tiles required cleaning or replacing / joints in the walls shall be sealed / touch up painting on walls | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32468 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 21 | fouge and tiles required cleaning or replacing / sealant around tiles needs improvement | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32469 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 22 | fouge and tiles required cleaning or replacing / touch up painting on walls | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32470 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 23 | fouge and tiles required cleaning or replacing / tile around valve need to be replaced/ cover angel shall be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32471 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 24 | fouge and tiles required cleaning or replacing | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32472 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 25 | fouge and tiles required cleaning or replacing / cracks on gypsum board shall be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32473 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 26 | fouge and tiles required cleaning or replacing / sealant around tiles needs improvement / touch up painting on walls | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32474 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 27 | fouge and tiles required cleaning or replacing | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32475 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 28 | fouge and tiles required cleaning or replacing | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32476 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 29 | cracks on gypsum board shall be repaired / fouge and tiles required cleaning or replacing / touch up painting on walls | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32477 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 30 | cracks on gypsum board shall be repaired / fouge and tiles required cleaning or replacing / touch up painting on walls | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32478 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 31 | fouge and tiles required cleaning or replacing / touch up painting on walls / floor require cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32479 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 32 | fouge and tiles required cleaning or replacing | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32480 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 33 | fouge and tiles required cleaning or replacing / touch up painting on walls | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32481 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 34 | fouge and tiles required cleaning or replacing / sealant around tiles needs improvement / joints in wall shall be sealed / touch up painting on walls / floor require cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32482 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 37 | fouge and tiles required cleaning or replacing / sealant around tiles needs improvement / touch up painting on walls / cracks on gypsum board shall be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32483 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 40 | tiles and fouges - cleaning and replacing / touch up painting / sealant to be done / cracks on walls | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32598 | 800.00 | 1304-12-20 | laboratory building |  | too high temperature in room no 32 X-Ray | C | HV | HEC HV Construction | Ms. Inga Żmuda-Trzebiatowska | 2023-06-16 |  | PAC | [8 empty] | RFC/RFSU
. | 32653 | 800.00 | 1304-12-20 | 1000-LB-41 | DOORS - GENERAL | Doors shall be cleaned, adjust, touch up painted, repaired or exchanged if required / install missing handles | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32654 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 19 | door required cleaning, touch up and adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32655 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 20 | door required cleaning, touch up and adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32656 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 21 | door required cleaning, touch up and adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32657 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 22 | door required cleaning, touch up and adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32658 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 23 | door required cleaning, touch up and adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32659 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 24 | door required cleaning, touch up and adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32660 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 25 | door required cleaning, touch up and adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32661 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 26 | door required cleaning, touch up and adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32662 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 27 | door required cleaning, touch up and adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32663 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 28 | door required cleaning and touch up | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32664 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 29 | door required cleaning and touch up | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32665 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 31 | door required cleaning, touch up and adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32666 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 32 | door required cleaning, touch up and adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32667 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 33 | door required cleaning, touch up and adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 | [10 empty] | RFC/RFSU
. | 32668 | 800.00 | 1304-12-20 | 1000-LB-41 | DOOR - ROOM 34 | door required cleaning, touch up and adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32669 | 800.00 | 1304-12-20 | 1000-LB-41 | GENERAL - WINDOWS | Windows require adjustment, cleaning, touch up painting and windows fittings to be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32670 | 800.00 | 1304-12-20 | 1000-LB-41 | WINDOWS - ROOM 19 | Windows require touch up and sills need to be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32671 | 800.00 | 1304-12-20 | 1000-LB-41 | WINDOWS - ROOM 20 | Windows require adjustment, cleaning, touch up painting and windows fittings to be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32672 | 800.00 | 1304-12-20 | 1000-LB-41 | WINDOWS - ROOM 22 | Windows require adjustment, cleaning, touch up painting and windows fittings to be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32673 | 800.00 | 1304-12-20 | 1000-LB-41 | WINDOWS - ROOM 23 | Windows require adjustment, cleaning, touch up painting and windows fittings to be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32674 | 800.00 | 1304-12-20 | 1000-LB-41 | WINDOWS - ROOM 25 | Windows require adjustment, cleaning, touch up painting and windows fittings to be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32675 | 800.00 | 1304-12-20 | 1000-LB-41 | WINDOWS - ROOM 27 | Windows require adjustment, cleaning, touch up painting and windows fittings to be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32676 | 800.00 | 1304-12-20 | 1000-LB-41 | WINDOWS - ROOM 28 | Windows require cleaning and touch up painting | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32677 | 800.00 | 1304-12-20 | 1000-LB-41 | WINDOWS - ROOM 32 | Windows require cleaning and touch up painting | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32678 | 800.00 | 1304-12-20 | 1000-LB-41 | WINDOWS - ROOM 33 | Windows require cleaning and touch up painting | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32679 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 31 | pull of test need to be submitted / the resistance test of the floor should be performed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32680 | 800.00 | 1304-12-20 | 1000-LB-41 | Room no. 34 | pull of test need to be submitted / the resistance test of the floor should be performed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | EGAT-RFI-AR-UB-01661.01 | 800.00 | 1304-12-20 | 1000-LB-41 | - | To be attach Survey report | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2021-03-22 | 2021-04-14 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-01661.01 | C-AR-UB-00054 |  | Construction
. | EGAT-RFI-AR-UB-01681.01 | 800.00 | 1304-12-20 | 1000-LB-41 | - | To be attach Survey report | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2021-03-08 | 2021-04-14 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-01681.01 | C-AR-UB-00057 |  | Construction
. | EGAT-RFI-AR-UB-01720.01 | 800.00 | 1304-12-20 | 1000-LB-41 | - | To be attach Survey report | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2021-03-08 | 2021-04-14 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-01720.01 | C-AR-UB-00059 |  | Construction
. | EGAT-RFI-AR-UB-01845.01 | 800.00 | 1304-12-20 | 1000-LB-41 | - | To be attach Survey report | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2021-03-08 | 2021-04-14 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-01845.01 | C-AR-UB-00065 |  | Construction
. | EGAT-RFI-AR-UB-05309.01 | 800.00 | 1304-12-20 | 1000-LB-41 | General | To fix membrane | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-07-05 | 2023-06-23 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05309 |  |  | Construction
. | EGAT-RFI-AR-UB-05309.02 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Missing pad for HV/EL equipment | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-07-05 | 2023-06-23 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05309 |  |  | Construction
. | EGAT-RFI-AR-UB-05348.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 38, 39 | Surface finishing | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-07-26 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05348 |  |  | Construction
. | EGAT-RFI-AR-UB-05348.02 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Ceiling cleaning of plywood | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-07-26 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05348 |  |  | Construction
. | EGAT-RFI-AR-UB-05348.03 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Installation holes in ceiling | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-07-26 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05348 |  |  | Construction
. | EGAT-RFI-AR-UB-05481.01 | 800.00 | 1304-12-20 | 1000-LB-41 | - | Wet surface | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-01 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05481 |  |  | Construction
. | EGAT-RFI-AR-UB-05481.02 | 800.00 | 1304-12-20 | 1000-LB-41 | - | Lack of flashing on top side of plastering | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-01 | 2023-06-01 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05481 |  |  | Construction
. | EGAT-RFI-AR-UB-05481.03 | 800.00 | 1304-12-20 | 1000-LB-41 | - | Crack around joint | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-01 | 2023-06-01 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05481 |  |  | Construction
. | EGAT-RFI-AR-UB-05481.04 | 800.00 | 1304-12-20 | 1000-LB-41 | - | Damage of plastering | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-01 | 2023-06-01 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05481 |  |  | Construction
. | EGAT-RFI-AR-UB-05532.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Dilatation (axis 4/C) | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2022-10-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05532 |  |  | Construction
. | EGAT-RFI-AR-UB-05532.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Touch-up painting (axis 6) | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2022-10-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05532 |  |  | Construction
. | EGAT-RFI-AR-UB-05532.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Acryl to paint | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2022-10-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05532 |  |  | Construction
. | EGAT-RFI-AR-UB-05532.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Acryl to paint | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05532 |  |  | Construction
. | EGAT-RFI-AR-UB-05532.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Corner to paint | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2022-10-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05532 |  |  | Construction
. | EGAT-RFI-AR-UB-05532.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Acryl to paint | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2022-10-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05532 |  |  | Construction
. | EGAT-RFI-AR-UB-05532.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Touch-up painting (axis D) | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2022-10-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05532 |  |  | Construction
. | EGAT-RFI-AR-UB-05532.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Touch-up painting around windows | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2022-10-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05532 |  |  | Construction
. | EGAT-RFI-AR-UB-05532.09 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Touch-up painting around nearby door | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05532 |  |  | Construction
. | EGAT-RFI-AR-UB-05532.10 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Acryl finishing around door | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2022-10-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05532 |  |  | Construction
. | EGAT-RFI-AR-UB-05532.11 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Touch-up painting (axis 9) | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05532 |  |  | Construction
. | EGAT-RFI-AR-UB-05532.12 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Acryl to paint | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2022-10-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05532 |  |  | Construction
. | EGAT-RFI-AR-UB-05534.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 38 | To fix after support installation | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05534 |  |  | Construction
. | EGAT-RFI-AR-UB-05534.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 38 | Touch-up painting/ fixing of concrete surface | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05534 |  |  | Construction
. | EGAT-RFI-AR-UB-05534.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 39 | To fix after support installation | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05534 |  |  | Construction
. | EGAT-RFI-AR-UB-05534.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 39 | Touch-up painting/ fixing of concrete surface | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05534 |  |  | Construction
. | EGAT-RFI-AR-UB-05558.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | Cleaning of profiles | C | AR | HEC AR Construction | Paweł Zygmunt | 2022-09-23 | 2022-10-13 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05558 |  |  | Construction
. | EGAT-RFI-AR-UB-05558.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | Removing of damaged profiles | C | AR | HEC AR Construction | Paweł Zygmunt | 2022-09-23 | 2022-10-13 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05558 |  |  | Construction
. | EGAT-RFI-AR-UB-05559.01 | 800.00 | 1304-12-20 | 1000-LB-41 | General | To remove tape/ clean profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-08 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05559 |  |  | Construction
. | EGAT-RFI-AR-UB-05561.01 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Cleaning of doors, windows, sills | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-04 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05561 |  |  | Construction
. | EGAT-RFI-AR-UB-05561.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Axis 8-9 | Finishing around doors | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-04 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05561 |  |  | Construction
. | EGAT-RFI-AR-UB-05561.03 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Plinth to be done | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-04 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05561 |  |  | Construction
. | EGAT-RFI-AR-UB-05561.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Axis D1 | Dilatation joint to fix | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-04 | 2022-12-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05561 |  |  | Construction
. | EGAT-RFI-AR-UB-05561.05 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Sills to finish | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-04 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05561 |  |  | Construction
. | EGAT-RFI-AR-UB-05563.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | To regulate elevation of suspended ceiling | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-27 | 2022-10-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05563 |  |  | Construction
. | EGAT-RFI-AR-UB-05563.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | To regulate elevation of suspended ceiling | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-27 | 2022-10-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05563 |  |  | Construction
. | EGAT-RFI-AR-UB-05563.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 26 | To regulate elevation of suspended ceiling | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-27 | 2022-10-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05563 |  |  | Construction
. | EGAT-RFI-AR-UB-05563.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 26 | To clean profiles | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-27 | 2022-10-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05563 |  |  | Construction
. | EGAT-RFI-AR-UB-05563.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | To regulate around AC | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-27 | 2022-10-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05563 |  |  | Construction
. | EGAT-RFI-AR-UB-05563.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Finishing of opening for pipes | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-27 | 2022-10-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05563 |  |  | Construction
. | EGAT-RFI-AR-UB-05563.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 37 | To regulate profiles | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-27 | 2022-10-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05563 |  |  | Construction
. | EGAT-RFI-AR-UB-05563.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 37 | To clean panels | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-27 | 2022-10-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05563 |  |  | Construction
. | EGAT-RFI-AR-UB-05563.09 | 800.00 | 1304-12-20 | 1000-LB-41 | General | To remove tape/ clean profiles | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-27 | 2022-10-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05563 |  |  | Construction
. | EGAT-RFI-AR-UB-05564.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-28 | 2022-10-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05564 |  |  | Construction
. | EGAT-RFI-AR-UB-05564.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 33 | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-28 | 2022-10-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05564 |  |  | Construction
. | EGAT-RFI-AR-UB-05564.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-28 | 2022-10-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05564 |  |  | Construction
. | EGAT-RFI-AR-UB-05564.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 | Finishing around opening | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-28 | 2022-10-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05564 |  |  | Construction
. | EGAT-RFI-AR-UB-05567.01 | 800.00 | 1304-12-20 | 1000-LB-41 | - | To clean profiles | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-08 | 2022-11-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05567 |  |  | Construction
. | EGAT-RFI-AR-UB-05567.02 | 800.00 | 1304-12-20 | 1000-LB-41 | - | Finishing of openings for HV/EL | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-08 | 2023-03-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05567 |  |  | Construction
. | EGAT-RFI-AR-UB-05568.01 | 800.00 | 1304-12-20 | 1000-LB-41 | - | Touch-up painting | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-08 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05568 |  |  | Construction
. | EGAT-RFI-AR-UB-05568.02 | 800.00 | 1304-12-20 | 1000-LB-41 | - | To fix crack | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-08 | 2022-12-22 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05568 |  |  | Construction
. | EGAT-RFI-AR-UB-05568.03 | 800.00 | 1304-12-20 | 1000-LB-41 | - | To clean doors/ windows | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-08 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05568 |  |  | Construction
. | EGAT-RFI-AR-UB-05568.04 | 800.00 | 1304-12-20 | 1000-LB-41 | - | Fire cable to clean | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-08 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05568 |  |  | Construction
. | EGAT-RFI-AR-UB-05568.05 | 800.00 | 1304-12-20 | 1000-LB-41 | - | Tiles to clean | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-08 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05568 |  |  | Construction
. | EGAT-RFI-AR-UB-05568.06 | 800.00 | 1304-12-20 | 1000-LB-41 | - | To paint acryl | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-08 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05568 |  |  | Construction
. | EGAT-RFI-AR-UB-05601.01 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Acryl finishing | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-06 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05601 |  |  | Construction
. | EGAT-RFI-AR-UB-05601.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 | Crack in corner | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-06 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05601 |  |  | Construction
. | EGAT-RFI-AR-UB-05601.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 | Technical opening to finish | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-06 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05601 |  |  | Construction
. | EGAT-RFI-AR-UB-05601.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 33 | To fix corner | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-06 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05601 |  |  | Construction
. | EGAT-RFI-AR-UB-05601.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | To paint wall | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-06 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05601 |  |  | Construction
. | EGAT-RFI-AR-UB-05602.01 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Tapes to remove | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-09-30 | 2022-10-11 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05602 |  |  | Construction
. | EGAT-RFI-AR-UB-05602.02 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Finishing of pipe's openings | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-09-30 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05602 |  |  | Construction
. | EGAT-RFI-AR-UB-05602.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | To regulate profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-09-30 | 2022-10-11 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05602 |  |  | Construction
. | EGAT-RFI-AR-UB-05602.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 26 | To regulate profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-09-30 | 2022-10-11 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05602 |  |  | Construction
. | EGAT-RFI-AR-UB-05602.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 40 | To regulate profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-09-30 | 2022-10-11 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05602 |  |  | Construction
. | EGAT-RFI-AR-UB-05602.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 37 | To clean/replace panel - 2 pcs. | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-09-30 | 2022-10-11 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05602 |  |  | Construction
. | EGAT-RFI-AR-UB-05602.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 37 | Finishing of openings - HV/EL | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-09-30 | 2023-03-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05602 |  |  | Construction
. | EGAT-RFI-AR-UB-05603.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 Axis 5 | To paint wall | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2022-12-22 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05603 |  |  | Construction
. | EGAT-RFI-AR-UB-05603.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | To clean cable | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05603 |  |  | Construction
. | EGAT-RFI-AR-UB-05603.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Finishing of electrical box | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2022-11-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05603 |  |  | Construction
. | EGAT-RFI-AR-UB-05603.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 Axis 4A | To paint wall | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05603 |  |  | Construction
. | EGAT-RFI-AR-UB-05603.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 Axis 1B | To paint wall | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05603 |  |  | Construction
. | EGAT-RFI-AR-UB-05603.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | To paint/clean all room | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05603 |  |  | Construction
. | EGAT-RFI-AR-UB-05603.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 Axis 5A | To paint wall | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05603 |  |  | Construction
. | EGAT-RFI-AR-UB-05603.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 Axis 6 | To paint wall | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05603 |  |  | Construction
. | EGAT-RFI-AR-UB-05603.09 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 Axis 1B | To paint wall | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05603 |  |  | Construction
. | EGAT-RFI-AR-UB-05603.10 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | To paint/clean all room | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2022-11-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05603 |  |  | Construction
. | EGAT-RFI-AR-UB-05604.01 | 800.00 | 1304-12-20 | 1000-LB-41 | General | To remove tape/clean profile | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05604 |  |  | Construction
. | EGAT-RFI-AR-UB-05604.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 3 | HV equipment to regulate | B | HV | HEC HV Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05604 |  |  | Construction
. | EGAT-RFI-AR-UB-05604.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 4 | HV equipment to regulate | B | HV | HEC HV Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05604 |  |  | Construction
. | EGAT-RFI-AR-UB-05604.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 4 | To install 5 panels | B | HV | HEC HV Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05604 |  |  | Construction
. | EGAT-RFI-AR-UB-05604.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 5 | HV equipment to regulate | B | HV | HEC HV Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05604 |  |  | Construction
. | EGAT-RFI-AR-UB-05604.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 14 | HV equipment to regulate | B | HV | HEC HV Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05604 |  |  | Construction
. | EGAT-RFI-AR-UB-05604.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 15 | HV equipment to regulate | B | HV | HEC HV Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05604 |  |  | Construction
. | EGAT-RFI-AR-UB-05604.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 15 | To install 1 panels | C | EL | HEC EL Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2023-04-21 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05604 |  |  | Construction
. | EGAT-RFI-AR-UB-05604.09 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Finishing of technical electrical opening | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-13 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05604 |  |  | Construction
. | EGAT-RFI-AR-UB-05604.10 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 18 | To install 3 panels | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-13 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05604 |  |  | Construction
. | EGAT-RFI-AR-UB-05618.01 | 800.00 | 1304-12-20 | 1000-LB-41 | General | To clean windows/glass | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05618 |  |  | Construction
. | EGAT-RFI-AR-UB-05618.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 "8-9" | Handle to change | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05618 |  |  | Construction
. | EGAT-RFI-AR-UB-05618.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 "8-9" | Scratch on frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05618 |  |  | Construction
. | EGAT-RFI-AR-UB-05618.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 Axis 1B-C | Handle to change | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05618 |  |  | Construction
. | EGAT-RFI-AR-UB-05618.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 | Gasket to fix | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05618 |  |  | Construction
. | EGAT-RFI-AR-UB-05618.06 | 800.00 | 1304-12-20 | 1000-LB-41 | General | External side of windows covered | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05618 |  |  | Construction
. | EGAT-RFI-AR-UB-05618.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05618 |  |  | Construction
. | EGAT-RFI-AR-UB-05618.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 | Handle to change | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05618 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | To regulate door rkz (self closing system) | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Scratch of active door leaf - bottom | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 | To regulate door rkz (self closing system) | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 | Touch-up painting on passive door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 | Touch-up painting on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 29/30 | Touch-up painting on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.09 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | Touch-up painting on active/passive door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.10 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | Touch-up painting on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.11 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | Doors and accesories to regulate | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.12 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24/22 | Touch-up painting on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.13 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24/22 | Touch-up painting on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.14 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24/25 | Touch-up painting on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.15 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24/25 | Touch-up painting on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.16 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24/25 | Door to regulate | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.17 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | Touch-up painting on passive door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.18 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21/19 | Touch-up painting on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.19 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19/20 | Touch-up painting on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.20 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19/20 | Touch-up painting on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.21 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28/29 | Touch-up painting on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.22 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28/29 | Touch-up painting on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.23 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Touch-up painting on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.24 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Touch-up painting on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.25 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | To fix panic bar | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.26 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27/23 | Touch-up painting on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.27 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27E | Touch-up painting on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.28 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27E | Touch-up painting on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-04-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.29 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27E | Lack of threshold | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2023-05-12 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05619.30 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27E | To fix RKZ | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05619 |  |  | Construction
. | EGAT-RFI-AR-UB-05641.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Tile to reinstall | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-16 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05641 |  |  | Construction
. | EGAT-RFI-AR-UB-05641.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Tile to reinstall | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-16 | 2022-12-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05641 |  |  | Construction
. | EGAT-RFI-AR-UB-05670.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 34 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-18 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 34 | Scratch of passive door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-12 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 33 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-18 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 32 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-18 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 32/33 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-18 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 31 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-18 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 29 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-18 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 20/22 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-18 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.09 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 22/25 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-18 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.10 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 23/25 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-18 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.11 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 33 | Touch-up painting on passive door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-12 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.12 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 32 | Touch-up painting on passive door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-12 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.13 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 31 | Touch-up painting on passive door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-12 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.14 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 26 | Touch-up painting on passive door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-12 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.15 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 33 | Touch-up painting on active door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-12 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.16 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 32 | Touch-up painting on active door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-12 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.17 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 32/33 | Touch-up painting on active door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-12 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.18 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 31 | Touch-up painting on active door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-12 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.19 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 26 | Touch-up painting on active door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-04-12 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.20 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 29 | To fix RKZ | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2022-12-07 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05670.21 | 800.00 | 1304-12-20 | 1000-LB-41 | Door No. 23/25 | To regulate lock/door-closer | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-19 | 2023-05-12 | Construction |  |  |  |  | V |  | EGAT-RFI-AR-UB-05670 |  | Construction
. | EGAT-RFI-AR-UB-05673.01 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Plinth to be done | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-16 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05673 |  |  | Construction
. | EGAT-RFI-AR-UB-05685.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 17 | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-12-22 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05685 |  |  | Construction
. | EGAT-RFI-AR-UB-05685.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 2 | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-12-22 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05685 |  |  | Construction
. | EGAT-RFI-AR-UB-05685.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 2 | Acryl | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-12-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05685 |  |  | Construction
. | EGAT-RFI-AR-UB-05685.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 3 | Acryl | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-12-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05685 |  |  | Construction
. | EGAT-RFI-AR-UB-05685.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 3 | Finishing around window | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05685 |  |  | Construction
. | EGAT-RFI-AR-UB-05685.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 4 | Finishing around window | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05685 |  |  | Construction
. | EGAT-RFI-AR-UB-05685.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 4 | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05685 |  |  | Construction
. | EGAT-RFI-AR-UB-05685.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 5 | Acryl | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-12-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05685 |  |  | Construction
. | EGAT-RFI-AR-UB-05685.09 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 5 | Finishing around window | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05685 |  |  | Construction
. | EGAT-RFI-AR-UB-05685.10 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 5 | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05685 |  |  | Construction
. | EGAT-RFI-AR-UB-05687.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 13 | To fix installation of tiles | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-21 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05687 |  |  | Construction
. | EGAT-RFI-AR-UB-05687.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 13 | Silicone finishing | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-21 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05687 |  |  | Construction
. | EGAT-RFI-AR-UB-05687.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 7 | Electrical cable | C | EL | HEC EL Construction | Mr. Maciej Rudnicki | 2022-10-21 | 2023-04-11 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05687 |  |  | Construction
. | EGAT-RFI-AR-UB-05687.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 10 | Silicone finishing | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-21 | 2022-12-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05687 |  |  | Construction
. | EGAT-RFI-AR-UB-05687.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 10 | Fugue finishing | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-21 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05687 |  |  | Construction
. | EGAT-RFI-AR-UB-05687.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 12 | HV opening/ pipe | B | HV | HEC HV Construction | Mr. Maciej Rudnicki | 2022-10-21 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05687 |  |  | Construction
. | EGAT-RFI-AR-UB-05687.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 12 | Silicone/ tiles finishing | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-21 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05687 |  |  | Construction
. | EGAT-RFI-AR-UB-05687.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 2 | Skirting to fix | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-21 | 2022-12-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05687 |  |  | Construction
. | EGAT-RFI-AR-UB-05687.09 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 2 | Silicone to fix | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-21 | 2022-12-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05687 |  |  | Construction
. | EGAT-RFI-AR-UB-05687.10 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 17 | Silicone to fix | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-21 | 2022-12-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05687 |  |  | Construction
. | EGAT-RFI-AR-UB-05687.11 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 17 | Cleaning | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-21 | 2022-11-03 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05687 |  |  | Construction
. | EGAT-RFI-AR-UB-05752.01 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Plinth to be done | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-16 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05752 |  |  | Construction
. | EGAT-RFI-AR-UB-05760.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room 25 | Crack | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2022-12-22 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05760.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room 29 | Crack | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2022-12-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05760.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room 32 | Crack | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2022-12-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05760.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room 11 | Crack | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2022-12-22 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05760.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room 6 | Crack | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2022-12-22 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05760.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room 14 | Crack | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2022-12-22 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05760.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room 20 | Damage | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2022-12-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05760.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room 12 | Damage | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-07 | 2022-12-22 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-05788.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19, Axis C/4, Axis D/5 | To fix fugue | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-24 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05788 |  |  | Construction
. | EGAT-RFI-AR-UB-05788.02 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Covers for plugs/ finishing of cables | C | EL | HEC EL Construction | Mr. Maciej Rudnicki | 2022-11-24 | 2023-04-11 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05788 |  |  | Construction
. | EGAT-RFI-AR-UB-05788.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | To fix tiles around plug - 1 pcs. | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-24 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05788 |  |  | Construction
. | EGAT-RFI-AR-UB-05788.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | To fix tile - 1 pcs. | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-24 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05788 |  |  | Construction
. | EGAT-RFI-AR-UB-05788.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | To finish fugue | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-24 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05788 |  |  | Construction
. | EGAT-RFI-AR-UB-05788.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20, Axis A/4 | To fix tiles - 6 pcs. | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-24 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05788 |  |  | Construction
. | EGAT-RFI-AR-UB-05788.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | To fix silicone nearby door | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-11-24 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05788 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Walls required touch up painting | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Tiles and fouges desired cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Suspended ceiling should be aligned | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 | 2023-03-07 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Perimeter suspended ceiling profiles to be improved | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 | 2023-03-07 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Panels from suspended ceiling shall be replaced | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 | 2023-03-07 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Suspended ceiling profiles to be improved | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 | 2023-03-07 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Windows sills required cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 |  | Construction |  | Changed from Cat. B |  |  |  | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Doors desired cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 |  | Construction |  | Changed from Cat. B |  |  |  | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.09 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Doors required touch up | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 |  | Construction |  | Changed from Cat. B |  |  |  | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.10 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Doors needed aligned | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 |  | Construction |  | Changed from Cat. B |  |  |  | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.11 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Windows required touch up | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 |  | Construction |  | Changed from Cat. B |  |  |  | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.12 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Sealant between wall and suspended ceiling shall be done | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.13 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Tiles to be improved | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.14 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Clean out desired cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05951.15 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 19 | Sealant on walls shall be improved | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-03 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05951 |  |  | Construction
. | EGAT-RFI-AR-UB-05957.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Axis A-D/1-9 | Membrane required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-08 | 2023-06-23 | [5 empty] | V | EGAT-RFI-AR-UB-05957 |  |  | Construction
. | EGAT-RFI-AR-UB-05957.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Axis A-D/1-9 | Rust dust need to be remove from membrane | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-08 | 2023-06-23 | [5 empty] | V | EGAT-RFI-AR-UB-05957 |  |  | Construction
. | EGAT-RFI-AR-UB-05957.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Axis A-D/1-9 | Subcontractor's statement of repairs in roof sheating (membrane) for facility 1000-LB-41 | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-08 | 2023-06-23 |  |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05957 |  |  | Construction
. | EGAT-RFI-AR-UB-05968.01 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Doors required touch up painting | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-17 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05968 |  |  | Construction
. | EGAT-RFI-AR-UB-05968.02 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Windows required touch up painting | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-17 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05968 |  |  | Construction
. | EGAT-RFI-AR-UB-05968.03 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Doors shall be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-17 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05968 |  |  | Construction
. | EGAT-RFI-AR-UB-05968.04 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Windows shall be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-17 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05968 |  |  | Construction
. | EGAT-RFI-AR-UB-05968.05 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Doors need to be adjustement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-17 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05968 |  |  | Construction
. | EGAT-RFI-AR-UB-05968.06 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Windows need to be adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-17 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05968 |  |  | Construction
. | EGAT-RFI-AR-UB-05968.07 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Doors require door stopper | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-17 | 2023-03-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05968 |  |  | Construction
. | EGAT-RFI-AR-UB-05968.08 | 800.00 | 1304-12-20 | 1000-LB-41 | General | Windows fittings shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-17 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05968 |  |  | Construction
. | EGAT-RFI-AR-UB-05969.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Tile around valve need to be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-10 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05969 |  |  | Construction
. | EGAT-RFI-AR-UB-05969.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Cover angel shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-10 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05969 |  |  | Construction
. | EGAT-RFI-AR-UB-05969.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Tile and fouge requisite cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-10 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05969 |  |  | Construction
. | EGAT-RFI-AR-UB-05970.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 37 | Touch up painting | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-08 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05970 |  |  | Construction
. | EGAT-RFI-AR-UB-05970.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 40 | Touch up painting | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-08 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05970 |  |  | Construction
. | EGAT-RFI-AR-UB-05970.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 37/40 | Cracks on the walls | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-08 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05970 |  |  | Construction
. | EGAT-RFI-AR-UB-05979.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 37 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-14 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05979 |  |  | Construction
. | EGAT-RFI-AR-UB-05979.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 37 | Fouge to be replaced for walls and floor | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-14 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05979 |  |  | Construction
. | EGAT-RFI-AR-UB-05979.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 37 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-14 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05979 |  |  | Construction
. | EGAT-RFI-AR-UB-05979.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 37 | Sealant to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-14 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05979 |  |  | Construction
. | EGAT-RFI-AR-UB-05979.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 40 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-14 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05979 |  |  | Construction
. | EGAT-RFI-AR-UB-05979.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 40 | Fouge to be replaced for walls and floor | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-14 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05979 |  |  | Construction
. | EGAT-RFI-AR-UB-05979.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 40 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-14 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05979 |  |  | Construction
. | EGAT-RFI-AR-UB-05979.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 40 | Sealant to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-14 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05979 |  |  | Construction
. | EGAT-RFI-AR-UB-05980.01 | 800.00 | 1304-12-20 | 1000-LB-41 | - | Tiles installation isn't good quality | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-24 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05980 |  |  | Construction
. | EGAT-RFI-AR-UB-05981.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 | Fouge and tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05981 |  |  | Construction
. | EGAT-RFI-AR-UB-05981.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 | Painted walls requisite touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 | 2023-04-24 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05981 |  |  | Construction
. | EGAT-RFI-AR-UB-05981.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05981 |  |  | Construction
. | EGAT-RFI-AR-UB-05981.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 | Suspended ceiling need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 | 2023-03-07 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05981 |  |  | Construction
. | EGAT-RFI-AR-UB-05981.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 | Doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 |  | Construction |  | Changed from Cat. B |  |  |  | EGAT-RFI-AR-UB-05981 |  |  | Construction
. | EGAT-RFI-AR-UB-05981.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 | Touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 |  | Construction |  | Changed from Cat. B |  |  |  | EGAT-RFI-AR-UB-05981 |  |  | Construction
. | EGAT-RFI-AR-UB-05981.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 | Windows need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 |  | Construction |  | Changed from Cat. B |  |  |  | EGAT-RFI-AR-UB-05981 |  |  | Construction
. | EGAT-RFI-AR-UB-05981.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 28 | Touch up on windows to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 |  | Construction |  | Changed from Cat. B |  |  |  | EGAT-RFI-AR-UB-05981 |  |  | Construction
. | EGAT-RFI-AR-UB-05982.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 29 | Fouge and tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05982 |  |  | Construction
. | EGAT-RFI-AR-UB-05982.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 29 | Painted walls requisite touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05982 |  |  | Construction
. | EGAT-RFI-AR-UB-05982.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 29 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05982 |  |  | Construction
. | EGAT-RFI-AR-UB-05982.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 29 | Suspended ceiling need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-03-03 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05982 |  |  | Construction
. | EGAT-RFI-AR-UB-05982.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 29 | Cracks on gypsum wall board need to be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05982 |  |  | Construction
. | EGAT-RFI-AR-UB-05982.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 29 | Installations openings shall be improved | C | EL | HEC EL Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05982 |  |  | Construction
. | EGAT-RFI-AR-UB-05982.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 29 | Doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05982 |  |  | Construction
. | EGAT-RFI-AR-UB-05982.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 29 | Touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05982 |  |  | Construction
. | EGAT-RFI-AR-UB-05983.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 | Fouge and tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05983 |  |  | Construction
. | EGAT-RFI-AR-UB-05983.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 | Painted walls requisite touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05983 |  |  | Construction
. | EGAT-RFI-AR-UB-05983.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05983 |  |  | Construction
. | EGAT-RFI-AR-UB-05983.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 | Suspended ceiling need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 | 2023-03-07 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05983 |  |  | Construction
. | EGAT-RFI-AR-UB-05983.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 30 | Cracks on gypsum wall board need to be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05983 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Fouge and tiles required cleaning or replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Sealant around tiles needs improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Suspended ceiling need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-03-03 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Doors requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Windows requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.09 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.10 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Touch up on windows to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.11 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Windows need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.12 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Cracks on gypsum boards shall be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.13 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Window fittings to be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.14 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 20 | Painted walls requisite touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.15 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | Fouge and tiles required cleaning or replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.16 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.17 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | Sealant around tiles needs improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.18 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | Suspended ceiling need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-03-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.19 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | Doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.20 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | Touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.21 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | Doors requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.22 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | Joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.23 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | Cracks on gypsum boards shall be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.24 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 21 | Painted walls requisite touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.25 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Fouge and tiles required cleaning or replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.26 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.27 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Sealant around tiles needs improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.28 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Suspended ceiling need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-03-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.29 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.30 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.31 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Doors requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.32 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Windows requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.33 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.34 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Touch up on windows to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.35 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Windows need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.36 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Cracks on gypsum boards shall be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-18 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.37 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Window fittings to be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.38 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 22 | Painted walls requisite touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.39 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Fouge and tiles required cleaning or replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.40 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.41 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Sealant around tiles needs improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.42 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Suspended ceiling need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-03-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.43 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.44 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.45 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Doors requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.46 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Windows requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.47 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.48 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Touch up on windows to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.49 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Windows need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.50 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Cracks on gypsum boards shall be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.51 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Window fittings to be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.52 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 23 | Painted walls requisite touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.53 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | Fouge and tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.54 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.55 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | Sealant around tiles needs improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.56 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | Suspended ceiling need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-03-03 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.57 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | Doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.58 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | Touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.59 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | Doors requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.60 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | Joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.61 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | Cracks on gypsum boards shall be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-18 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.62 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 24 | Painted walls requisite touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.63 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Fouge and tiles required cleaning or replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.64 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.65 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Sealant around tiles needs improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.66 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Suspended ceiling need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-03-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.67 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.68 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.69 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Doors requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.70 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Windows requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.71 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.72 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Touch up on windows to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.73 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Windows need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.74 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Cracks on gypsum boards shall be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.75 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 25 | Window fittings to be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.76 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 26 | fouge and tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.77 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 26 | tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.78 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 26 | sealant around tiles needs improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.79 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 26 | suspended ceiling need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-03-07 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.80 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 26 | doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.81 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 26 | touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.82 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 26 | doors requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.83 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 26 | joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.84 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 26 | cracks on gypsum boards shall be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05988.85 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 26 | painted walls requisite touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction | [5 empty] | EGAT-RFI-AR-UB-05988 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Fouge and tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Sealant around tiles needs improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Suspended ceiling needs to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-03-24 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Doors requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-04-14 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.09 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Touch up on windows to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.10 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Windows need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.11 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Cracks on gypsum boards shall be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-04-14 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.12 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Window fittings to be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.13 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 27 | Painted walls requisite touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-04-14 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.14 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Fouge and tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.15 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Painted walls requisite touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.16 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.17 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Sealant around tiles needs improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.18 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Suspended ceiling needs to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-03-07 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.19 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.20 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.21 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Doors requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.22 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.23 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Touch up on windows to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.24 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Cracks on gypsum boards shall be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-04-18 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.25 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 32 | Fouge and tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.26 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 32 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.27 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 32 | Sealant around tiles needs improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.28 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 32 | Suspended ceiling needs to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-03-07 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.29 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 32 | Doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.30 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 32 | Touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.31 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 32 | Windows need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.32 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 32 | Doors requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction |  | Changed from Cat. B |  |  |  | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.33 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 32 | Joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-04-14 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.34 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 32 | Touch up on windows to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.35 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 33 | Fouge and tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.36 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 33 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.37 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 33 | Sealant around tiles needs improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.38 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 33 | Suspended ceiling needs to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-03-24 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.39 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 33 | Doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.40 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 33 | Touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.41 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 33 | Windows need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.42 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 33 | Doors requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction |  | Changed from Cat. B |  |  |  | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.43 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 33 | Touch up on windows to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.44 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 33 | Painted walls requisite touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.45 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Fouge and tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.46 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Tiles shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.47 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Sealant around tiles needs improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.48 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Suspended ceiling needs to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-03-07 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.49 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Doors need to be cleaned | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.50 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Touch up on doors to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.51 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Doors requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 |  | Construction |  | Changed from Cat. B |  |  |  | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.52 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.53 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Window fittings to be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-05989.54 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Painted walls requisite touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-15 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05989 |  |  | Construction
. | EGAT-RFI-AR-UB-06021.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Floor require cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-24 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-06021 |  |  | Construction
. | EGAT-RFI-AR-UB-06021.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Floor require cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-24 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-06021 |  |  | Construction
. | EGAT-RFI-AR-UB-06021.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | Pull of testneed to submitted | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-24 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-06021 |  |  | Construction
. | EGAT-RFI-AR-UB-06021.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | Pull of testneed to submitted | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-24 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-06021 |  |  | Construction
. | EGAT-RFI-AR-UB-06021.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 31 | The resistance test of the floor should be performed | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-24 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-06021 |  |  | Construction
. | EGAT-RFI-AR-UB-06021.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 34 | The resistance test of the floor should be performed | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-24 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-06021 |  |  | Construction
. | EGAT-RFI-AR-UB-06047.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Room No. 10 | Mirror with defect shall be replaced | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-24 | 2023-06-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03930.01 | 800.00 | 1304-12-20 | Workshop PP Area | EGAT-HEC-300-INC-DWG-00007_7 | Penetration hole need to be provide seal foam | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-31 | 2023-01-12 |  |  |  | 2023-01-12 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-03930.02 | 800.00 | 1304-12-20 | Workshop PP Area | EGAT-HEC-300-INC-DWG-00007_7 | Duct tray clip to be provide prior to cover | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-10-31 | 2023-01-12 |  |  |  | 2023-01-12 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04813.01 | 800.00 | 1304-12-20 | LABORATORY PP AREA | 1000-HS-7901A/T | Proper Name plate need to be provided | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-12-08 | 2023-01-10 |  |  |  | 2023-01-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04813.02 | 800.00 | 1304-12-20 | LABORATORY PP AREA | 1000-HS-7901A/T | Hand switch need to be provided rubber for separation | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-12-08 | 2023-01-10 |  |  |  | 2023-01-09 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04816.01 | 800.00 | 1304-12-20 | Laboratory & Workshop office building PP Area | 1000-GB-7920, 1000-TGB-7920, 1000-GH/TGH-7920, 1000-GB-8220, 1000-TGB-8220, 1000-GH/TGH-8220 | Name plate need to be provided | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-12-08 | 2023-01-03 |  |  |  | 2023-01-03 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04825.01 | 800.00 | 1304-12-20 | Laboratory & Workshop office building PP Area | For all tags in description | 1000-GB-8222, 1000-TGB-8222, 1000-GGH/TGH-8222, 1000-GB-8223, 1000-TGB-8223, 1000-GB-7920, 1000-TGB-7920, 1000-GH/TGH-7920 - SS Cable tag to be provided | C | CI | CW Construction | Mr. Paweł Rogoziński | 2022-12-08 | 2023-03-17 |  |  |  | 2023-03-17 | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04825.02 | 800.00 | 1304-12-20 | Laboratory & Workshop office building PP Area | 1000-HS-7901A/T | Earthing cable need to be fixed | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-12-08 | 2023-01-19 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04825.03 | 800.00 | 1304-12-20 | Laboratory & Workshop office building PP Area | EGAT-HEC-300-INC-DWG-00007-Z0 | Fire stop need to be done & provide sticker | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-12-08 | 2023-01-03 |  |  |  | 2023-01-03 |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-01351.05 | 800.00 | 1304-12-20 | 1000-SS-01 | V-SPL-E02-000-00000-00287 | Point 16.5 - To much window in A01. For main breaker o keep IP2X when open the door (where it is possible to touch the live part) | A | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-02-09 | 2022-03-16 | SAT |  |  |  |  | V | EGAT-RFI-EL-SB-1351 |  |  | Construction
. | EGAT-RFI-EL-SB-02866.01 | 800.00 | 1304-12-20 | 1000-LB-41 | EGAT-HEC-900-ELE-DLP-03024_1 | Earthing connection should be provided for cable tray | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-06-16 | 2023-04-21 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03370.01 | 800.00 | 1304-12-20 | 1000-LB-41 | EGAT-HEC-1000-ELE-DLP-06004_2 | Fire alarm smoke detector tag provided all room | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-16 | 2023-04-11 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03370.02 | 800.00 | 1304-12-20 | 1000-LB-41 | EGAT-HEC-1000-ELE-DLP-06004_2 | Logical address should be provided for each SD | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-16 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03370.03 | 800.00 | 1304-12-20 | 1000-LB-41 | EGAT-HEC-1000-ELE-DLP-06004_2 | The place of the one SD is to be changed in PP Analysis room | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-16 | 2023-05-12 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03370.04 | 800.00 | 1304-12-20 | 1000-LB-41 | EGAT-HEC-1000-ELE-DLP-06004_2 | The place og the one SD is to be changed in lobby area | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2022-07-16 | 2023-05-12 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03435.01 | 800.00 | 1304-12-20 | 1000-LB-41 | EGAT-HEC-1000-ELE-DLP-05006_5 | Earthing connection should be provided for cable tray | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-07-21 | 2023-05-04 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03655.01 | 800.00 | 1304-12-20 | 1000-LB-41 | EGAT-HEC-900-ELE-DLP-01030_2 | Earthing connection should be provided for cable tray | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-04 | 2023-04-17 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03668.01 | 800.00 | 1304-12-20 | 1000-LB-41 | EGAT-HEC-1000-ELE-DLP-00003_0 | Should be provide proper polish name tag on the 41-MDB-001 (+A06) Panel | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-05 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04149.01 | 800.00 | 1304-12-20 | PPL Aux Area | EGAT-HEC-1000-ELE-SCH-00002_1 | Fire barriers have to be installed where the cable is passing the wall | C | EL |  | Mr. Adam Siewiorek | 2022-09-13 | 2023-05-25 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04149.02 | 800.00 | 1304-12-20 | PPL Aux Area | EGAT-HEC-1000-ELE-SCH-00002_1 | The cable from the cable tray to the equipment is to be tie-up into the conduit or have to be clamping in the wall | C | EL |  | Mr. Adam Siewiorek | 2022-09-13 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04149.03 | 800.00 | 1304-12-20 | PPL Aux Area | EGAT-HEC-1000-ELE-SCH-00002_1 | Missing cable tag should be provided | C | EL |  | Mr. Adam Siewiorek | 2022-09-13 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04150.01 | 800.00 | 1304-12-20 | PPL Aux Area | EGAT-HEC-1000-ELE-SCH-00002_1 | Fire barriers have to be installed where the cable is passing the ewall | C | EL |  | Mr. Adam Siewiorek | 2022-09-13 | 2023-05-25 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04150.02 | 800.00 | 1304-12-20 | PPL Aux Area | EGAT-HEC-1000-ELE-SCH-00002_1 | The cable from the cable tray to the equipment is to tie-up into the conduit or have to be clamping in the wall | C | EL |  | Mr. Adam Siewiorek | 2022-09-13 | 2023-05-25 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04150.03 | 800.00 | 1304-12-20 | PPL Aux Area | EGAT-HEC-1000-ELE-SCH-00002_1 | Missing cable tag should be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-09-13 | 2023-05-17 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04309.01 | 800.00 | 1304-12-20 | Laboratory | V-SPL-E02-000-00000-00287 | Interface test with ECMS not completed | C | EL |  | Mr. Adam Siewiorek | 2022-09-26 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04309.02 | 800.00 | 1304-12-20 | Laboratory | V-SPL-E02-000-00000-00287 | Panel roof to be repaired | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-09-26 | 2023-05-05 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04427.01 | 800.00 | 1304-12-20 | Laboratory | EGAT-ELE-1000-ELE-DGA-00003_0 | Actual site MCB is 16A but in the drawing it is 63A Clarify with HEC Design (41-PDP-002 & 41-PDP-003) | C | EL |  | Mr. Arkadiusz Tryniszewski | 2022-09-29 | 2023-03-30 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04696.01 | 800.00 | 1304-12-20 | LABORATORY ROOF AREA | EGAT-HEC-1000-ELE-DLP-05006_5 | EARTHING CONNECTION SHLOULD BE PROVIDED FOR CABLE TRAY | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2023-04-25 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-04796.01 | 800.00 | 1304-12-20 | Laboratory Building Roof | EGAT-HEC-1000-ELE-DLP-05006_5 | Earthing connection should be provided for Cable Tray. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2022-10-18 | 2023-04-05 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05061.01 | 800.00 | 1304-12-20 | Laboratory Bldg. | EAGT-HEC-1000-ELE-DLP-05006_Z0 | The Tag Should be provided for Normal & Emergency Lighting Fixture, JB & Socket Outlet (Recepticals}. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2022-11-04 | 2023-04-14 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05061.02 | 800.00 | 1304-12-20 | Laboratory Bldg. | EAGT-HEC-1000-ELE-DLP-05006_Z0 | Unused holes with the Socket Outlet(Recepticals) Square Boxes after updated revision need to be clerify. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2022-11-04 | 2023-05-09 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05061.03 | 800.00 | 1304-12-20 | Laboratory Bldg. | EAGT-HEC-1000-ELE-DLP-05006_Z0 | Locker Room One Recepticals need to be replace. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2022-11-04 | 2023-05-18 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05061.04 | 800.00 | 1304-12-20 | Laboratory Bldg. | EAGT-HEC-1000-ELE-DLP-05006_Z0 | Missing CNBOP Lighting fixture install in Toilet Area. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2022-11-04 | 2023-04-14 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05061.05 | 800.00 | 1304-12-20 | Laboratory Bldg. | EAGT-HEC-1000-ELE-DLP-05006_Z0 | Drawing should be updated in the next revision | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2022-11-04 | 2023-05-09 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05073.01 | 800.00 | 1304-12-20 | Laboratory Bldg. | EGAT-HEC-1000-ELE-DLP-05006_Z0 | The Tag Should be provided for Escape & Exit Lighting Fixture &JB. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2022-11-04 | 2023-04-18 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05073.02 | 800.00 | 1304-12-20 | Laboratory Bldg. | EGAT-HEC-1000-ELE-DLP-05006_Z0 | Chemical Storage Room need to install Escape Light should be clerify with designer. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2022-11-04 | 2023-05-10 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05073.03 | 800.00 | 1304-12-20 | Laboratory Bldg. | EGAT-HEC-1000-ELE-DLP-05006_Z0 | Emergency & Exit Light tag Colour Should be Changed. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2022-11-04 | 2023-04-04 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05074.01 | 800.00 | 1304-12-20 | LB-41 | EGAT-HEC-1000-ELE-DLP-05006_Z0 | All Escape & Exit Lighting Cable Tag Should be Provided. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2022-11-04 | 2023-04-14 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05074.02 | 800.00 | 1304-12-20 | LB-41 | EGAT-HEC-1000-ELE-DLP-05006_Z0 | All Escape & Exit lighting cables should not hang more than 500 mm from the junction box to the lighting fixture. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2022-11-04 | 2023-04-14 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05074.03 | 800.00 | 1304-12-20 | LB-41 | EGAT-HEC-1000-ELE-DLP-05006_Z0 | Provide the fire stopper & Hilti stickers for the cable entry & exit points. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2022-11-04 | 2023-04-13 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05742.01 | 800.00 | 1304-12-20 | LB-41 | EGAT-HEC-1000-ELE-DLP-05006_Z0 | 41-PDP-012 CKT no. -FZ3 Cable Termination & Loop Impedance Shall be done. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2023-02-02 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05742.02 | 800.00 | 1304-12-20 | LB-41 | EGAT-HEC-1000-ELE-DLP-05006_Z0 | 41-POP-014 CKT no. -FZ8,FZ9,FZ14,FZ17 Cable Termination & Loop Impedance Shall be done. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2023-02-02 | 2023-03-23 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05742.03 | 800.00 | 1304-12-20 | LB-41 | EGAT-HEC-1000-ELE-DLP-05006_Z0 | 41-PDP-015 CKT no. -FZ10,FZ20 Cable Termination & loop Impedance Shall be done. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2023-02-02 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05742.04 | 800.00 | 1304-12-20 | LB-41 | EGAT-HEC-1000-ELE-DLP-05006_Z0 | 41-PDP-018 CKT no. -FZ16 Cable Termination & Loop Impedance Shall be done. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2023-02-02 |  | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05742.05 | 800.00 | 1304-12-20 | LB-41 | EGAT-HEC-1000-ELE-DLP-05006_Z0 | 41-PDP-013 CKT no. -FZ23 Cable Termination & Loop Impedance Shall be done. | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2023-02-02 | 2023-05-09 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06146.02 | 800.00 | 1304-12-20 | Laboratory bldg | EGAT-HEC-1000-INC-DLP-50212_2 | 41-EEB-011 Broken glass should be replace & labelling should be correct. | C | EL |  | Mr. Adam Zbroja | 2023-01-26 | 2023-04-04 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07025.01 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | All faults to be cleared from FACP. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.02 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Tag no's missing for FH/FB outdoor. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 | 2023-06-15 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07025.03 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | 1000-FH-7903 volume temporarly reduced for SAT (dipswitch) -volume to be turned up. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.04 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Tag no's decetors on the ceiling to be provided. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.05 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Tag no's missing for Remote Indicators: 1000-SD-8006-RI, 7980-RI, 8060-RI. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 | 2023-06-06 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07025.06 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Loical numbers for all devices to be provided. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.07 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Tag no's missing for decetors and RI's in PP Balance Room (24). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07025.08 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Position of duct smoke detectors shell be visually signed on the ceiling (e.g. by red dot). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.09 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Fire dampers 1000-LB41-MFD-001, 002 temporarly disabled for SAT (zones 3738-3739, outputs 3675-3676). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.10 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | 1000-SD-7932: wrong sticker with tag no (7931). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 | 2023-06-06 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07025.11 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | 1000-SD-7931: 7932: wrong sticker with tag no (7932). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 | 2023-06-06 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07025.12 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | 1000-SD-8011: wrong sticker with tag no on RI (7911-RI). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 | 2023-06-06 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07025.13 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | 1000-SD-8009:wrong sticker with tag no on RI (8011-RI). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 | 2023-06-06 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07025.14 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | 1000-SD-8024, 8034, 7976 gets fault after testing - to be cleared from dust. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.15 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Power Supply 1000-LB41-PSU-0001 - Cable tag missing. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07025.16 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Fault output: FB-7912, 7913 is displayed after testing detectors in PDH Analyzing room (19) | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.17 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Fault output: FB-7914,7915 is displayed after testing detectors in Air Lock -1. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.18 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Fault output: FB-7916 is displayed after testing detectors in Shower M (10). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.19 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Fault output: FB-7904,7905,7906 is displayed after testing detectors in Elec. Room (36). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.20 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Location descriptions on FACP to be corrected (for listed devices): - Air Lock Room-Air Lock-1 (1000-SD-7902, 7962), - MAC Conference R.- MAC Air Lock-1 (1000-MAC-7901), - Corridor CV-Corridor-1-CV (1000-SD-7963,7964,7973), - Corridor-Corridor-1(1000-SD-7906,7907,7908), - Locker R.F. Clear-Locker R.F. Clean (1000-SD-7974,7912), - Locker R.M. Clear-Locker R.M. Clean (1000-SD-7975, 7913), - Corridor-Corridor-1(1000-MAC-7902). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.21 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | 1000-SD-7907-Location on FACP is displayed as ''CV'' (7907 is not CV detector). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.22 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | 1000-SD-7964-Location on FACP is displayed without ''CV'' (7964 is CV detector). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.23 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | 1000-SD-8060-Location on FACP is displayed with ''CV'' instead of ''AV'' (Access Void detector). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.24 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | Glow in the dark plate missing for 1000-MAC-7907 in Electrical Room. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 | 2023-06-06 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07025.25 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | 1000-LB41-HCP-0001-FAS not connected to HVAC cabinet. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07025.26 | 800.00 | 1304-12-20 | 1000-LB-41 (Lab building) | EGAT-HEC-1000-ELE-DLP-06004 | FAS connection with DCS (ESD signal), HVAC, etc. to be tested. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-02 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-4310.01 | 800.00 | 1304-12-20 | Laboratory | V-SPL-E02-000-00000-00292 | Interface test with ECMS not completed. | C | EL |  | Mr. Adam Siewiorek | 2022-09-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-4310.02 | 800.00 | 1304-12-20 | Laboratory | V-SPL-E02-000-00000-00292 | F1 is missing in feeder A02.DA001(Manufacturer Scope) | C | EL |  | Mr. Adam Siewiorek | 2022-09-28 | 2023-04-14 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-4310.03 | 800.00 | 1304-12-20 | Laboratory | V-SPL-E02-000-00000-00292 | Q1 Contact is missing in feeder A04.BA001 (Manufacturer Scope) | C | EL |  | Mr. Adam Siewiorek | 2022-09-28 | 2023-04-14 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-4310.04 | 800.00 | 1304-12-20 | Laboratory | V-SPL-E02-000-00000-00292 | F1 is missing in feeder A05.LA001 (Manufacturer Scope) | C | EL |  | Mr. Adam Siewiorek | 2022-09-28 | 2023-04-14 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-4310.05 | 800.00 | 1304-12-20 | Laboratory | V-SPL-E02-000-00000-00292 | F1 is Incompatible in feeder A05.NA001 (Manufacturer Scope) | C | EL |  | Mr. Adam Siewiorek | 2022-09-28 | 2023-04-14 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-4310.06 | 800.00 | 1304-12-20 | Laboratory | V-SPL-E02-000-00000-00292 | Q1 Contact is missing in feeder A04.DA001 (Manufacturer Scope) | C | EL |  | Mr. Adam Siewiorek | 2022-09-28 | 2023-04-14 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-4310.07 | 800.00 | 1304-12-20 | Laboratory | V-SPL-E02-000-00000-00292 | F1 is Incompatible in feeder A05.QA001 (Manufacturer Scope) | C | EL |  | Mr. Adam Siewiorek | 2022-09-28 | 2023-04-14 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-4310.08 | 800.00 | 1304-12-20 | Laboratory | V-SPL-E02-000-00000-00292 | K2 Contact not working in feeder A06.FA001 (Manufacturer Scope) | C | EL |  | Mr. Adam Siewiorek | 2022-09-28 | 2023-04-14 | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-4310.09 | 800.00 | 1304-12-20 | Laboratory | V-SPL-E02-000-00000-00292 | No settings to A05 Outgoing Feeders (CBS-001, CBS-002) | C | EL |  | Mr. Adam Siewiorek | 2022-09-28 |  | SAT |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-00716.01 | 800.00 | 1304-12-20 | 1000-LB-41 | RL/RG Installation | To be arrangment of pipes and cables in cable trays | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00716 |  |  | Construction
. | EGAT-RFI-HV-JW-00716.02 | 800.00 | 1304-12-20 | 1000-LB-41 | RL/RG Installation | To be provided statment of using nitrogen | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-07-07 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00716 |  |  | Construction
. | EGAT-RFI-HV-JW-00716.03 | 800.00 | 1304-12-20 | 1000-LB-41 | RL/RG Installation | To be assembly of clips for holding pipes | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-08-10 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00716 |  |  | Construction
. | EGAT-RFI-HV-JW-00716.04 | 800.00 | 1304-12-20 | 1000-LB-41 | RL/RG Installation | To be corrected crossing of pipes - Room 2 and 36 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-08-10 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00716 |  |  | Construction
. | EGAT-RFI-HV-JW-00717.01 | 800.00 | 1304-12-20 | 1000-LB-41 | RL/RG Installation | To be corrected clamps in cable trays | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-07-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00717 |  |  | Construction
. | EGAT-RFI-HV-JW-00717.02 | 800.00 | 1304-12-20 | 1000-LB-41 | RL/RG Installation | To be fixed sharp edges on cable trays | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-10-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00717 |  |  | Construction
. | EGAT-RFI-HV-JW-00717.03 | 800.00 | 1304-12-20 | 1000-LB-41 | RL/RG Installation | To be provided statment of using nitrogen | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-07-07 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00717 |  |  | Construction
. | EGAT-RFI-HV-JW-00717.04 | 800.00 | 1304-12-20 | 1000-LB-41 | RL/RG Installation | To be assembly of caps on profiles | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-06 | 2022-07-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00717 |  |  | Construction
. | EGAT-RFI-HV-JW-00720.01 | 800.00 | 1304-12-20 | 1000-LB-41 | IA, PN, OW pipe installation | Location of connection (floor and wall) to check with Architecture Team. Lack of information about dimansions in the HVAC design | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-04 | 2023-03-20 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00720 |  |  | Construction
. | EGAT-RFI-HV-JW-00815.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Vent Pipe Installation | To be assembled pipe sleeves on vents going thru wall | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00815 |  |  | Construction
. | EGAT-RFI-HV-JW-00832.01 | 800.00 | 1304-12-20 | 1000-LB-41 | RL/RG Pipe Insulation | To be provided as-built dwg. including route change | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-08 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00832 |  |  | Construction
. | EGAT-RFI-HV-JW-00832.02 | 800.00 | 1304-12-20 | 1000-LB-41 | RL/RG Pipe Insulation | To be sealed opens for cable tray with pipes acc. to detail | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-08 | 2022-12-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00832 |  |  | Construction
. | EGAT-RFI-HV-JW-00836.01 | 800.00 | 1304-12-20 | 1000-LB-41 | CTH Installation | Damaged paint coating | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 | 2023-01-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00836 |  |  | Construction
. | EGAT-RFI-HV-JW-00836.02 | 800.00 | 1304-12-20 | 1000-LB-41 | CTH Installation | Damaged air supply element | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 | 2023-01-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00836 |  |  | Construction
. | EGAT-RFI-HV-JW-00836.03 | 800.00 | 1304-12-20 | 1000-LB-41 | CTH Installation | Gap between unit elements | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 | 2023-05-22 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00836 |  |  | Construction
. | EGAT-RFI-HV-JW-00841.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Installation | Lack of revisions on ducts | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00841 |  |  | Construction
. | EGAT-RFI-HV-JW-00841.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Installation | Ducts are in collisions with other installations and support elements | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00841 |  |  | Construction
. | EGAT-RFI-HV-JW-00841.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Installation | Lack of connecting elements for flexible ducts | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00841 |  |  | Construction
. | EGAT-RFI-HV-JW-00841.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Installation | Lack of access to VD | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00841 |  |  | Construction
. | EGAT-RFI-HV-JW-00841.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Installation | Lack of access to exhoust fan | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00841 |  |  | Construction
. | EGAT-RFI-HV-JW-00841.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Installation | Lack of rubber at profiles - uninsulated ducts | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-09-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00841 |  |  | Construction
. | EGAT-RFI-HV-JW-00841.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Installation | To be corrected/ performed all passes thru wall | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-01-19 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00841 |  |  | Construction
. | EGAT-RFI-HV-JW-00841.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Installation | Lack of joint (wholes) for fume hood/ arm hood/ canopy hood | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00841 |  |  | Construction
. | EGAT-RFI-HV-JW-00841.09 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Installation | Routine/ level of ducts different than at the desing | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-02-03 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00841 |  |  | Construction
. | EGAT-RFI-HV-JW-00842.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Support Installation | Ducts are in collisions with other installations and support elements | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00842 |  |  | Construction
. | EGAT-RFI-HV-JW-00844.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Installation | Duct elements are not fitted | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 | 2022-08-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00844 |  |  | Construction
. | EGAT-RFI-HV-JW-00844.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Installation | Corrosion on ducts | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 | 2023-01-20 | Construction |  | 'Punch Category' changed A -> B (2022-09-28) evidence attached |  |  | V | EGAT-RFI-HV-JW-00844 |  |  | Construction
. | EGAT-RFI-HV-JW-00844.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Installation | Screw need to be replaced with stainless screw | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 | 2022-08-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00844 |  |  | Construction
. | EGAT-RFI-HV-JW-00845.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Support Installation | Missing caps on support profiles | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 | 2022-08-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00845 |  |  | Construction
. | EGAT-RFI-HV-JW-00845.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Support Installation | Profiles are screwed not thight | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 | 2023-01-19 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00845 |  |  | Construction
. | EGAT-RFI-HV-JW-00846.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accesory Installation | Corrosion on the fans | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00846 |  |  | Construction
. | EGAT-RFI-HV-JW-00846.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accesory Installation | Screw need to be replaced with stainless screw | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 | 2022-10-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00846 |  |  | Construction
. | EGAT-RFI-HV-JW-00846.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accesory Installation | Remove safeguard from antivibrations pads | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 | 2022-07-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00846 |  |  | Construction
. | EGAT-RFI-HV-JW-00846.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accesory Installation | Duct elements are not fitted | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 | 2022-10-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00846 |  |  | Construction
. | EGAT-RFI-HV-JW-00852.01 | 800.00 | 1304-12-20 | 1000-LB-41 | ED Pipe Installation | To be provided as-built dwg. including all changes | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-01 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00852 |  |  | Construction
. | EGAT-RFI-HV-JW-00859.01 | 800.00 | 1304-12-20 | 1000-LB-41 | AHU Installation | To be removed traces of corrosion - all AHU | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 |  | Construction |  | 'Punch Category' changed A -> B (2022-09-28) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-00859 |  |  | Construction
. | EGAT-RFI-HV-JW-00859.02 | 800.00 | 1304-12-20 | 1000-LB-41 | AHU Installation | To be removed remaining tapes on all AHU | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00859 |  |  | Construction
. | EGAT-RFI-HV-JW-00859.03 | 800.00 | 1304-12-20 | 1000-LB-41 | AHU Installation | To be cut profile for full opening the access door - AHU-003 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-10-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00859 |  |  | Construction
. | EGAT-RFI-HV-JW-00859.04 | 800.00 | 1304-12-20 | 1000-LB-41 | AHU Installation | To be removed cable tray for full openning the access door - AHU-003 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-10-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00859 |  |  | Construction
. | EGAT-RFI-HV-JW-00859.05 | 800.00 | 1304-12-20 | 1000-LB-41 | AHU Installation | To be fixed internal door in control panel - AHU-001 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00859 |  |  | Construction
. | EGAT-RFI-HV-JW-00860.01 | 800.00 | 1304-12-20 | 1000-LB-41 | FAN Installation | To be removed traces of corrosion - all Fans | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-28 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00860 |  |  | Construction
. | EGAT-RFI-HV-JW-00860.02 | 800.00 | 1304-12-20 | 1000-LB-41 | FAN Installation | To be corrected flexible connection and positioned centrally - all Fans | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-28 | 2023-01-19 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00860 |  |  | Construction
. | EGAT-RFI-HV-JW-00860.03 | 800.00 | 1304-12-20 | 1000-LB-41 | FAN Installation | To be corrected assembly of impuls tubes - all Fans | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-28 | 2022-10-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00860 |  |  | Construction
. | EGAT-RFI-HV-JW-00860.04 | 800.00 | 1304-12-20 | 1000-LB-41 | FAN Installation | To be fixed open damper - FN-005 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-28 | 2022-10-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00860 |  |  | Construction
. | EGAT-RFI-HV-JW-00860.05 | 800.00 | 1304-12-20 | 1000-LB-41 | FAN Installation | To be installed cap on lubricant container | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-28 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00860 |  |  | Construction
. | EGAT-RFI-HV-JW-00860.06 | 800.00 | 1304-12-20 | 1000-LB-41 | FAN Installation | To check the distance from rainhood | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-28 | 2022-10-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00860 |  |  | Construction
. | EGAT-RFI-HV-JW-00860.07 | 800.00 | 1304-12-20 | 1000-LB-41 | FAN Installation | To be removed corrosion bearing bare | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-28 | 2023-03-06 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00860 |  |  | Construction
. | EGAT-RFI-HV-JW-00860.08 | 800.00 | 1304-12-20 | 1000-LB-41 | FAN Installation | Corrosion - junction box housing | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-28 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00860 |  |  | Construction
. | EGAT-RFI-HV-JW-00860.09 | 800.00 | 1304-12-20 | 1000-LB-41 | FAN Installation | Corrosion - shaft protection | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-28 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00860 |  |  | Construction
. | EGAT-RFI-HV-JW-00861.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Fan Installation | To be provided access and maintenance to fan - Room No. 12 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-01-20 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00861 |  |  | Construction
. | EGAT-RFI-HV-JW-00861.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Fan Installation | To be corrected flexible connection - Room No. 12 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00861 |  |  | Construction
. | EGAT-RFI-HV-JW-00861.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Fan Installation | To be corrected assembly of fan in line to ductwork - Room No. 16 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-01-20 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00861 |  |  | Construction
. | EGAT-RFI-HV-JW-00861.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Fan Installation | To be adjusted ductwork in line to fan - Room No. 14 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00861 |  |  | Construction
. | EGAT-RFI-HV-JW-00862.01 | 800.00 | 1304-12-20 | 1000-LB-41 | FAN Installation | To be translated description of nameplates into polish language - all | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-02-03 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00862 |  |  | Construction
. | EGAT-RFI-HV-JW-00862.02 | 800.00 | 1304-12-20 | 1000-LB-41 | FAN Installation | To be provided access to electrical duct heater - Room No. 30 | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-05-22 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00862 |  |  | Construction
. | EGAT-RFI-HV-JW-00863.01 | 800.00 | 1304-12-20 | 1000-LB-41 | ACCU Installation | To be protected assembling bolts for rust | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2023-01-20 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00863 |  |  | Construction
. | EGAT-RFI-HV-JW-00863.02 | 800.00 | 1304-12-20 | 1000-LB-41 | ACCU Installation | To be comb of lamells on evaporators - all ACCU | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-27 | 2022-10-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00863 |  |  | Construction
. | EGAT-RFI-HV-JW-00901.01 | 800.00 | 1304-12-20 | 1000-LB-41 | PW, WWS, WWR pipe insulation | To be corrected pipes going thru partition wall acc. to detail | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-25 | 2022-12-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00901 |  |  | Construction
. | EGAT-RFI-HV-JW-00901.02 | 800.00 | 1304-12-20 | 1000-LB-41 | PW, WWS, WWR pipe insulation | To be corrected pipes going thru partition wall acc. to approval | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-25 | 2022-12-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00901 |  |  | Construction
. | EGAT-RFI-HV-JW-00901.03 | 800.00 | 1304-12-20 | 1000-LB-41 | PW, WWS, WWR pipe insulation | To be removed mechanical damages on insulation | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-25 | 2022-12-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00901 |  |  | Construction
. | EGAT-RFI-HV-JW-00901.04 | 800.00 | 1304-12-20 | 1000-LB-41 | PW, WWS, WWR pipe insulation | To be corrected unglued tapes, insulation etc. | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-25 | 2022-12-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00901 |  |  | Construction
. | EGAT-RFI-HV-JW-00901.05 | 800.00 | 1304-12-20 | 1000-LB-41 | PW, WWS, WWR pipe insulation | To be cleaned insulation on pipes | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-25 | 2023-05-04 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00901 |  |  | Construction
. | EGAT-RFI-HV-JW-00902.01 | 800.00 | 1304-12-20 | 1000-LB-41 | IA, PN, DW pipe insulation | To be corrected pipes going thru partition wall acc. to detail | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-25 | 2022-12-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00902 |  |  | Construction
. | EGAT-RFI-HV-JW-00902.02 | 800.00 | 1304-12-20 | 1000-LB-41 | IA, PN, DW pipe insulation | To be corrected pipes going thru partition wall acc. to approval | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-25 | 2022-12-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00902 |  |  | Construction
. | EGAT-RFI-HV-JW-00902.03 | 800.00 | 1304-12-20 | 1000-LB-41 | IA, PN, DW pipe insulation | To be removed mechanical damages on insulation | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-25 | 2022-12-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00902 |  |  | Construction
. | EGAT-RFI-HV-JW-00902.04 | 800.00 | 1304-12-20 | 1000-LB-41 | IA, PN, DW pipe insulation | To be corrected unglued tapes, insulation etc. | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-25 | 2022-12-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00902 |  |  | Construction
. | EGAT-RFI-HV-JW-00902.05 | 800.00 | 1304-12-20 | 1000-LB-41 | IA, PN, DW pipe insulation | To be cleaned insulation on pipes | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-25 | 2023-05-04 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00902 |  |  | Construction
. | EGAT-RFI-HV-JW-00919.01 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Installation | Add supports for ducts | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-26 | 2023-01-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00919 |  |  | Construction
. | EGAT-RFI-HV-JW-00919.02 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Installation | Silicones should be smoother, remove sharp edges on duct on high 2,5 counting from floor elevation | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-26 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00919 |  |  | Construction
. | EGAT-RFI-HV-JW-00919.03 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Installation | In Room No. 27 duct is laying on savage installation | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-26 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00919 |  |  | Construction
. | EGAT-RFI-HV-JW-00919.04 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Installation | Wall passages | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-26 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00919 |  |  | Construction
. | EGAT-RFI-HV-JW-00919.05 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Installation | In Rooms No. 23 and 25 ducts are not straight | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-26 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00919 |  |  | Construction
. | EGAT-RFI-HV-JW-00919.06 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Installation | Room No. 20 - turn the fitting | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-26 | 2022-12-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00919 |  |  | Construction
. | EGAT-RFI-HV-JW-00919.07 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Installation | Room No. 28 - lack of passage in B axis, duct is not straight | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-26 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00919 |  |  | Construction
. | EGAT-RFI-HV-JW-00919.08 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Installation | The screws inside the ducts | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-26 | 2023-01-03 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00919 |  |  | Construction
. | EGAT-RFI-HV-JW-00919.09 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Installation | Room No. 19 - lack of anti vibration element on hangers | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-26 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00919 |  |  | Construction
. | EGAT-RFI-HV-JW-00919.10 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Installation | Room No. 30 - support is missing, duct should be longer due to colisions of ducts | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-26 | 2022-12-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00919 |  |  | Construction
. | EGAT-RFI-HV-JW-00919.11 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Installation | Rooms No. 34 and 31 was not inspected because doors was closed | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-26 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00919 |  |  | Construction
. | EGAT-RFI-HV-JW-00920.01 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Support Installation | To be added supports for ducts | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-29 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00920 |  |  | Construction
. | EGAT-RFI-HV-JW-00920.02 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Support Installation | To be fixed threaded rods | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-29 | 2023-01-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00920 |  |  | Construction
. | EGAT-RFI-HV-JW-00920.03 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Support Installation | To be added rubber for supports | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-29 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00920 |  |  | Construction
. | EGAT-RFI-HV-JW-00920.04 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Support Installation | To be removed sharp edges | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-29 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00920 |  |  | Construction
. | EGAT-RFI-HV-JW-00920.05 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Support Installation | To be adjusted and regulated all supports threaded rods | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-29 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00920 |  |  | Construction
. | EGAT-RFI-HV-JW-00921.01 | 800.00 | 1304-12-20 | 1000-LB-41 | EA Duct Installation | Rust on ducts, make straight top of steel coating, fix silicones | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-26 | 2023-02-15 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00921 |  |  | Construction
. | EGAT-RFI-HV-JW-00922.01 | 800.00 | 1304-12-20 | 1000-LB-41 | EA duct support installation | Rust on ducts, make straight top of steel coating, fix silicones | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-08-25 | 2023-01-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00922 |  |  | Construction
. | EGAT-RFI-HV-JW-01042.01 | 800.00 | 1304-12-20 | 1000-LB-41 | PW, WWS, WWR Pipe insulation | To be cleaned insulation on installation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-22 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01043 |  |  | Construction
. | EGAT-RFI-HV-JW-01042.02 | 800.00 | 1304-12-20 | 1000-LB-41 | PW, WWS, WWR Pipe insulation | To be filled sleeves acc. to detail | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-22 | 2022-12-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01043 |  |  | Construction
. | EGAT-RFI-HV-JW-01043.01 | 800.00 | 1304-12-20 | 1000-LB-41 | IA, PN, DW Pipe insulation | To be cleaned insulation on installation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-22 | 2023-05-04 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01043 |  |  | Construction
. | EGAT-RFI-HV-JW-01043.02 | 800.00 | 1304-12-20 | 1000-LB-41 | IA, PN, DW Pipe insulation | To be filled pipe sleeves acc. to detail | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-22 | 2022-12-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01043 |  |  | Construction
. | EGAT-RFI-HV-JW-01085.01 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Control Work - Cabling | To be installed tags on cables, next to devices, before walls etc. | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-01-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01085 |  |  | Construction
. | EGAT-RFI-HV-JW-01085.02 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Control Work - Cabling | To be corrected dimension of cables on dwg as-built | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-03-17 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01085 |  |  | Construction
. | EGAT-RFI-HV-JW-01085.03 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Control Work - Cabling | To be corrected routing of control cable to control panels hiding behind a wall | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01085 |  |  | Construction
. | EGAT-RFI-HV-JW-01085.04 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Control Work - Cabling | To be changed flush-mounted box on surface-mounted box for control panel | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01085 |  |  | Construction
. | EGAT-RFI-HV-JW-01085.05 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Control Work - Cabling | To be corrected height of installation control panel - Room No. 36 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-01-19 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01085 |  |  | Construction
. | EGAT-RFI-HV-JW-01085.06 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Control Work - Cabling | To be separated control cable from power cables in cable trays | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-02-07 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01085 |  |  | Construction
. | EGAT-RFI-HV-JW-01085.07 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Control Work - Cabling | To be assembled control panels, Room No. 1 and Room No. 15 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01085 |  |  | Construction
. | EGAT-RFI-HV-JW-01086.01 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Control Work - Cabling | To be removed rubber insulation from cables | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01086 |  |  | Construction
. | EGAT-RFI-HV-JW-01086.02 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Control Work - Cabling | To be added caps inside control panel | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01086 |  |  | Construction
. | EGAT-RFI-HV-JW-01086.03 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Control Work - Cabling | To be cut bigger openings in jacketing for MT, TT sensors | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01086 |  |  | Construction
. | EGAT-RFI-HV-JW-01086.04 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Control Work - Cabling | To be tighten the gland | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-01-19 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01086 |  |  | Construction
. | EGAT-RFI-HV-JW-01133.01 | 800.00 | 1304-12-20 | 1000-LB-41 | ED Pipe Instalation | To be sealed pipe going thru wall acc. to detail | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2022-12-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01133 |  |  | Construction
. | EGAT-RFI-HV-JW-01133.02 | 800.00 | 1304-12-20 | 1000-LB-41 | ED Pipe Instalation | To be extended last part of pipe to U-ditch | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-04-26 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01133 |  |  | Construction
. | EGAT-RFI-HV-JW-01133.03 | 800.00 | 1304-12-20 | 1000-LB-41 | ED Pipe Instalation | To be added support | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01133 |  |  | Construction
. | EGAT-RFI-HV-JW-01135.01 | 800.00 | 1304-12-20 | 1000-LB-41 | ED Pipe Insulation | To be removed mechanical damages on insulation | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2022-12-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01135 |  |  | Construction
. | EGAT-RFI-HV-JW-01135.02 | 800.00 | 1304-12-20 | 1000-LB-41 | ED Pipe Insulation | To be cleaned insulation on pipes | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-05-08 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01135 |  |  | Construction
. | EGAT-RFI-HV-JW-01135.03 | 800.00 | 1304-12-20 | 1000-LB-41 | ED Pipe Insulation | To be fixed support in Room No. 27 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01135 |  |  | Construction
. | EGAT-RFI-HV-JW-01135.04 | 800.00 | 1304-12-20 | 1000-LB-41 | ED Pipe Insulation | To be provided as-bulit including rerouting ED pipe in Room No. 31 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01135 |  |  | Construction
. | EGAT-RFI-HV-JW-01169.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Insulation | To be corrected insulation on duct - Room No. 19 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01169 |  |  | Construction
. | EGAT-RFI-HV-JW-01169.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Insulation | To be corrected insulation on duct - Room No. 21 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01169 |  |  | Construction
. | EGAT-RFI-HV-JW-01169.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Insulation | To be corrected insulation on duct - Room No. 26 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01169 |  |  | Construction
. | EGAT-RFI-HV-JW-01169.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Insulation | To be corrected insulation on duct - Room No. 24 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01169 |  |  | Construction
. | EGAT-RFI-HV-JW-01169.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Insulation | To be corrected insulation on duct - Room No. 34 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01169 |  |  | Construction
. | EGAT-RFI-HV-JW-01169.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Insulation | To be corrected insulation on duct - Room No. 30 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01169 |  |  | Construction
. | EGAT-RFI-HV-JW-01169.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Insulation | To be corrected insulation on duct - Room No. 28 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01169 |  |  | Construction
. | EGAT-RFI-HV-JW-01169.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Insulation | To be corrected insulation on duct - corridor | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01169 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be corrected felxible duct - Room No. 22 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be corrected felxible duct - Room No. 20 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be corrected felxible duct - Room No. 26 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.04 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be corrected felxible duct - Room No. 24 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.05 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be corrected felxible duct - Room No. 34 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.06 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be corrected felxible duct - Room No. 33 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.07 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be corrected felxible duct - Room No. 28 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.08 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be corrected felxible duct - corridor | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.09 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be corrected felxible duct - Room No. 8 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.10 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be corrected felxible duct - Room No. 13 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.11 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be install stickers open/close on VD - Room No. 31 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.12 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be install stickers open/close on VD - corridor | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.13 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be install stickers open/close on VD - Room No. 14 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.14 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be install stickers open/close on VD - Room No. 13 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.15 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be install stickers open/close on VD - Room No. 12 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.16 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be install stickers open/close on VD - Room No. 35 | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01170.17 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Accessory Installation | To be install stickers open/close on VD - corridor | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2022-12-21 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01170 |  |  | Construction
. | EGAT-RFI-HV-JW-01209.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Jacketing | To be installed access doors access to PN/EN | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-09 | 2023-01-20 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01209 |  |  | Construction
. | EGAT-RFI-HV-JW-01209.02 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Jacketing | To be installed stickers on VD open/closed | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-09 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01209 |  |  | Construction
. | EGAT-RFI-HV-JW-01209.03 | 800.00 | 1304-12-20 | 1000-LB-41 | Duct Jacketing | To be cleaned ducts/jacketing from mortar and etc. | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-09 | 2023-01-20 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01209 |  |  | Construction
. | EGAT-RFI-HV-JW-01237.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Vent Pipe Installation | To be provided as-built dwg of vent pipe detail | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-16 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01237 |  |  | Construction
. | EGAT-RFI-HV-JW-01282.01 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Equipment Installation | To be provided as-built dwg | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01282 |  |  | Construction
. | EGAT-RFI-HV-JW-01282.02 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Equipment Installation | To be corrected no. of ERD - stickers | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-08 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01282 |  |  | Construction
. | EGAT-RFI-HV-JW-01306.01 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Equipment Installation | The eyewash (safety shower) are not installed stably | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-21 | 2023-01-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01306 |  |  | Construction
. | EGAT-RFI-HV-JW-01306.02 | 800.00 | 1304-12-20 | 1000-LB-41 | HVAC Equipment Installation | Touch up painting should be provided | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-21 | 2023-01-23 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01306 |  |  | Construction
. | EGAT-RFI-HV-JW-01317.01 | 800.00 | 1304-12-20 | 1000-LB-41 | Fire Extinguisher Installtion | To be provided validity of fire extinguishers | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-23 | 2023-01-20 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01317 |  |  | Construction
. | EGAT-RFI-SS-MK-01369.01 | 800.00 | 1304-12-20 | AUX | 1000-LB-41 | Closing not secured of slipping | A | SS | HEC SS Construction | Mr. Andrzej Misiek | 2022-06-03 | 2022-09-12 | Construction |  |  |  |  | V | EGAT-RFI-SS-MK-01369 |  |  | Construction
. | EGAT-RFI-SS-MK-01369.02 | 800.00 | 1304-12-20 | AUX | 1000-LB-41 | Ladder not supported by foundation | C | SS | HEC SS Construction | Mr. Andrzej Misiek | 2022-06-03 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-SS-MK-01369 |  |  | Construction
. | EGAT-RFI-SS-MK-01369.03 | 800.00 | 1304-12-20 | AUX | 1000-LB-41 | U-Ditch gratings excluded from inspection | C | SS | HEC SS Construction | Mr. Andrzej Misiek | 2022-06-03 |  | Construction | [5 empty] | EGAT-RFI-SS-MK-01369 |  |  | Construction
. | 26070 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) |  | Final inspection for a building to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26071 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) |  | Final inspection for a cladding to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26072 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) |  | Final inspection for a flashing to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26073 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) |  | Final inspection for a doors and windows to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26074 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) |  | Final inspection for a paintig to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26075 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) |  | Final inspection for a suspended ceiling to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 | 2023-06-19 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26076 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) |  | Final inspection for a canopy to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26077 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) |  | Final inspection for a walkway to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26078 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) |  | Final inspection for a floor to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26079 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Refer to Photo in 04-PDHP-HEC-E-1377 | After concreting the walkway install sealant.reinforcement of the threshold with an angle bar | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26080 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Refer to Photo in 04-PDHP-HEC-E-1377 | General. Finish downspouts | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26081 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Refer to Photo in 04-PDHP-HEC-E-1377 | Install doors, frames and apropriate threseholds | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26082 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Refer to Photo in 04-PDHP-HEC-E-1377 | Find the reason of interior stains and fix/repair. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26083 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Refer to Photo in 04-PDHP-HEC-E-1377 | All damages on foundation surface should be repaired. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-20 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26084 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Waste shelter | Waste shelter not finished. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-20 | 2023-06-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26085 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Facades | All openings in the facades must be sealed with flashings. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-20 | 2023-05-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26086 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Facades | Scratches and damages on facades must be fixed. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-20 | 2023-06-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26087 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Overhead crane service platform | Grating grips must be tight. | C | SS | HEC SS Construction | Mr. Sebastian Stępień | 2023-01-20 | 2023-03-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26088 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Eastern facade | A gate is missing. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-20 | 2023-05-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26089 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | General | Plinth and walkway not done. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-20 | 2023-06-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26090 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | General | Facades must be cleaned. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-20 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26091 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Northern facade | One window on the Northern facades is missing. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-20 | 2023-04-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26092 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Western facade | Canopy above the door is missing. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-20 | 2023-04-18 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26093 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | General | Leakages on the facades must be cleaned and its reason investigated and eliminated. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-20 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26094 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | General | All structures must be cleaned. | C | SS | HEC SS Construction | Mr. Sebastian Stępień | 2023-01-20 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26095 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Steel structures | Rust must be removed, touch-up painting must be done. | C | SS | HEC SS Construction | Mr. Sebastian Stępień | 2023-01-20 |  | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26096 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | Doors | Doors are not finished. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-20 | 2023-05-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26097 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | General | The floor is dirty, there are many materials and equipment stored - no possibility to check floor condition. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-20 | 2023-05-19 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26098 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | General | Staff rooms are not finished. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-20 | 2023-05-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26893 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | EGAT-HEC-900-ELE-DLP-01018,04005,05007 | Tagno-34-ELP-001& 34-NLP-001 Lighting switch inspection to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-16 | 2023-05-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26894 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | EGAT-HEC-900-ELE-DLP-01018,04005,05007 | Lighting Fixture Tag, JB Tag & Cable tag to be install | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-16 | 2023-03-21 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26895 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | EGAT-HEC-900-ELE-DLP-01018,04005,05007 | Cable tray main earthing to be provided. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-16 | 2023-03-21 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26896 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | EGAT-HEC-900-ELE-DLP-01018,04005,05007 | Lighting panels Cable termination to be complete. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-16 | 2023-04-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26897 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | EGAT-HEC-900-ELE-DLP-01018,04005,05007 | Office room & Toilet room Lighting Fixtures, Socket Outlets and Switches to be install and official inspection to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-16 | 2023-05-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26898 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | EGAT-HEC-900-ELE-DLP-01018,04005,05007 | Illumination test to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-16 | 2023-05-08 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26899 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | EGAT-HEC-900-ELE-DLP-01018,04005,05007 | Lighting cable testing tobe done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-16 | 2023-04-21 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26900 | 800.00 | 1304-12-21 | Storage Building (1000-ST-34) | EGAT-HEC-900-ELE-DLP-01018,04005,05007 | CBS (Evacuation Lighting ) Cable termination and sat to be done and protocol to be submitted. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-16 | 2023-04-21 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 32452 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 (Axis 10-11/B-C) | Coating (paint) damages due to construction work activities. All structure including miscellaneus structure. | C | SS | HEC SS Construction | Mr. Sławomir Nasiłowski | 2023-06-21 |  | PAC | [8 empty] | RFC/RFSU
. | 32490 | 800.00 | 1304-12-21 | 1000-ST-34 | Facades | fix scratches and damages / clean / leakages on facades clean and the reason investigated and eliminated | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32491 | 800.00 | 1304-12-21 | 1000-ST-34 | TILES - Room no. 3 | tile and fouge cleaning / cleanout elevation shall be lover than floor elevation (duplicated) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32492 | 800.00 | 1304-12-21 | 1000-ST-34 | TILES - Room no. 3 | tile and fouge cleaning (floor and wall), wall tiles in corner and around switcher to replace | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32493 | 800.00 | 1304-12-21 | 1000-ST-34 | GATE - B-C/12 | flashing to do around gate inside and outside / bulb to remove and touch up painting / missing gate | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32494 | 800.00 | 1304-12-21 | 1000-ST-34 | Final inspection | Missing final inpsection for a building, cladding, flashing, doors and windows, painting, suspended ceiling, canopy, walkway, floor | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32495 | 800.00 | 1304-12-21 | 1000-ST-34 | GENERAL - SANDWICH PANEL - METAL ROOFING AND SIDING INSTALLATION | seak the substructure-south wall / damage to root panel joints / damage to root panel joints / replacement of corroded screw / dirty due to concrete and tape / traces of rust around the shutters / mechanival damage to panels - south side | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32635 | 800.00 | 1304-12-21 | 1000-ST-34 | Facades | fix scratches and damages / clean / leakages on facades clean and the reason investigated and eliminated | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32636 | 800.00 | 1304-12-21 | 1000-ST-34 | DOORS - ROOM NO. 1 | door cleaning and touch up painting / sealant around doors / door leaf requisite adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32637 | 800.00 | 1304-12-21 | 1000-ST-34 | DOORS - ROOM NO. 3 | door cleaning and touch up painting / sealant around doors / door leaf requisite adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | 32638 | 800.00 | 1304-12-21 | 1000-ST-34 | DOORS - ROOM NO. 4 | door cleaning and touch up painting / sealant around doors / door leaf requisite adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-26 |  | PAC | [8 empty] | RFC/RFSU
. | EGAT-RFI-AR-UB-01607.01 | 800.00 | 1304-12-21 | 1000-ST-34 | - | To be attach Survey report | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2021-03-22 | 2021-09-13 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-01607.01 | C-AR-UB-00099 |  | Construction
. | EGAT-RFI-AR-UB-01607.02 | 800.00 | 1304-12-21 | 1000-ST-34 | - | To be attach compaction test report | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2021-03-22 | 2021-09-13 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-01607.02 | C-AR-UB-00099 |  | Construction
. | EGAT-RFI-AR-UB-01728.01 | 800.00 | 1304-12-21 | 1000-ST-34 | - | To be attach Survey report | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2021-03-08 | 2021-09-15 | Construction |  | 11/03/2021 Transfer to Unibep |  |  | V | EGAT-RFI-AR-UB-01728.01 | C-AR-UB-00007 |  | Construction
. | EGAT-RFI-AR-UB-01728.02 | 800.00 | 1304-12-21 | 1000-ST-34 | - | To be attach Compaction test report | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2021-03-08 | 2021-09-15 | Construction |  | 11/03/2021 Transfer to Unibep |  |  | V | EGAT-RFI-AR-UB-01728.02 | C-AR-UB-00007 |  | Construction
. | EGAT-RFI-AR-UB-05480.01 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 5 | Wet surface | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-01 | 2023-04-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05480 |  |  | Construction
. | EGAT-RFI-AR-UB-05480.02 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 5 | Crack around joint | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-01 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05480 |  |  | Construction
. | EGAT-RFI-AR-UB-05480.03 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 5 | Lack of flashing | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-01 | 2023-04-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05480 |  |  | Construction
. | EGAT-RFI-AR-UB-05535.01 | 800.00 | 1304-12-21 | 1000-ST-34 | General | Touch-up painting/ fixing of concrete surface | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-09-16 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05535 |  |  | Construction
. | EGAT-RFI-AR-UB-05684.01 | 800.00 | 1304-12-21 | 1000-ST-34 | General | Cleaning | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05684 |  |  | Construction
. | EGAT-RFI-AR-UB-05863.01 | 800.00 | 1304-12-21 | 1000-ST-34 | General | Cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-08 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05863 |  |  | Construction
. | EGAT-RFI-AR-UB-05863.02 | 800.00 | 1304-12-21 | 1000-ST-34 | General | Stagnant water - to fix leakage from roof/ventilation louvers | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-08 | 2023-05-19 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05863 |  |  | Construction
. | EGAT-RFI-AR-UB-05907.01 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 4 | Touch up painting on window frame | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-05 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05907 |  |  | Construction
. | EGAT-RFI-AR-UB-05907.02 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 4 | Insect screen need to be installed | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-05 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05907 |  |  | Construction
. | EGAT-RFI-AR-UB-05907.03 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 4 | Door leaf regulation needs to be provide | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-05 | 2023-03-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05907 |  |  | Construction
. | EGAT-RFI-AR-UB-05907.04 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 4 | Door stopper to be performed | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-05 | 2023-03-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05907 |  |  | Construction
. | EGAT-RFI-AR-UB-05907.05 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 4 | Door closer to be installed | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-05 | 2023-03-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05907 |  |  | Construction
. | EGAT-RFI-AR-UB-05953.01 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 4 | Skirting part of plastering requiste improvement | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2023-03-06 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05953 |  |  | Construction
. | EGAT-RFI-AR-UB-05967.01 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 3 | Cleanout elevation shall be lower than floor elevation | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 |  | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05967 |  |  | Construction
. | EGAT-RFI-AR-UB-05967.02 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 3 | Tile and fouge required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 |  | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05967 |  |  | Construction
. | EGAT-RFI-AR-UB-05967.03 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 3 | Soot door required installation | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 | 2023-03-06 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05967 |  |  | Construction
. | EGAT-RFI-AR-UB-06058.01 | 800.00 | 1304-12-21 | 1000-ST-34 | 1A/1 | Touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.02 | 800.00 | 1304-12-21 | 1000-ST-34 | 1A/1 | Door require cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.03 | 800.00 | 1304-12-21 | 1000-ST-34 | 1A/1 | Panic bar shall be adjusted | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.04 | 800.00 | 1304-12-21 | 1000-ST-34 | 1A/1 | Installation botls need to be tightened | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.05 | 800.00 | 1304-12-21 | 1000-ST-34 | 1A/1 | Sealant around door to be done | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.06 | 800.00 | 1304-12-21 | 1000-ST-34 | 1A/1 | Earthing to the door leaf shall be installled | C | EL | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-04-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.07 | 800.00 | 1304-12-21 | 1000-ST-34 | B/12 | Door require cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.08 | 800.00 | 1304-12-21 | 1000-ST-34 | B/12 | Sealant around door to be done | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.09 | 800.00 | 1304-12-21 | 1000-ST-34 | B/12 | Earthing to the door leaf shall be installled | C | EL | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-04-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.10 | 800.00 | 1304-12-21 | 1000-ST-34 | B/12 | Door leaf shall be adjusted | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.11 | 800.00 | 1304-12-21 | 1000-ST-34 | B/12 | Damaged door require reparation | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.12 | 800.00 | 1304-12-21 | 1000-ST-34 | 1A/11 | Door require cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.13 | 800.00 | 1304-12-21 | 1000-ST-34 | 1A/11 | Sealant around door to be done | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.14 | 800.00 | 1304-12-21 | 1000-ST-34 | A/11 | Door require cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06058.15 | 800.00 | 1304-12-21 | 1000-ST-34 | A/11 | Sealant around door to be done | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-13 | 2023-05-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06059.01 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 1 | Doors require cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06059.02 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 1 | Touch up painting to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06059.03 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 1 | Sealant around door frame shall be finished | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06059.04 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 1 | Door leaf requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06059.05 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 3 | Doors require cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06059.06 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 3 | Touch up painting to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06059.07 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 3 | Sealant around door frame shall be finished | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06059.08 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 3 | Door leaf requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06059.09 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 4 | Doors require cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06059.10 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 4 | Touch up painting to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06059.11 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 4 | Sealant around door frame shall be finished | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06059.12 | 800.00 | 1304-12-21 | 1000-ST-34 | Room No. 4 | Door leaf requisite adjustment | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06077.01 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Touch-up painting to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-16 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06106.01 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Flshing to do ground gate inside and outside | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-04-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06106.02 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Bulb to remove and touch-up paint | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-04-22 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06111.01 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Dirty due to concrete and tape | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-05-04 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06111.02 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Traces of rust around the shutters | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-05-04 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06111.03 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Mechanical damage to panels-south wall | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-05-04 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06111.04 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Provide MAR on splash block, wrong splash block | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-05-04 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06111.05 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Seak the substructure-south wall | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-05-04 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06111.06 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Replacement of corroded screw | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-05-04 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06111.07 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Lack of bottom base angle | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-05-04 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06111.08 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Damage to root panel joints | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-05-04 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06111.09 | 800.00 | 1304-12-21 | 1000-ST-34 | - | MAR for sandwich panel | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-05-04 | 2023-06-01 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06132.01 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Fence to clean | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-31 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06132.02 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Tiles to clean | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-31 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06133.01 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Tiles to clean | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-31 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06133.02 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Tile in corner to replace | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-31 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06133.03 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Fence to clean | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-31 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06133.04 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Tiles around switches to replace | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-31 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06134.01 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Surface to improve around pedestal A/11 | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-31 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-AR-UB-06134.02 | 800.00 | 1304-12-21 | 1000-ST-34 | - | Lack of epoxy paint inside trench to check | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-05-31 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01276.01 | 800.00 | 1304-12-21 | 1000-ST-34 | EGAT-HEC-300-INC-DWG-00007_7 | Touch up paint to be done | A | CI | HEC CI Construction | Mr. Tomasz Jozel | 2022-05-12 | 2022-05-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-05718.01 | 800.00 | 1304-12-21 | PP area | 1000-TGD-8102 | Plug with ATEX mark need to be provided | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2023-01-25 | 2023-02-16 |  |  |  | 2023-02-15 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-05785.01 | 800.00 | 1304-12-21 | PDH area | 1000-hs-8101A/T | Hand switch push button cover for open touches with switch. Need to replace or rectify the cover | C | CI | CW Construction | Mr. Paweł Rogoziński | 2023-01-31 | 2023-03-23 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-05785.02 | 800.00 | 1304-12-21 | PDH area | 1000-hs-8101A/T | Rubber seperator between Handswitch and Galvanize plate need to be provided | C | CI | CW Construction | Mr. Paweł Rogoziński | 2023-01-31 | 2023-03-17 |  |  |  | 2023-03-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-05831.01 | 800.00 | 1304-12-21 | Calibration | Gas Detector 6ea | Alarm and pre alarm are not mentioned in calibration report | C | CI | CW Office | Mr. Paweł Rogoziński | 2023-02-20 | 2023-04-03 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01064.01 | 800.00 | 1304-12-21 | 1000-ST-34 | PW Pipe Installation | To be cleaned entire installation from mortar | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-20 | 2023-02-15 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01064 |  |  | Construction
. | EGAT-RFI-HV-JW-01064.02 | 800.00 | 1304-12-21 | 1000-ST-34 | PW Pipe Installation | To be installed pipesleeves on installation going thru partition | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-20 | 2023-02-15 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01064 |  |  | Construction
. | EGAT-RFI-HV-JW-01066.01 | 800.00 | 1304-12-21 | 1000-ST-34 | Vent Pipe Installation | To be installed pipesleeves on installation going thru partition | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-20 | 2023-02-15 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01066 |  |  | Construction
. | EGAT-RFI-HV-JW-01066.02 | 800.00 | 1304-12-21 | 1000-ST-34 | Vent Pipe Installation | To be cleaned installation from mortar | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-20 | 2023-02-15 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01066 |  |  | Construction
. | EGAT-RFI-HV-JW-01120.01 | 800.00 | 1304-12-21 | 1000-ST-34 | UG PW Pipe Installation | To be provided bolting report of PW connection | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2022-11-17 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01120 |  |  | Construction
. | EGAT-RFI-HV-JW-01120.02 | 800.00 | 1304-12-21 | 1000-ST-34 | UG PW Pipe Installation | To be provided wrapping report of PW connection | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2022-11-16 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01120 |  |  | Construction
. | EGAT-RFI-HV-JW-01137.01 | 800.00 | 1304-12-21 | 1000-ST-34 | PW Pipe Insulation | To be cleaned insulation on PW installation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-20 | 2023-02-15 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01137 |  |  | Construction
. | EGAT-RFI-HV-JW-01313.01 | 800.00 | 1304-12-21 | 1000-ST-34 | ED Pipe Installation | To be sealed pipe going thru a wall acc. to detail | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-23 | 2023-02-17 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01313 |  |  | Construction
. | EGAT-RFI-HV-JW-01313.02 | 800.00 | 1304-12-21 | 1000-ST-34 | ED Pipe Installation | To be assembled lost elbow and adjust the equipment of the piece of pipe | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-12-23 | 2023-02-15 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01313 |  |  | Construction
. | EGAT-RFI-HV-JW-01339.01 | 800.00 | 1304-12-21 | 1000-ST-34 | Duct Installation | To be sealed ducts going thru a walls acc. to detail | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-17 | 2023-03-09 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01339 |  |  | Construction
. | EGAT-RFI-HV-JW-01340.01 | 800.00 | 1304-12-21 | 1000-ST-34 | Duct Support Installation | To be added support and adjusting level of ducts | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-17 | 2023-03-09 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01340 |  |  | Construction
. | EGAT-RFI-HV-JW-01342.01 | 800.00 | 1304-12-21 | 1000-ST-34 | Duct insulation inspection | To be installed insulation on duct in walls | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-17 | 2023-03-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01342 |  |  | Construction
. | EGAT-RFI-HV-JW-01343.01 | 800.00 | 1304-12-21 | 1000-ST-34 | Fan installation inspection | To be installed impulse tube and PDS | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-17 | 2023-02-20 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01343 |  |  | Construction
. | EGAT-RFI-HV-JW-01343.02 | 800.00 | 1304-12-21 | 1000-ST-34 | Fan installation inspection | To be installed electrical and earthing cables | C | EL | HEC EL Construction | Mr. Jerzy Wegner | 2023-01-17 | 2023-04-18 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01343 |  |  | Construction
. | EGAT-RFI-HV-JW-01344.01 | 800.00 | 1304-12-21 | 1000-ST-34 | HRU Installation | To be provided acces to access door for maintenance | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-17 | 2023-05-10 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01344 |  |  | Construction
. | EGAT-RFI-HV-JW-01344.02 | 800.00 | 1304-12-21 | 1000-ST-34 | HRU Installation | To be added additional nuts on rods for supporting | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-17 | 2023-03-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01344 |  |  | Construction
. | EGAT-RFI-HV-JW-01344.03 | 800.00 | 1304-12-21 | 1000-ST-34 | HRU Installation | To be installed electrical and instruments cables | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-17 | 2023-02-20 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01344 |  |  | Construction
. | EGAT-RFI-HV-JW-01385.01 | 800.00 | 1304-12-21 | 1000-ST-34 | RL/RG Pipe Installation | To be corrected pipe sleeve on RL/RG installation | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-16 | 2023-02-17 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01385 |  |  | Construction
. | EGAT-RFI-HV-JW-01391.01 | 800.00 | 1304-12-21 | 1000-ST-34 | HVAC Equipment Installation | To be connected power cable to ACCU | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-21 | 2023-04-14 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01391 |  |  | Construction
. | EGAT-RFI-HV-JW-01391.02 | 800.00 | 1304-12-21 | 1000-ST-34 | HVAC Equipment Installation | Route of control cable do not agree with dwg | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-02-21 | 2023-05-15 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01391 |  |  | Construction
. | EGAT-RFI-HV-JW-01451.01 | 800.00 | 1304-12-21 | 1000-ST-34 | Hvac Equipment Installation | Extinguishers should be install on the walls due to documentations | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-04-07 | 2023-05-16 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01466.01 | 800.00 | 1304-12-21 | 1000-ST-34 | Hvac Equipment Instalation | Tag of fan is missing | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-04-07 | 2023-04-11 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01504.01 | 800.00 | 1304-12-21 | AUX | HVAC Equipment | Electric radiators are not connected to electrical instalation | C | HV | HEC HV Construction | Tomasz Ulatowski | 2002-05-16 | 2023-06-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-SS-MK-00713.01 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 | Anchor bolts not straight. Straightness is out of tolerance. | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2021-08-30 | 2022-03-03 | Construction |  |  |  |  | V | EGAT-RFI-SS-MK-00713 |  |  | Construction
. | EGAT-RFI-SS-MK-00722.01 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 | Straighness of anchor bolts out of tolerance | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2021-09-10 | 2022-03-03 | Construction |  |  |  |  | V | EGAT-RFI-SS-MK-00722 |  |  | Construction
. | EGAT-RFI-SS-MK-00727.01 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 | Straighness of anchor bolts out of tolerance | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2021-09-10 | 2022-03-03 | Construction |  |  |  |  | V | EGAT-RFI-SS-MK-00727 |  |  | Construction
. | EGAT-RFI-SS-MK-00735.01 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 | Straighness of anchor bolts out of tolerance | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2021-09-10 | 2022-03-03 | Construction |  |  |  |  | V | EGAT-RFI-SS-MK-00735 |  |  | Construction
. | EGAT-RFI-SS-MK-00775.01 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 | Excluded elements marked in attached ITR | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2021-09-20 | 2022-03-03 | Construction | 2021-12-16 |  |  |  | V | EGAT-RFI-SS-MK-00775 |  |  | Construction
. | EGAT-RFI-SS-MK-01068.01 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 Axis 10-11/B-C | Paint damages by bolts | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-01-28 | 2022-03-03 | Construction | 2022-01-29 | 'Punch Category' changed A -> C (2022-02-20) evidence attached |  |  | V | EGAT-RFI-SS-MK-01068 |  |  | Construction
. | EGAT-RFI-SS-MK-01068.02 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 Axis 10-11/B-C | Paint damages by transport | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-01-28 | 2023-06-21 | Construction | 2022-01-29 | 'Punch Category' changed A -> C (2022-02-20) evidence attached |  |  | V | EGAT-RFI-SS-MK-01068 |  |  | Construction
. | EGAT-RFI-SS-MK-01186.01 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 | Closing not secured of slipping | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-04 | 2022-06-24 | Construction | 2022-03-04 |  |  |  | V | EGAT-RFI-SS-MK-01186 |  |  | Construction
. | EGAT-RFI-SS-MK-01187.01 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 | Touch up painting (other branches) | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-03 | 2023-06-21 | Construction | 2022-03-11 |  |  |  | V | EGAT-RFI-SS-MK-01187 |  |  | Construction
. | EGAT-RFI-SS-MK-01187.02 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 | Closing of slipping not secure | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-03 | 2022-06-24 | Construction | 2022-03-11 |  |  |  | V | EGAT-RFI-SS-MK-01187 |  |  | Construction
. | EGAT-RFI-SS-MK-01187.03 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 | Lack of nuts in two anchor bolts (grid line B/12) | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-03 | 2023-03-17 | Construction | 2022-03-11 |  |  | SCAN CAT | V | EGAT-RFI-SS-MK-01187 |  |  | Construction
. | EGAT-RFI-SS-MK-01187.04 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 | Paint damages by transport | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-04 | 2023-06-21 | Construction | 2022-03-11 |  |  |  | V | EGAT-RFI-SS-MK-01187 |  |  | Construction
. | EGAT-RFI-SS-MK-01187.05 | 800.00 | 1304-12-21 | AUX | 1000-ST-34 | Paint damages by instalators | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-04 | 2023-06-21 | Construction | 2022-03-11 |  |  |  | V | EGAT-RFI-SS-MK-01187 |  |  | Construction
. | 26782 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) |  | Final inspection for a building to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26783 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) |  | Final inspection for a cladding to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26784 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) |  | Final inspection for a flashing to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26785 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) |  | Final inspection for a doors and windows to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26786 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) |  | Final inspection for a painting to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26787 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) |  | Final inspection for a suspended ceiling to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26788 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) |  | Final inspection for a canopy to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26789 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) |  | Final inspection for a walkway to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26790 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) |  | Final inspection for a floor to be done. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26791 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Ground floor should be finish | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-05 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26792 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Walls and ceilings have to be painted | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-05 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26793 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | A main gate should be done . | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-05-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26794 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Assembly a suspended ceiling | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-09 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26795 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Lack of the door. Install. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-05-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26796 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Repair damaged doors. General | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26797 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Repair damaged walls. General. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26798 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Lack of frame of the doors | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-05-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26799 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Install sealant after concreting a walkway | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26800 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | General. Finish downspouts | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26801 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Clean all rooms .General. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26802 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Assambly flashing on a garbage room and paint a facade. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26803 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Install doors and apropriate threseholds | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-05 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26804 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Paint again demaged doors | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-05 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26805 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Repair a facade. Close every hole and fill with fireproof material. | C | EL | HEC EL Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-04-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26806 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | A plinth should be finish. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26807 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Repair all damages on the canopy and flashing. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26808 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Plaster should be done | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-05 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26809 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Damaged floor must be repaired | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26810 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Every damages of drywall should be repaired. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26811 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Refer to photo in 04-PDHP-HEC-E-1381 | Finish the floor. | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-17 | 2023-06-05 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26812 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | All gas alarm horn (sounder) dual tone | There is discrepancy between site (1 horn: GH/TGH) and EGAT-HEC-300-INC-DWG-00007 (2 horns: GH & TGH).e.g. 1000-GH/TGH-6005 vs 1000-GH-6005 & 1000-TGH-6005 | C | CI | CW Construction | Mr. Mariusz Celmer | 2022-01-18 | 2023-03-27 | Walkdown |  |  | 2023-03-01 | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26813 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | 1000-GB-8221, 1000-GH-8221, 1000-TGB-8221, 1000-TGH-8221 | There is discrepancy between site and EGAT-HEC-300-INC-DWG-00007 (visual and audible alarm appliance shall be located at 2.3m above the floor). | C | CI | CW Construction | Mr. Mariusz Celmer | 2022-01-18 |  | Walkdown |  |  | 2023-03-01 | Rejected... DWG to be update as per site condition | V |  |  |  | RFC/RFSU
. | 26814 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Tags in description | No acces to device. Device shall be inspected during additional Walk Down. 1000-GB-6020, 1000-GH-6020, 1000-TGB-6020, 1000-TGH-6020, 1000-GD-6010, 1000-GD-6002, 1000-TGD-6002, 1000-TGD-6011, 1000-GD-6011, 1000-GD-8201, 1000-GD-8201, 1000-TGD-8210 | C | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-01-18 | 2023-03-28 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26815 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | 1000-HS-6002A/T, 1000-HS-8201A/T | Nameplates with pushbuttons description missing. | C | CI | HEC CI Construction | Mr. Mariusz Celmer | 2022-01-18 | 2023-03-01 | Walkdown |  |  | 2023-02-28 | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26816 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General | Lack of FAT and SAT | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26817 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General | Lack of sanitary equipment | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-05-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26818 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General | Lack of stickers on installations | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-05-18 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26819 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General ventillation | Transfer grill's are damaged | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-03-28 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26820 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General ventillation | Wall louvers need to be regulated | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26821 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Warehouse -4, warehouse-7 / ventillation | FN-0007 and FN-0008 are not conected to electrical instalation | C | EL | HEC EL Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-05-19 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26822 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Warehouse -4 / ventillation | FAN hanging need to be corrected | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26823 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General ventillation | Ventillation ducts need to be cleaned inside and outside | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26824 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General | Wall passes need to be done | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-04-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26825 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Room 17 and 18 / Sewage installation | Ceiling passe's need to be done (Sewage installation) | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-10 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26826 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Room 17 and 18 / ventillation | Duct's hangers need to be added | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26827 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Room 17 | Lack of sleeve's on wall passe's | A | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26828 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Hall / ventillation | Lack of earthning on heater (Hall) | C | EL | HEC EL Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-03-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26829 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Hall / ventillation | Fan's are not connected to electrical installation (Hall) | C | EL | HEC EL Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-05-04 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26830 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | 29 Main Workshop / ventillation | Corrosion on electric heater | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26831 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General | Hangers (ribbed bar) need to be cleaned | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-03-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26832 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General / Sewage installation | Lack of Sawage installation fire passes | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-16 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26833 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | room 12, 13, 27, 20 / Ventillation | Lack of intake louver | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-04-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26834 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General / Ventillation | Fire dumper actuator must be clened | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-04-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26835 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General | need to cleaning and repair isulation | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-05-08 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26836 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General AC | Uncompleted air conditioning unit ( | A | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-01-26 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26837 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | room 26 Ventillation | Fire dumper actuator need to be fixed | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26838 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | HVAC room 3 / PW | need to remove cut valve install before safety valve (x 2 ) | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-01 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26839 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General / AC | cable protection pipe for control panel need to be extended | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26840 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | room 1 | dameges on SAC and RL/RG tray cover damaged | A | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-01-30 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26841 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | ground floor, first floor | passes through the walls in the space of suspended celling need to be corrected | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-04-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26842 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Room 14 / Ventillation | damper located too close to the wall (no possible to operate) | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-07 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26843 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General / Ventillation | Lack of vent diffuser's | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-05-18 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26844 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Staircase / Ventillation | Duct limits the width of the escape route on staircase | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26845 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | dining room -11 | room was closed | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-05-08 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26846 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Room 10 / air condition | control panel is not straight mounted on the wall | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-01-18 | 2023-02-01 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26847 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General | No one room is finished. No possibility to check an accordance with drawing, specification, etc. The walkdown must be repeated. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26848 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Base floor | Cracks in the concrete slab must be repaired. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26849 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | Electric rooms | In electric rooms works of other branches are ongoing. Raised floor cannot be checked fully, it is damaged in some areas. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26850 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General | All openings must be filled/covered (with proper fireproofing where required). | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26851 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General | Expansion joints/gaps between columns or columns and walls must be properly finished. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-19 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26852 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General | The walkway around the building is not done. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-19 | 2023-05-12 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26853 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General | The facades must be homogeneously finished (painted), without patches. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-19 | 2023-06-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26854 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General | All facades, doors, windows etc. must be cleaned. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-19 | 2023-06-23 | Walkdown |  |  |  |  | V |  |  |  | RFC/RFSU
. | 26855 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | General | Satisfying physiological needs in rooms not adapted to it is unacceptable! Contaminated rooms must be disinfected and cleaned. | C | AR | HEC AR Construction | Mr. Sebastian Stępień | 2023-01-19 | 2023-05-12 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26919 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | (Normal, Emergency, Ecacuation & Exit) Lighting Fixtures, J/B installation, Cable pulling and termination to be done and official inspection to be carried out for ground floor and 1st floor | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-04-21 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26920 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Fire Alarm, Telcom & Paga devices to be installed , cable pulling and termination to be compete and official inpspection to be carried out for ground floor and 1st floor | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26921 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Overhead crane main line S/W box Tag and cable tag to be installed. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-04-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26922 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | HVAC fan cabinets earthing to be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-03-23 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26923 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Wall openings for cable trays fire sealing to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-05-05 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26924 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Roof fans Cable tray installation, cable pulling , termination and earthing works to be complete. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-04-03 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26925 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | illumination test to be done for workshop and office building for ground floor and 1st floor | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26926 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Earth resistance test to be performed and protocol to be submitted. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-05-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26927 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Small power socket outlets to be installed, cable pulling & cable terminations works to be complete for ground floor and 1st floor | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-04-11 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26928 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | General NCRs to be closed. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26929 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Cleaning under the raise floor inside Telecommunication room and Electrical room | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26930 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | 42-PDP-003,004,005 for panel support metal cover to be closed. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-04-12 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26931 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Electrical room raise floor water to be remove and cleaning to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26932 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | 21-PDP-005,001, 42-PDP-001,006,001, 21-NLP-001, 21-ELP-002 for panel support metal cover to be closed. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-04-12 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26933 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Verify the water leakage location and repair works to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26934 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Missing Lightfixture tags, JB tags, LTG Switch tags, Socket outlet tags to be provide for all rooms. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-04-17 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26935 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | 21-CBS-001, 42-CBS-001 Sat to be done. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 |  | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26936 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Housekeeping and cleaning in UPS room and battery room. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-04-12 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26937 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Cleaning to be done inside UPS (PCB, fans, filters..etc) & Batteries in battery room | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-04-18 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26938 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | 42-ELP-002, 42-ELP-001, 21-ELP-001 for panel support metal cover to be closed | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-04-12 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26939 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Canopy Lighting fixtures to be installed. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-03-27 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26940 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Staircase lighting fixtures to be installed. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-05-15 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 26941 | 800.00 | 1304-12-22 | Workshop with Office Building (1000-WS-42) | EGAT-HEC-900-ELE-DLP-01015,EGAT-HEC-1000-ELE-DGA-00003, DLP-04006, DLP-05004 | Lighting cable IR test to be done | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-01-18 | 2023-04-21 | Walkdown |  |  |  | SCAN CAT | V |  |  |  | RFC/RFSU
. | 31522 | 800.00 | 1304-12-22 | 1000-WS-42 | General | Touch-up painting on door(frame, leaf, hardware) inc. cleaning | C | AR | HEC AR Construction | Mr. Bartosz Skórzewski | 2023-04-28 | 2023-06-23 | PAC |  |  |  |  | V |  |  |  | RFC/RFSU
. | 31984 | 800.00 | 1304-12-22 | AUX | MCC Room | Remove the water and clean under the rised floor in MCC Room WS-42 . Then carry out works preventing the ingress of water. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2023-05-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32453 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 (Axis 10-11/A-D) | Coating (paint) damages due to construction work activities. All structure including miscellaneus structure. | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2023-06-21 |  | PAC | [8 empty] | RFC/RFSU
. | 32514 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 1 | Cracks and damages on plaster / Finishing nearby column / Finishing surface of floor by the wall / Regulation of raised floor | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32515 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 2 | Wall surface reuire touch up painting / Joints in wall shall be sealed / Skirting part of plaster need to be improved / Crack in joint needs to be repaired / Damages (done by installation) on wall surface need to be repaired / Touch up painting to be done / Construction profiles requisite adjustment / Panels require cleaning/replacement / Sealing/fireproof around installation openings shall be executed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32516 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 4 | Installation of skirting around door / Skirting to fix in corner - 2 pcs. | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32517 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 5 | Touch up painting to be done / Sealing, fireproof around installation openings shall be executed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32518 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 6 | Tiles required cleaning / Grout between wall and floor shall be cleaned / Touch up painting to be done / | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32519 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 7 | Crack in joint needs to be repaired / Finishing around door need to be done | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32520 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 9 | Clean out required proper installation and elevation / Fugue to be cleaned / Tiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32521 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 10 | Tiles required cleaning / Dirty fugue required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32522 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 11 | Painted walls required touch up / Tiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32523 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 15 | Skirting part of plaster need to be improved / Installation openings shall be improved / Plastering surface required improvement / Wall surface reuire touch up painting / Damages (done by installation) on wall surface need to be repaired / Joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32524 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 16 | Sealing / fireproof around installation openings shall be executed / Touch up painting to be done | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32525 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 17 | Installation openings shall be improved / Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32526 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 18 | Plastering surface required improvement / Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32527 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 19 | Installation openings shall be improved / Plastering surface required improvement (in edge) | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32528 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 21 | Plastering surface required improvement / Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32529 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 22 | Skirting part of plaster need to be improved / Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32530 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 23 | Damages of plaster / To clean under raised floor / Levelling of raised floor to fix / To fix installation holes on epoxy paint / To clean raised floor | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32531 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 25 | Finishing around door need to be done / Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32532 | 800.00 | 1304-12-22 | 1000-WS-42 | ROOM No. 34 | nstallation openings shall be improved / Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32533 | 800.00 | 1304-12-22 | 1000-WS-42 | Final inspection | 1000-WS-42. Missing Final Inspection for doors, windows, building, floor, walkway,flashing, suspended ceiling, cladding, paiting, canopy | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32534 | 800.00 | 1304-12-22 | 1000-WS-42 | General - Plinth | Plinth to be done | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32535 | 800.00 | 1304-12-22 | 1000-WS-42 | General - Tiles | Tiles and fouge cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32536 | 800.00 | 1304-12-22 | 1000-WS-42 | General - Facades | All facades, doors, windows etc. must be cleaned / Façade must be painted without patches | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32537 | 800.00 | 1304-12-22 | 1000-WS-42 | General - Doors | Rapair damage doors / finishing around doors / touch up painting on door | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-06-22 |  | PAC | [8 empty] | RFC/RFSU
. | 32593 | 800.00 | 1304-12-22 | workshop with office building |  | fault of PDIS-X0001 | C | HV | HEC HV Construction | Mr. Karol Pytel | 2023-06-16 |  | PAC | [8 empty] | RFC/RFSU
. | 32594 | 800.00 | 1304-12-22 | workshop with office building |  | fault of 1000-TGD-8201 shows negative value | C | HV | HEC HV Construction | Mr. Karol Pytel | 2023-06-16 |  | PAC | [8 empty] | RFC/RFSU
. | 32597 | 800.00 | 1304-12-22 | workshop with office building |  | fault of ACCU (1000-WS42-ACCU-0006A) ice on service valves | C | HV | HEC HV Construction | Mr. Karol Pytel | 2023-06-16 |  | PAC | [8 empty] | RFC/RFSU
. | EGAT-RFI-AR-UB-01647.01 | 800.00 | 1304-12-22 | 1000-WS-42 | - | To be attach Survey report | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2021-03-22 | 2021-09-15 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-01647.01 | C-AR-UB-00100 |  | Construction
. | EGAT-RFI-AR-UB-01647.02 | 800.00 | 1304-12-22 | 1000-WS-42 | - | To be attach compaction test report | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2021-03-22 | 2021-09-15 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-01647.02 | C-AR-UB-00100 |  | Construction
. | EGAT-RFI-AR-UB-05045.01 | 800.00 | 1304-12-22 | 1000-WS-42 | UPS Room No. 1 | Regulation of raised floor | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-20 | 2023-06-23 | Construction | 2022-04-20 |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05045 |  |  | Construction
. | EGAT-RFI-AR-UB-05045.02 | 800.00 | 1304-12-22 | 1000-WS-42 | UPS Room No. 1 | Skirting has to be installed | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-20 | 2023-04-06 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-AR-UB-05045 |  |  | Construction
. | EGAT-RFI-AR-UB-05045.03 | 800.00 | 1304-12-22 | 1000-WS-42 | UPS Room No. 1 | Finishing surface of floor by the wall | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-20 | 2023-06-23 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-AR-UB-05045 |  |  | Construction
. | EGAT-RFI-AR-UB-05047.01 | 800.00 | 1304-12-22 | 1000-WS-42 | UPS Room No. 1 | Cracks/damages on plaster | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-20 | 2023-06-23 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-AR-UB-05047 |  |  | Construction
. | EGAT-RFI-AR-UB-05047.02 | 800.00 | 1304-12-22 | 1000-WS-42 | UPS Room No. 1 | Finishing of plaster | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-20 | 2023-06-05 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-AR-UB-05047 |  |  | Construction
. | EGAT-RFI-AR-UB-05047.03 | 800.00 | 1304-12-22 | 1000-WS-42 | UPS Room No. 1 | Finishing nearby column | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-04-20 | 2023-06-23 | Construction | 2022-04-20 |  |  |  | V | EGAT-RFI-AR-UB-05047 |  |  | Construction
. | EGAT-RFI-AR-UB-05109.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 23 | Damages of plaster | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-07 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05109 |  |  | Construction
. | EGAT-RFI-AR-UB-05109.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 23 | Finishing of plaster | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-07 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05109 |  |  | Construction
. | EGAT-RFI-AR-UB-05109.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 23 | Dilatation joints to do | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-07 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05109 |  |  | Construction
. | EGAT-RFI-AR-UB-05110.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 23 | To fix installation holes on epoxy paint | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-07 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05110 |  |  | Construction
. | EGAT-RFI-AR-UB-05110.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 23 | To clean under raised floor | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-07 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05110 |  |  | Construction
. | EGAT-RFI-AR-UB-05110.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 23 | To clean raised floor | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-07 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05110 |  |  | Construction
. | EGAT-RFI-AR-UB-05110.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 23 | Levelling of raised floor to fix | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-07 | 2023-06-23 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05110 |  |  | Construction
. | EGAT-RFI-AR-UB-05110.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 23 | Skirting to do | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-06-07 | 2023-04-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05110 |  |  | Construction
. | EGAT-RFI-AR-UB-05167.01 | 800.00 | 1304-12-22 | 1000-WS-42 | General | Facade to clean | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-05-30 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05167 |  |  | Construction
. | EGAT-RFI-AR-UB-05167.02 | 800.00 | 1304-12-22 | 1000-WS-42 | General | Facade plinth to be done | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-05-30 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05167 |  |  | Construction
. | EGAT-RFI-AR-UB-05444.01 | 800.00 | 1304-12-22 | 1000-WS-42 | General | Corners to install | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-08-10 | 2023-02-15 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05444 |  |  | Construction
. | EGAT-RFI-AR-UB-05444.02 | 800.00 | 1304-12-22 | 1000-WS-42 | General | To clean plastering | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-08-10 | 2023-02-15 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05444 |  |  | Construction
. | EGAT-RFI-AR-UB-05444.03 | 800.00 | 1304-12-22 | 1000-WS-42 | General | To finish top and side part of plastering | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-08-10 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05444 |  |  | Construction
. | EGAT-RFI-AR-UB-05444.04 | 800.00 | 1304-12-22 | 1000-WS-42 | General | To fix scratches | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-08-10 | 2022-12-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05444 |  |  | Construction
. | EGAT-RFI-AR-UB-05482.01 | 800.00 | 1304-12-22 | 1000-WS-42 | - | To fix around canopy | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-26 | 2022-12-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05482 |  |  | Construction
. | EGAT-RFI-AR-UB-05482.02 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Dilatation to fix | B | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-26 | 2022-12-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05482 |  |  | Construction
. | EGAT-RFI-AR-UB-05482.03 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Plinth to be done | C | AR | HEC AR Construction | Mr. Maciej Rudnicki | 2022-10-26 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05482 |  |  | Construction
. | EGAT-RFI-AR-UB-05514.01 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Wet surface | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-16 | 2023-04-28 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05514 |  |  | Construction
. | EGAT-RFI-AR-UB-05514.02 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Lack of flashing on top side of plastering | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-16 | 2023-04-28 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05514 |  |  | Construction
. | EGAT-RFI-AR-UB-05642.01 | 800.00 | 1304-12-22 | 1000-WS-42 | General | To install skirting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-13 | 2022-12-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05642 |  |  | Construction
. | EGAT-RFI-AR-UB-05686.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 24 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05686 |  |  | Construction
. | EGAT-RFI-AR-UB-05686.02 | 800.00 | 1304-12-22 | 1000-WS-42 | General | To clean door leaf/ frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05686 |  |  | Construction
. | EGAT-RFI-AR-UB-05686.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 25 | Scratches on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05686 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 80 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 79 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 78 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 77 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 76 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 75 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.07 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 74 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.08 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 89E | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.09 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 89W | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.10 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 66 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.11 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 67 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.12 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 68 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.13 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 65 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.14 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 64 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.15 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 59 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.16 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 54 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.17 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 53 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.18 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 52 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.19 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 55 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.20 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 57 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.21 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 70 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.22 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 58 | Scratches on door frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.23 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 80 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.24 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 79 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.25 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 78 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.26 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 75 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.27 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 74 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.28 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 89E | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.29 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 67 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.30 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 68 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.31 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 65 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.32 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 64 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.33 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 63 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.34 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 62 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.35 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 61 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.36 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 54 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.37 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 58 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.38 | 800.00 | 1304-12-22 | 1000-WS-42 | General | Cleaning | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.39 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 77 | To regulate door | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.40 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 75 | Foil on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.41 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 66 | Lack of door closer | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-11-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.42 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 67 | Lack of door closer | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-12-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.43 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 68 | Lack of door closer | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2022-12-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05717.44 | 800.00 | 1304-12-22 | 1000-WS-42 | Door No. 58 | Hinge to fix | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-25 | 2023-04-28 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05717 |  |  | Construction
. | EGAT-RFI-AR-UB-05719.01 | 800.00 | 1304-12-22 | 1000-WS-42 | General | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-10-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05719 |  |  | Construction
. | EGAT-RFI-AR-UB-05719.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82/90 | Acryl | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-10-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05719 |  |  | Construction
. | EGAT-RFI-AR-UB-05719.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Axis 5B | Dilatation to fix | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2023-04-28 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05719 |  |  | Construction
. | EGAT-RFI-AR-UB-05719.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Axis B/4 | Dilatation to fix | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2023-04-28 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05719 |  |  | Construction
. | EGAT-RFI-AR-UB-05724.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 80 | Silicone nearby window | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-10-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05724 |  |  | Construction
. | EGAT-RFI-AR-UB-05724.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 80 | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-10-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05724 |  |  | Construction
. | EGAT-RFI-AR-UB-05724.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 88 | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-10-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05724 |  |  | Construction
. | EGAT-RFI-AR-UB-05724.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 58 | Dilatation joint | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-12-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05724 |  |  | Construction
. | EGAT-RFI-AR-UB-05724.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 58 | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-10-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05724 |  |  | Construction
. | EGAT-RFI-AR-UB-05724.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82 | Acryl finishing | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-10-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05724 |  |  | Construction
. | EGAT-RFI-AR-UB-05724.07 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82 | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-10-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05724 |  |  | Construction
. | EGAT-RFI-AR-UB-05724.08 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 91 | Touch-up painting | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-10-21 | 2022-10-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05724 |  |  | Construction
. | EGAT-RFI-AR-UB-05847.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 84 | Fugue finishing | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-11-29 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05847 |  |  | Construction
. | EGAT-RFI-AR-UB-05847.02 | 800.00 | 1304-12-22 | 1000-WS-42 | General | Tiles and fugue cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-11-29 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05847 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.01 | 800.00 | 1304-12-22 | 1000-WS-42 | General | Cleaning | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 87/90 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 87 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 88W | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 88E | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 90 Axis 3 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.07 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 81 | Scratch on door leaf | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.08 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 87/90 | Scratch on frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.09 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 87 | Scratch on frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.10 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 88W | Scratch on frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.11 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 88E | Scratch on frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.12 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 90 Axis 3 | Scratch on frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.13 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 90 Axis 6 | Scratch on frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.14 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 81 | Scratch on frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.15 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 91 | Scratch on frame | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.16 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 87/90 | Doors regulation | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2023-03-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05848.17 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 90 Axis 6 | To verificate fireproof El60 | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-11-29 | 2022-12-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05848 |  |  | Construction
. | EGAT-RFI-AR-UB-05866.01 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Tiles to reinstall - 4 pcs. | B | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-02 | 2022-12-22 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05849 |  |  | Construction
. | EGAT-RFI-AR-UB-05877.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 66 | To install lights | C | EL | HEC EL Construction | Piotr Zygmunt | 2022-12-08 | 2023-04-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05877 |  |  | Construction
. | EGAT-RFI-AR-UB-05877.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 65 | To install lights | C | EL | HEC EL Construction | Piotr Zygmunt | 2022-12-08 | 2023-04-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05877 |  |  | Construction
. | EGAT-RFI-AR-UB-05877.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 65 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-08 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05877 |  |  | Construction
. | EGAT-RFI-AR-UB-05877.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 62 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-08 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05877 |  |  | Construction
. | EGAT-RFI-AR-UB-05877.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 60 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-08 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05877 |  |  | Construction
. | EGAT-RFI-AR-UB-05877.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 63 | Wall profile to fix nearby window | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-08 | 2022-12-20 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05877 |  |  | Construction
. | EGAT-RFI-AR-UB-05877.07 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 62 | Wall profile to fix nearby window | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-08 | 2022-12-20 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05877 |  |  | Construction
. | EGAT-RFI-AR-UB-05877.08 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 61 | Alignment of profile - corner nearby window | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-08 | 2022-12-20 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05877 |  |  | Construction
. | EGAT-RFI-AR-UB-05887.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 59 | To remove tapes | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-19 | 2021-03-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05887 |  |  | Construction
. | EGAT-RFI-AR-UB-05887.02 | 800.00 | 1304-12-22 | 1000-WS-42 | General | Lamps to install | C | EL | HEC EL Construction | Piotr Zygmunt | 2022-12-19 | 2023-04-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05887 |  |  | Construction
. | EGAT-RFI-AR-UB-05887.03 | 800.00 | 1304-12-22 | 1000-WS-42 | General | HV equipment to adjustment | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-19 | 2023-01-27 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05887 |  |  | Construction
. | EGAT-RFI-AR-UB-05888.01 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Finishing around doors | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-19 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05888 |  |  | Construction
. | EGAT-RFI-AR-UB-05889.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 66 | Dirty panel - 3 pcs. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-21 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05889 |  |  | Construction
. | EGAT-RFI-AR-UB-05889.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 65 | Dirty panel - 2 pcs. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-21 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05889 |  |  | Construction
. | EGAT-RFI-AR-UB-05889.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 62 | Dirty panel - 2 pcs. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-21 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05889 |  |  | Construction
. | EGAT-RFI-AR-UB-05889.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 61 | Dirty panel - 1 pcs. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-21 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05889 |  |  | Construction
. | EGAT-RFI-AR-UB-05889.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 60 | Dirty panel - 1 pcs. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-21 |  | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05889 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.01 | 800.00 | 1304-12-22 | 1000-WS-42 | General | Lack of lamps | C | EL | HEC EL Construction | Piotr Zygmunt | 2022-12-21 | 2023-04-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 56 | Profiles nearby HV equipment to fix | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-21 | 2022-12-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 56 | To install panels - 4 pcs. | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-21 | 2022-12-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 56 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-21 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 69 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-21 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 70 | To remove tapes | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-21 | 2022-12-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.07 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 70 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-21 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.08 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 71 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-21 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.09 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 71 | Panels to regulate around HV equipment - 4 pcs. | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-21 | 2022-12-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.10 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 74 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-21 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.11 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 74 | Panels to regulate around HV equipment - 2 pcs. | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-21 | 2022-12-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.12 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 75 | To remove tapes | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-21 | 2022-12-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.13 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 75 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-21 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.14 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 76 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-21 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.15 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 77 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-21 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.16 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 77 | Panels/ profiles to regulate around HV equipment | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-21 | 2022-12-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.17 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 78 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-21 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05893.18 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 79 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-21 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05893 |  |  | Construction
. | EGAT-RFI-AR-UB-05894.01 | 800.00 | 1304-12-22 | 1000-WS-42 | General | Skirting to fix in corner - 2 pcs. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-21 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05894 |  |  | Construction
. | EGAT-RFI-AR-UB-05894.02 | 800.00 | 1304-12-22 | 1000-WS-42 | General | Installation of skirting around door | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-12-21 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05894 |  |  | Construction
. | EGAT-RFI-AR-UB-05895.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 68 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-21 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05895 |  |  | Construction
. | EGAT-RFI-AR-UB-05895.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 68 | Lamps to install | C | EL | HEC EL Construction | Piotr Zygmunt | 2022-12-21 | 2023-04-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05895 |  |  | Construction
. | EGAT-RFI-AR-UB-05895.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 68 | Profiles nearby columns to install | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-21 | 2023-05-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05895 |  |  | Construction
. | EGAT-RFI-AR-UB-05895.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 67 | To regulate profile on N side | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-21 | 2023-04-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05895 |  |  | Construction
. | EGAT-RFI-AR-UB-05895.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 67 | To regulate profile around column | C | AR | HEC AR Construction | Piotr Zygmunt | 2022-12-21 | 2023-05-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05895 |  |  | Construction
. | EGAT-RFI-AR-UB-05895.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 67 | HV equipment to regulate | C | HV | HEC HV Construction | Piotr Zygmunt | 2022-12-21 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05895 |  |  | Construction
. | EGAT-RFI-AR-UB-05895.07 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 67 | Lamps to install | C | EL | HEC EL Construction | Piotr Zygmunt | 2022-12-21 | 2023-04-04 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05895 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 55 | Panels need to be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 55 | Panels need to be aligned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 55 | Corner of suspended ceiling profile need to be aligned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 56 | Panels need to be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 56 | Suspended ceiling profile need to be aligned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 57 | Suspended ceiling profile need to be aligned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.07 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 57 | Suspended ceiling profiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.08 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 57 | Connection between walls and profiles need to be sealed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.09 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 68 | Panels need to be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.10 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 68 | Suspended ceiling profiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.11 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 69 | Panels need to be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.12 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 69 | Suspended ceiling profiles need to be aligned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.13 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 70 | Suspended ceiling profiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.14 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 70 | Connection between walls and profiles need to be sealed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.15 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 71 | Suspended ceiling profiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.16 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 71 | Connection between walls and profiles need to be sealed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.17 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 74 | Suspended ceiling profiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.18 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 74 | Connection between walls and profiles need to be sealed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.19 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 75 | Suspended ceiling profiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.20 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 75 | Connection between walls and profiles need to be sealed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.21 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 75 | panels need to be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.22 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 76 | Suspended ceiling profiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.23 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 76 | Connection between walls and profiles need to be sealed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.24 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 76 | Profiles around column need to be installed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.25 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 77 | Panels need to be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.26 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 77 | Suspended ceiling profiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.27 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 77 | Connection between walls and profiles need to be sealed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.28 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 77 | Profiles around column need to be installed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.29 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 77 | Suspended ceiling profile need to be aligned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.30 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 78 | Panels need to be replaced | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.31 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 78 | Suspended ceiling profiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.32 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 78 | Connection between walls and profiles need to be sealed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05900.33 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 78 | Suspended ceiling profile need to be aligned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05900 |  |  | Construction
. | EGAT-RFI-AR-UB-05901.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 86 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05901 |  |  | Construction
. | EGAT-RFI-AR-UB-05901.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 86 | Refill the grout | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05901 |  |  | Construction
. | EGAT-RFI-AR-UB-05901.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 86 | Connection between door threshold and tile need to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05901 |  |  | Construction
. | EGAT-RFI-AR-UB-05901.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 87 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05901 |  |  | Construction
. | EGAT-RFI-AR-UB-05901.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 87 | Connection between door threshold and tile need to be finished | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05901 |  |  | Construction
. | EGAT-RFI-AR-UB-05901.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 87 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05901 |  |  | Construction
. | EGAT-RFI-AR-UB-05902.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 6 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05902 |  |  | Construction
. | EGAT-RFI-AR-UB-05902.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 6 | Grout between wall and floor shall be cleaned | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05902 |  |  | Construction
. | EGAT-RFI-AR-UB-05902.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 6 | Location of electrical outlets for water heaters need to be verified | C | EL | HEC EL Construction | Mr. Andrzej Misiek | 2023-01-05 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05902 |  |  | Construction
. | EGAT-RFI-AR-UB-05902.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 6 | Location of water connections needs to be verified | C | HV | HEC HV Construction | Mr. Andrzej Misiek | 2023-01-05 | 2023-04-11 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-AR-UB-05902 |  |  | Construction
. | EGAT-RFI-AR-UB-05908.01 | 800.00 | 1304-12-22 | 1000-WS-42 | General | Clean out required proper installation elevation | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-23 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05908 |  |  | Construction
. | EGAT-RFI-AR-UB-05909.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 81 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-01-14 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05909 |  |  | Construction
. | EGAT-RFI-AR-UB-05922.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 11 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-01-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05922 |  |  | Construction
. | EGAT-RFI-AR-UB-05922.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 11 | Tiles on floor need to be replaced - 1 pcs. | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-01-18 | 2023-03-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05922 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 9 | Door stop required installation | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-05-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 9 | Door need to be cleand | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 9 | Touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 9 | Doors required cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No.10.1 | Scratches on door hardware | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No.10.1 | Touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.07 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No.10.1 | Threshold installation need to be improved | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-03-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.08 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No.10.1 | Doors required cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.09 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 10.2 | Threshold installation need to be improved | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-03-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.10 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 10.2 | Doors required cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.11 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 11 | Touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.12 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 11 | Doors required cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.13 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 11 | Threshold installation need to be improved | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.14 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 11 | Scratches on door hardware | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.15 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 11 | Door leaf regulation | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-03-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.16 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 24 | Threshold installation need to be improved | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-03-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.17 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 24 | Doors required cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.18 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 24 | Door stop required installation | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-03-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.19 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 24 | Gasket need to be assembly | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.20 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 25 | Threshold installation need to be improved | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-03-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.21 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 25 | Doors required cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.22 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 25 | Door stop required installation | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-03-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.23 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 26 | Doors required cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.24 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 26 | Threshold installation need to be improved | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.25 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 26 | Door closer need to be montaged | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-03-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.26 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 27 | Threshold installation need to be improved | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05927.27 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 27 | Doors required cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-20 | 2023-04-18 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05927 |  |  | Construction
. | EGAT-RFI-AR-UB-05928.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 9 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-27 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05928 |  |  | Construction
. | EGAT-RFI-AR-UB-05928.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 9 | Clean out required proper installation/ elevation | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-27 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05928 |  |  | Construction
. | EGAT-RFI-AR-UB-05928.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 9 | Fugue to be cleaned | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-27 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05928 |  |  | Construction
. | EGAT-RFI-AR-UB-05929.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-27 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05929 |  |  | Construction
. | EGAT-RFI-AR-UB-05929.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82 | Skirting part of tiles need to be improved | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-27 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05929 |  |  | Construction
. | EGAT-RFI-AR-UB-05929.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82 | Dirty fugue required cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-27 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05929 |  |  | Construction
. | EGAT-RFI-AR-UB-05939.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 10 | Tiles required cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-27 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05939 |  |  | Construction
. | EGAT-RFI-AR-UB-05939.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 10 | Dirty fugue required cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-01-27 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05939 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82 | Panels required cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82 | Profiles shall be aligned/ cut with circumferential profiles | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82 | Sealant with wall and circumferential profile need to be done | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82 | Hangers need to be tightened | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 89 | Profiles around wall need to be cleaned | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 91 | Sealant with wall and circumferential profil need to be done | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-04-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.07 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 91 | Profiles shall be aligned/cut with circumferential profiles | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.08 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 58 | Panels required cleaning | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-04-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.09 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 58 | Sealant with wall and circumferential profil need to be done | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.10 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 58 | Hangers need to be tightened | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.11 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 58 | Remove tape from wall profile | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.12 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 58 | Circumferential profiles shall be aligned | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.13 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 90 | Sealant with wall and circumferential profil need to be done | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.14 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 90 | Profiles shall be aligned/cut with circumferential profiles | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05952.15 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 90 | Complete missing profiles | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-01-30 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05952 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 20 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 |  | Construction |  | Changed from Cat. B |  |  |  | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 21 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-15 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 21 | Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 22 | Skirting part of plaster need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 22 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-15 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 24 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-09 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.07 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 25 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-15 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.08 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 25 | Finishing around door need to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-15 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.09 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 26 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.10 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 27 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-15 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.11 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 2 | Crack in joint needs to be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.12 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 2 | Skirting part of plaster need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.13 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 7 | Skirting part of plaster need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.14 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 7 | Crack in joint needs to be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-19 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.15 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 7 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.16 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 7 | Finishing around door need to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-19 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.17 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 8 | Skirting part of plaster need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.18 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 12 | Finishing around door need to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.19 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 12 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.20 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 12 | Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.21 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 18 | Finishing around door need to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.22 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 18 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-15 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.23 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 18 | Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.24 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 17 | Finishing around door need to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.25 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 17 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-15 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.26 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 17 | Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.27 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 19 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-19 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.28 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 19 | Finishing around door need to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-04-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.29 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 19 | Crack in joint need to be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-04-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.30 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 19 | Plastering surface required improvement (in edge) | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-15 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.31 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 14 | not finished | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-03-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.32 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 15 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.33 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 15 | Skirting part of plaster need to be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.34 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 15 | Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-23 | Construction | [5 empty] | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.35 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 13 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.36 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 13 | Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.37 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 13 | Finishing around door need to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.38 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 30 | Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-04-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.39 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 30 | Crack in joint need to be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-03-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.40 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 31 | Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-04-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.41 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 32 | Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-04-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.42 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 33 | Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-03-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.43 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 34 | Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.44 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 35 | Finishing around door need to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-04-06 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.45 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 34 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.46 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 36 | Installation openings shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 |  | Construction | [5 empty] | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05955.47 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 36 | Plastering surface required improvement | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-03-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05955 |  |  | Construction
. | EGAT-RFI-AR-UB-05959.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82 | Panels required cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05959 |  |  | Construction
. | EGAT-RFI-AR-UB-05959.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82 | Profiles shall be aligned/cut with circumferential profiles | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2023-03-10 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05959 |  |  | Construction
. | EGAT-RFI-AR-UB-05959.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82 | Sealant with wall and circumferential profil need to be done | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2023-03-10 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05959 |  |  | Construction
. | EGAT-RFI-AR-UB-05959.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 82 | Hangers need to be tightened | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2023-03-10 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05959 |  |  | Construction
. | EGAT-RFI-AR-UB-05959.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 91 | Sealant with wall and circumferential profil need to be done | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05959 |  |  | Construction
. | EGAT-RFI-AR-UB-05959.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 58 | Panels required cleaning | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2023-05-30 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05959 |  |  | Construction
. | EGAT-RFI-AR-UB-05959.07 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 58 | Sealant with wall and circumferential profil need to be done | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2022-03-10 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05959 |  |  | Construction
. | EGAT-RFI-AR-UB-05959.08 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 58 | Hangers need to be tightened | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2023-03-10 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05959 |  |  | Construction
. | EGAT-RFI-AR-UB-05959.09 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 58 | Remove tape from wall profile | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2023-03-10 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05959 |  |  | Construction
. | EGAT-RFI-AR-UB-05959.10 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 58 | Circumferential profiles shall be aligned | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2023-03-10 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05959 |  |  | Construction
. | EGAT-RFI-AR-UB-05959.11 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 90 | Sealant with wall and circumferential profil need to be done | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2023-03-10 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05959 |  |  | Construction
. | EGAT-RFI-AR-UB-05959.12 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 90 | Profiles shall be aligned/cut with circumferential profiles | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2023-03-29 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05959 |  |  | Construction
. | EGAT-RFI-AR-UB-05959.13 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 90 | Complete missing panels | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-02 | 2023-06-05 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05959 |  |  | Construction
. | EGAT-RFI-AR-UB-05965.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 84 | Sealant between wall and suspended ceiling shall be done | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-02-01 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05965 |  |  | Construction
. | EGAT-RFI-AR-UB-05966.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 84, 92 | Steel hangers shall be cut in the end of rod | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 | 2023-03-10 | Construction |  | Changed from Cat. B |  |  | V | EGAT-RFI-AR-UB-05966 |  |  | Construction
. | EGAT-RFI-AR-UB-05966.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 84, 92 | Lighting fixtures not mounted | C | EL | HEC EL Construction | Mr. Slawomir Nasilowski | 2023-02-11 | 2023-04-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05966 |  |  | Construction
. | EGAT-RFI-AR-UB-05984.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 3 | Remove tape from profiles | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-10 | 2023-03-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05984 |  |  | Construction
. | EGAT-RFI-AR-UB-05984.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 4 | Corner of suspended ceiling shall be improved | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-10 | 2023-03-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05984 |  |  | Construction
. | EGAT-RFI-AR-UB-05986.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 11 | Remove tape from profiles | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-02-08 | 2023-05-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05986 |  |  | Construction
. | EGAT-RFI-AR-UB-05987.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 11 | Remove tape from profiles | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-11 | 2023-03-10 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05987 |  |  | Construction
. | EGAT-RFI-AR-UB-05990.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 59 | Joints shall be covered with sealant | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-02-08 | 2023-04-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05990 |  |  | Construction
. | EGAT-RFI-AR-UB-05990.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 85 | Joints shall be covered with sealant | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-02-08 | 2023-04-25 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05990 |  |  | Construction
. | EGAT-RFI-AR-UB-05990.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 6 | Surface required touch up painting | C | AR | HEC AR Construction | Piotr Malczewski | 2023-02-08 | 2023-06-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05990 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 4 | Joints in walls shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 4 | Touch up painting to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 6 | Lighting shall be installed | C | EL | HEC EL Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-21 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 6 | Joints in walls shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 6 | Touch up painting to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 6 | Finishing around HVAC heaters to be done | C | HV | HEC HV Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-03-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.07 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 6 | Cracks required reparation | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.08 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 59 | Joints in walls shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.09 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 81 | Joints in walls shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.10 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 81 | Lighting shall be installed | C | EL | HEC EL Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.11 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 81 | Finishing around HVAC heaters to be done | C | HV | HEC HV Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-03-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.12 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 81 | Touch up painting to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.13 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 85 | Joints in walls shall be sealed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.14 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 85 | Lighting shall be installed | C | EL | HEC EL Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.15 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 86 | Lighting shall be installed | C | EL | HEC EL Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.16 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 87 | Lighting shall be installed | C | EL | HEC EL Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-04-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-05998.17 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 87 | Touch up painting to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-18 | 2023-05-30 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-05998 |  |  | Construction
. | EGAT-RFI-AR-UB-06002.01 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Steel hangers need to be tighten | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-02-14 | 2023-02-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-06002 |  |  | Construction
. | EGAT-RFI-AR-UB-06002.02 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Sealant around profiles to be done | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-02-14 | 2023-02-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-06002 |  |  | Construction
. | EGAT-RFI-AR-UB-06002.03 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Panels required replacement | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-02-14 | 2023-02-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-06002 |  |  | Construction
. | EGAT-RFI-AR-UB-06002.04 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Profiles in corner shall be renewed | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-02-14 | 2023-02-17 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-06002 |  |  | Construction
. | EGAT-RFI-AR-UB-06003.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 11 | Painted walls required touch up | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-16 | 2023-06-23 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-06003 |  |  | Construction
. | EGAT-RFI-AR-UB-06004.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 51 | Surface elevation deviation up to 2,0 cm required reparation | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-21 | 2023-06-05 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-06004 |  |  | Construction
. | EGAT-RFI-AR-UB-06010.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 29 | Painted walls required touch up | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-02-15 | 2023-05-24 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-06010 |  |  | Construction
. | EGAT-RFI-AR-UB-06011.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 15 | Surface elevation deviation up to 2,5 cm required reparation | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-02-18 | 2023-03-20 | Construction | [5 empty] | EGAT-RFI-AR-UB-06011 |  |  | Construction
. | EGAT-RFI-AR-UB-06016.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 9 | Sealant shall be installed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-21 | 2023-06-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-06016 |  |  | Construction
. | EGAT-RFI-AR-UB-06016.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 10 | Sealant shall be installed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-02-21 | 2023-06-09 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-06016 |  |  | Construction
. | EGAT-RFI-AR-UB-06023.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 6 | Fastening of partition wall require improvement | C | AR | HEC AR Construction | Mr. Sławomir Nasiłowski | 2023-02-24 | 2023-03-29 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-06023 |  |  | Construction
. | EGAT-RFI-AR-UB-06028.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 5 | Surface elevation deviation up to 1,5 cm required reparation | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-02-24 | 2023-03-20 | Construction |  |  |  |  | V | EGAT-RFI-AR-UB-06028 |  |  | Construction
. | EGAT-RFI-AR-UB-06036.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 2 | Missing suspended ceiling panels shall be installed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-03-02 | 2023-06-09 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06036.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 2 | Panels require cleaning/replacement | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-03-02 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06036.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 2 | Construction profiles requisite adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-03-02 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06038.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 2 | Joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-03-06 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06038.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 2 | Wall surface reuire touch up painting | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-03-06 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06038.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 2 | Damages (done by installation) on wall surface need to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-03-06 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06038.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No.15 | Joints in wall shall be sealed | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-03-06 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06038.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No.15 | Wall surface reuire touch up painting | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-03-06 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06038.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No.15 | Damages (done by installation) on wall surface need to be repaired | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-03-06 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06044.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 74, 75, 75, 77, 78, 79, 80, 68, 67 | Floor surface to be cleaning | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-06 | 2023-06-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06044.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 74, 75, 76, 77, 78, 79, 80 | Joints between installed PVC panels shall be fulfilled | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-06 | 2023-06-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06044.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 68 | Skirting part shall be improved | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-06 | 2023-06-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06045.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 81 | Scratches on mirror need to be repaired | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-24 | 2023-06-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06045.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 86 | Selant shall be removed from mirror | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-24 | 2023-06-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06048.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 2 | Touch up painting to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-07 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06048.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 5 | Touch up painting to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-07 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06048.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 16 | Touch up painting to be done | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-07 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06048.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 2 | Sealing/fireproof around installation openings shall be executed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-07 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06048.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 5 | Sealing/fireproof around installation openings shall be executed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-07 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06048.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Room No. 16 | Sealing/fireproof around installation openings shall be executed | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-03-07 | 2023-06-23 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06049.01 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Tie bars shall be tightened/suspened ceiling adjustment | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-06 | 2023-06-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06049.02 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Complete the suspended ceiling panels | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-06 | 2023-06-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06049.03 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Install lighting on suspended ceiling | C | AR | HEC AR Construction | Mr. Andrzej Misiek | 2023-04-06 | 2023-06-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.01 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 12 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.02 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 13 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.03 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 14 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.04 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 17 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.05 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 18 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.06 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 19 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.07 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 24 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.08 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 25 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.09 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 26 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.10 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 27 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.11 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 30 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.12 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 31 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.13 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 32 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.14 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 33 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.15 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 34 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.16 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 35 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06054.17 | 800.00 | 1304-12-22 | 1304-12-22 | Room No. 36 | Wall surface require touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-09 | 2023-05-15 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06056.01 | 800.00 | 1304-12-22 | 1000-WS-42 | A-D/12 | Touch up painting | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-14 | 2023-04-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06056.02 | 800.00 | 1304-12-22 | 1000-WS-42 | A-D/12 | Fastening the anchoring require improvement | D | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-14 | 2023-04-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06056.03 | 800.00 | 1304-12-22 | 1000-WS-42 | A-D/12 | Gate concrete sills shall be finished | C | AR | HEC AR Construction | Paweł Zygmunt | 2023-03-14 | 2023-04-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06099.01 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Skirting at the corners to be corrected | C | AR | HEC AR Construction | Mr. Bartosz Krzywulski | 2023-04-03 | 2023-04-28 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-AR-UB-06114.01 | 800.00 | 1304-12-22 | 1000-WS-42 | - | Cleaning | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2023-04-28 | 2023-06-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-01731.01 | 800.00 | 1304-12-22 | PP Area | Beacon and Sounder (15ea) | Yellow labelling with black fonts to be provide with description in polish language attention gas | C | CI | CW Construction | Mr. Adam Zbroja | 2022-07-05 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04866.01 | 800.00 | 1304-12-22 | Work shop office building first floor PP Area | 1000-GB-8403 | Fire stop need to be done & provide sticker | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-12-28 | 2023-01-17 | Construction |  |  | 2023-01-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04866.02 | 800.00 | 1304-12-22 | Work shop office building first floor PP Area | 1000-GB-8205,1000-GB-8201,1000-GB-8202,1000-GB-8204 | surface square box sealant need to be provide | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-12-28 | 2023-01-17 | Construction |  |  | 2023-01-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04877.01 | 800.00 | 1304-12-22 | PP AREA | FOR ALL TAG | Cleaning need to be done (36EA) | C | CI | CW Construction | Mr. Paweł Rogoziński | 2022-12-28 | 2023-03-03 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-04877.02 | 800.00 | 1304-12-22 | PP AREA | EGAT-HEC-300-INC-DWG-00007_Z0 | Gas detector wiring layout to be revise | C | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-12-28 | 2023-04-03 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-05186.01 | 800.00 | 1304-12-22 | PDH AREA | 1000-HS-8201A/T | Grounding need to provide | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-12-28 | 2023-01-17 | Construction |  |  | 2023-01-17 |  | V |  |  |  | Construction
. | EGAT-RFI-CI-CW-05186.02 | 800.00 | 1304-12-22 | PDH AREA | 1000-HS-8201A/T | Rubber separator between handswitch and galvanized plate need to provide | B | CI | HEC CI Construction | Mr. Paweł Rogoziński | 2022-12-28 | 2023-01-17 | Construction |  |  | 2023-01-17 |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02357.01 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-900-ELE-DLP-03022_0 | Earthing connection should be provided for cable tray | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-04 | 2023-04-21 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02532.01 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-DGA-00003_2 | AC UPS Panel screw cover should be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-05-09 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02532.02 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-DGA-00003_2 | Panel back cover need to touch-up paint. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-05-09 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02532.03 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-DGA-00003_2 | Door lock should be closed properly | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-04-28 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02532.04 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-DGA-00003_2 | BMS need to be touch-up paint | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 | 2023-04-11 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02532.05 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-DGA-00003_2 | After completion of construction works (roof, walls), the vendor's position should be presented, confirming that the devices are not damaged | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-18 |  | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-02581.01 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-900-ELE-DLP-03022 | Earthing connection should be provided for cable tray | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-05-30 | 2023-05-09 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03323.01 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-DGA-00003_0 | Earthing connection should be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-07-15 | 2023-04-21 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03750.01 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-DGA-00003_0 | Internal earthing should be provided in NLP, ELP & PDP Panel (21-NLP-001, 21-PDP-001, 003, 004, 005, 006 & 21-ELP-001) | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-11 | 2023-03-24 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03754.01 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-900-ELE-DLP-01015, EGAT-HEC-400-ELE-DLP-05001_3 | Conduit coupling should be provide the tape. | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-10 | 2023-05-09 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-03755.01 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-400-ELE-DLP-05001_3 | Street light cable tag should be provided | C | EL | HEC EL Construction | Mr. Adam Siewiorek | 2022-08-10 | 2023-04-24 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05262 | 800.00 | 1304-12-22 | Workshop Office Bldg. | EGAT-HEC-1000-ELE-DLP-04006_Z0 | Drawing should be updated in the next revision | C | EL | HEC EL Design | Mr. Adam Siewiorek | 2022-11-15 | 2023-05-16 | [5 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-05849 | 800.00 | 1304-12-22 | Workshop | EGAT-HEC-150-INC-DLP-06009_Z0 | Logic number should be provided for fire alarm equipment | C | EL | HEC EL Design | Mr. Adam Zbroja | 2023-01-10 | [6 empty] | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06546.01 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-SCH-00003_Z0 | 42-PDP-005 Ckt. 8,9,10,11,12,13,14,15 & 16 Loop impedance & RCD test shall be done | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2023-05-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06546.02 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-SCH-00003_Z0 | 42-PDP-008 Ckt. 4,7,14,15 Loop impedance & RCD test shall be done | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2023-05-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06546.03 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-SCH-00003_Z0 | 42-PDP-006 Ckt. 6 & 7 Loop impedance & RCD test shall be done | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2023-05-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06546.04 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-SCH-00003_Z0 | 42-PDP-001/11/01, 42-PDP-001/11/03, Loop impedance & RCD test shall be done | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2023-05-22 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06926.01 | 800.00 | 1304-12-22 | WORKSHOP BLDG. | EGAT-HEC-1000-ELE-DLP-06006_Z0 | CABLE TAG SHOULD BE PROVIDED NEAR MFD AND CLIP ALSO | C | EL | Shinbo Electrical Subcon. | Mr. Michal Cwiklak | 2023-04-25 | 2023-05-05 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06926.02 | 800.00 | 1304-12-22 | WORKSHOP BLDG. | EGAT-HEC-1000-ELE-DLP-06006_Z0 | FIRE BARRIER TO INSTALLED | C | EL | Shinbo Electrical Subcon. | Mr. Michal Cwiklak | 2023-04-25 | 2023-05-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06926.03 | 800.00 | 1304-12-22 | WORKSHOP BLDG. | EGAT-HEC-1000-ELE-DLP-06006_Z0 | CABLE DRESSING SHOULD BE MADE PROPERLY ON THE CEILING FOR 8496 | C | EL | Shinbo Electrical Subcon. | Mr. Michal Cwiklak | 2023-04-25 | 2023-06-07 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06926.04 | 800.00 | 1304-12-22 | WORKSHOP BLDG. | EGAT-HEC-1000-ELE-DLP-06006_Z0 | REMOTE INDICATOR FOR 1000-SD-8512 SHOULD BE RELOCATED | C | EL | Shinbo Electrical Subcon. | Mr. Michal Cwiklak | 2023-04-25 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06926.05 | 800.00 | 1304-12-22 | WORKSHOP BLDG. | EGAT-HEC-1000-ELE-DLP-06006_Z0 | TAG AND LOGIC NUMBR SHLOULD BE PROVIDED ON THE SMOKE DETECTORREMOTE INDICATOR FOR 1000-SD-8512 SHOULD BE RELOCATED | C | EL | Shinbo Electrical Subcon. | Mr. Michal Cwiklak | 2023-04-25 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-EL-SB-06926.06 | 800.00 | 1304-12-22 | WORKSHOP BLDG. | EGAT-HEC-1000-ELE-DLP-06006_Z0 | CABLE SHALL BE PROPERLY DRESSED NEAR THE 1000-WS42-MFD-002 | C | EL | Shinbo Electrical Subcon. | Mr. Michal Cwiklak | 2023-04-25 | 2023-05-12 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-06926.07 | 800.00 | 1304-12-22 | WORKSHOP BLDG. | EGAT-HEC-1000-ELE-DLP-06006_Z0 | 2-ADDITIONAL SMOKE DETECTOR SHOULD BE PROVIDED INTHE ROOM NUMBER 92 & 83 | C | EL | HEC EL Design | Mr. Michal Cwiklak | 2023-04-25 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07062.01 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-DLP-06006_Z0 | Missing tag for smoke detector to be provided | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-14 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07062.02 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-DLP-06006_Z0 | Logic tag should be provided | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-14 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07062.03 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-DLP-06006_Z0 | CNBOP red sticker should be provided | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-14 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07062.04 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-ELE-DLP-06006_Z0 | Fire alarm cable should be clean ih the 3 room because paint on the cabinet (F3-30,32 & 34 GROUND FLOOR shelter Area) | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-14 |  | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07067.01 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-INC-DLP-00213 & 00313_Z0 | DO Tag should be provided in ground floor | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-14 | 2023-06-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07067.02 | 800.00 | 1304-12-22 | 1000-WS-42 | EGAT-HEC-1000-INC-DLP-00213 & 00313_Z0 | Speaker tag and cable tag should be provided for outdoor speaker | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-14 | 2023-06-21 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07070.01 | 800.00 | 1304-12-22 | Workshop with Office Bldg. | EGAT-HEC-1000-ELE-DLP-04006_Z1 | Air terminal should be fixed tight | C | EL | Shinbo Electrical Subcon. | Mr. Adam Siewiorek | 2023-05-22 | 2023-05-30 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.01 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | All faults to be cleared from FACP. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.02 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Technical alarms coming from 1000-WS42-IP-0002,0021,0023. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.03 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | 1000-WS42-MFD-010 (IP-0001) Fire damper not working. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.04 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | 1000-WS42-MFD-001,003,010,011-fir dampers disabled for SAT time. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.05 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Fault displayed on FACP coming from 1000-WS42-IP-021. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.06 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Output faults coming from ACS; ACS to be connected and tested with FAS. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.07 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Access void detectors position to be visually signed, TAG no's to be provided. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.08 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Logical tag no's to be provided. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.09 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | TAG no's for horns and beacons missing. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.10 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | TAG no's missing for heat detectors: 1000-HD-8201,8202, 8401, 8402, 8403, 8404. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-07 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.11 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | TAG no's missing for smoke detectors: 1000-SD-8235,8236,8255,8370,8371,8372,8373,8379,8518,8585. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.12 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | TAG no's missing for remote indicators: 1000-SD-8332-RI, 8381-RI, 8360-RI, 8361-RI, 8362-RI, 8363-RI, 8364-RI. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.13 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | TAG no's for all MAC's missing. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.14 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Glow in the dark plates missing for all MAC's. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-08 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.15 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Transparent plastic cover missing for all MAC's. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-08 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.16 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | 1000-MAC-8222: MCP is behind the door -to be moved to another side. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.17 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | 1000-MAC-8214: Cable tags missing. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-07 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.18 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | 1000-MAC-8206: Cable tags missing. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-07 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.19 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Socket to be changed for 1000-MAC-8403- problem with key actuation. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.20 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | One smoke Detector missing in Telecom Security Room (21) due to concrete beam on the ceiling - to be added/installed. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.21 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | SD gets fult after testing - to be cleared from dust: 1000-SD-8232, 8296, 8522. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.22 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Cause and Effect matrix to be updated for: Staircase-1, Staircase-2, Toilet (M)(87)-1000-SD-8586 missing in table. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.23 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | All typo errors to be corrected in Cause and Effect matrix (''cleanner'', ''persion''). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.24 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Protection from paint to be cleared from FAS cable in Warehouse-5. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.25 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Protection from paint to be cleared from FAS cable in Warehouse-6. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.26 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Smoke prevention system (NPK-1) not working. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.27 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Smoke prevention system (NPK-2) not working. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.28 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | NPK-2: wrong cable type (non fireproof). | C | EL | HEC CI Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.29 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | 1000-WS42-IP-0011: blind plugs missing in Office Room -23. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.30 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | 1000-WS-42-MFD-016: cable tag missing. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.31 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | 1000-SD-8456 wrong sticker with tag no (8580). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.32 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | 1000-SD-8444 wrong sticker with tag no (8445). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.33 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | 1000-SD-8445 wrong sticker with tag no (8444). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-13 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.34 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Tag's no missing for Flame Detectors (1000-FD-8201, 8202). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.35 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Cable tags missing for Flame Detectors (1000-FD-8201, 8202). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 | 2023-06-15 | SAT |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-EL-SB-07123.36 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Location nam display is missing (Main Workshop) on FACP for Flame Detectors (1000-FD-8201, 8202). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.37 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Location name displayed on FACP to be corrected for listed devices: 1000-MAC-8210-Staircase-1 MAC, 1000-MAC-8206-Staircase-2 MAC, 1000-SD-8229-Staircase-1, 1000-SD-8228-Staircase-2, 1000-SD-8434-Staircase-2, 1000-HD-8403-Waste Shelter, 1000-HD-8404- Waste Shelter. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.38 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | 1000-SD-8259: Wrong tag no on the ceiling (8255). | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.39 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | 1000-SD-8330: Hatch to be added under the detector. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.40 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | Fire alarm horn sound tone to be in line with safety team agreement. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.41 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | ESD signal to be tested with FAS. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.42 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | HVAC cabinet to be connected with FAS. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-EL-SB-07123.43 | 800.00 | 1304-12-22 | 1000-WS-42 (Workshop Building) | EGAT-HEC-1000-ELE-DLP-06006(1~5) | FACP display to be translated into polish. | C | EL | HEC EL Construction | Mr. Adam Zbroja | 2023-06-03 |  | SAT | [8 empty] | Construction
. | EGAT-RFI-HV-JW-00645.01 | 800.00 | 1304-12-22 | 1000-WS-42 | ED Pipe Installation | To be installed pipe sleeves in a walls non fire rated | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-05-10 | 2022-08-17 | Construction | 2022-05-12 |  |  |  | V | EGAT-RFI-HV-JW-00645 |  |  | Construction
. | EGAT-RFI-HV-JW-00645.02 | 800.00 | 1304-12-22 | 1000-WS-42 | ED Pipe Installation | To be secured sharp edges from cable tray to ED pipe | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-05-10 | 2023-02-15 | Construction | 2022-05-12 |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00645 |  |  | Construction
. | EGAT-RFI-HV-JW-00645.03 | 800.00 | 1304-12-22 | 1000-WS-42 | ED Pipe Installation | To be reassembly connections from equipment behind duct to get slope | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-05-10 | 2022-09-02 | Construction | 2022-05-12 |  |  |  | V | EGAT-RFI-HV-JW-00645 |  |  | Construction
. | EGAT-RFI-HV-JW-00645.04 | 800.00 | 1304-12-22 | 1000-WS-42 | ED Pipe Installation | To be provided connections of maine ED lines to SD line, both cases | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-05-10 | 2022-08-18 | Construction | 2022-05-12 |  |  |  | V | EGAT-RFI-HV-JW-00645 |  |  | Construction
. | EGAT-RFI-HV-JW-00647.01 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Installation | To be removed insulation in places where is welded connections are | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-05-10 | 2022-09-30 | Construction | 2022-05-12 | Only for preasure test |  |  | V | EGAT-RFI-HV-JW-00647 |  |  | Construction
. | EGAT-RFI-HV-JW-00647.02 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Installation | To be removed melted insulation on RL/RG pipes | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-05-10 | 2022-09-30 | Construction | 2022-05-12 |  |  |  | V | EGAT-RFI-HV-JW-00647 |  |  | Construction
. | EGAT-RFI-HV-JW-00647.03 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Installation | To be secured sharp edges between cable tray and pipes | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-05-10 | 2023-02-15 | Construction | 2022-05-12 |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00647 |  |  | Construction
. | EGAT-RFI-HV-JW-00647.04 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Installation | To be verified dimension of pipes acc. to dwg | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-05-10 | 2022-08-17 | Construction | 2022-05-12 |  |  |  | V | EGAT-RFI-HV-JW-00647 |  |  | Construction
. | EGAT-RFI-HV-JW-00647.05 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Installation | To be verified dimension on T connections acc. to dwg | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-05-10 | 2023-05-12 | Construction | 2022-05-12 |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00647 |  |  | Construction
. | EGAT-RFI-HV-JW-00768.01 | 800.00 | 1304-12-22 | 1000-WS-42 | PW, WWS Pipe Installation | To be installed pipe sleeves on PW pipe going thru a walls | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-14 | 2022-08-17 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00768 |  |  | Construction
. | EGAT-RFI-HV-JW-00768.02 | 800.00 | 1304-12-22 | 1000-WS-42 | PW, WWS Pipe Installation | To be corrected the straightening of the PW installation - all area | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-14 | 2022-07-20 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00768 |  |  | Construction
. | EGAT-RFI-HV-JW-00768.03 | 800.00 | 1304-12-22 | 1000-WS-42 | PW, WWS Pipe Installation | To be adjusted and removed threaded roads with clamps - all area | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-14 | 2022-07-20 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00768 |  |  | Construction
. | EGAT-RFI-HV-JW-00770.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Vent Pipe Installation | To be rised vent pipe due of laying on PW installation - 88 room | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-27 | 2022-09-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00770 |  |  | Construction
. | EGAT-RFI-HV-JW-00770.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Vent Pipe Installation | To be Installed pipe sleeves on Vent pipe going thru a walls | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-27 | 2022-08-17 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00770 |  |  | Construction
. | EGAT-RFI-HV-JW-00770.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Vent Pipe Installation | To be added supports for vents pipe located in installation shaft | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-27 | 2022-08-18 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00770 |  |  | Construction
. | EGAT-RFI-HV-JW-00770.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Vent Pipe Installation | To be corrected connection of vent pipe with drain of PRV heater | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-06-27 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00770 |  |  | Construction
. | EGAT-RFI-HV-JW-00820.01 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Installation | To be sealed opens of cable tray with pipes acc. to detail | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-12 | 2023-01-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00820 |  |  | Construction
. | EGAT-RFI-HV-JW-00820.02 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Installation | To be provided as-built dwg including all changes | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-12 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00820 |  |  | Construction
. | EGAT-RFI-HV-JW-00820.03 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Installation | To be provided attachment of using nitrogen during brezing | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-12 | 2022-07-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00820 |  |  | Construction
. | EGAT-RFI-HV-JW-00821.01 | 800.00 | 1304-12-22 | 1000-WS-42 | ED Pipe Installation | To be corrected pipe going thru wall acc. to detail | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-12 | 2023-01-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00821 |  |  | Construction
. | EGAT-RFI-HV-JW-00821.02 | 800.00 | 1304-12-22 | 1000-WS-42 | ED Pipe Installation | To be straighten drain line from unit 43 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-12 | 2022-09-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00821 |  |  | Construction
. | EGAT-RFI-HV-JW-00821.03 | 800.00 | 1304-12-22 | 1000-WS-42 | ED Pipe Installation | To be provided as-built including all changes | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-12 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00821 |  |  | Construction
. | EGAT-RFI-HV-JW-00857.01 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Installation | To be provided as-built DWG including routing changes of RL/RG pipes | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-07-21 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00857 |  |  | Construction
. | EGAT-RFI-HV-JW-00967.01 | 800.00 | 1304-12-22 | 1000-WS-42 | SD Pipe Installation | To be cleaned installation from mortar, etc. | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-17 | 2023-02-17 | Construction |  | 'Punch Category' changed A -> B (2022-09-28) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-00967 |  |  | Construction
. | EGAT-RFI-HV-JW-00967.02 | 800.00 | 1304-12-22 | 1000-WS-42 | SD Pipe Installation | To be installed rubber under clamps of pipes - few items. | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-17 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00967 |  |  | Construction
. | EGAT-RFI-HV-JW-00967.03 | 800.00 | 1304-12-22 | 1000-WS-42 | SD Pipe Installation | To be installed pipe sleeves on pipe going thru walls | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-17 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00967 |  |  | Construction
. | EGAT-RFI-HV-JW-00969.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Vent Pipe Installation | To be cleaned installation from mortar, etc. | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-17 | 2023-02-24 | Construction |  | 'Punch Category' changed A -> B (2022-09-28) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-00969 |  |  | Construction
. | EGAT-RFI-HV-JW-00969.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Vent Pipe Installation | To be installed pipe sleeves on pipe going thru walls | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-17 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00969 |  |  | Construction
. | EGAT-RFI-HV-JW-00969.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Vent Pipe Installation | To be installed rubber under clamps of pipes - few items. | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-17 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00969 |  |  | Construction
. | EGAT-RFI-HV-JW-00970.01 | 800.00 | 1304-12-22 | 1000-WS-42 | PW, WWS Pipe Installation | To be corrected installation of urinal frames | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-17 | 2022-09-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00970 |  |  | Construction
. | EGAT-RFI-HV-JW-00970.02 | 800.00 | 1304-12-22 | 1000-WS-42 | PW, WWS Pipe Installation | To be performed fire passes in walls | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-17 | 2023-02-16 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-00970 |  |  | Construction
. | EGAT-RFI-HV-JW-00970.03 | 800.00 | 1304-12-22 | 1000-WS-42 | PW, WWS Pipe Installation | To be installed pipe sleeves in walls | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-17 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-00970 |  |  | Construction
. | EGAT-RFI-HV-JW-01008.01 | 800.00 | 1304-12-22 | 1000-WS-42 | ED Pipe Installation | To be filled gap around pipe going thru wall | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-17 | 2023-01-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01008 |  |  | Construction
. | EGAT-RFI-HV-JW-01008.02 | 800.00 | 1304-12-22 | 1000-WS-42 | ED Pipe Installation | To be adjusted dimension of pipe outside of bld | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-17 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01008 |  |  | Construction
. | EGAT-RFI-HV-JW-01016.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct installation | To be provided access doors acc. to PN-EN | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-22 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01016 |  |  | Construction
. | EGAT-RFI-HV-JW-01016.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct installation | To be corrected flexible connection next to fans | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-22 | 2023-02-10 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01016 |  |  | Construction
. | EGAT-RFI-HV-JW-01016.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct installation | To be protected traces od corrosion | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-22 | 2023-02-10 | Construction |  | 'Punch Category' changed A -> B (2022-09-28) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-01016 |  |  | Construction
. | EGAT-RFI-HV-JW-01017.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct support installation | To be removed and secured traces of corrosion | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-22 | 2023-03-16 | Construction |  | 'Punch Category' changed A -> B (2022-09-28) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-01016 |  |  | Construction
. | EGAT-RFI-HV-JW-01037.01 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Insulation | To be filled all gaps in partition walls acc. to detail | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-26 | 2023-01-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01037 |  |  | Construction
. | EGAT-RFI-HV-JW-01037.02 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Insulation | To be filled all gaps in fire rated walls acc. to approval | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-26 | 2023-01-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01037 |  |  | Construction
. | EGAT-RFI-HV-JW-01037.03 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Insulation | To be cleaned insulation on installation and replace partially | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-26 | 2023-03-14 | Construction |  | 'Punch Category' changed A -> B (2022-09-28) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-01037 |  |  | Construction
. | EGAT-RFI-HV-JW-01073.01 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Insulation | To be removed and cleaned dust, mortar, etc. from insulation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-29 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01073 |  |  | Construction
. | EGAT-RFI-HV-JW-01074.01 | 800.00 | 1304-12-22 | 1000-WS-42 | ED Pipe Insulation | To be cleaned insulation from dust, mortar, etc. | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-29 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01074 |  |  | Construction
. | EGAT-RFI-HV-JW-01074.02 | 800.00 | 1304-12-22 | 1000-WS-42 | ED Pipe Insulation | To be removed sharp edges on insulation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-29 | 2023-02-15 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01074 |  |  | Construction
. | EGAT-RFI-HV-JW-01074.03 | 800.00 | 1304-12-22 | 1000-WS-42 | ED Pipe Insulation | To maintain the continuity of the insulation - Room No. 21 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-09-29 | 2023-01-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01074 |  |  | Construction
. | EGAT-RFI-HV-JW-01095.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct installation | To be sealed ducts going thru partition acc. to detail | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2023-03-24 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01095 |  |  | Construction
. | EGAT-RFI-HV-JW-01095.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct installation | To be sealed ducts going thru partition acc. to approval (fire wall) | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2023-06-26 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01095 |  |  | Construction
. | EGAT-RFI-HV-JW-01095.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct installation | To be corrected ducts and fans in one line | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01095 |  |  | Construction
. | EGAT-RFI-HV-JW-01095.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct installation | To be cleaned all ducts from dust, mortar etc. | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01095 |  |  | Construction
. | EGAT-RFI-HV-JW-01095.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct installation | To be corrected clamps on connection of ducts, to be check all | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2022-12-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01095 |  |  | Construction
. | EGAT-RFI-HV-JW-01095.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct installation | To be removed connection of duct from walls | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2022-12-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01095 |  |  | Construction
. | EGAT-RFI-HV-JW-01095.07 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct installation | To be provided as-built due of changed ducts routing in rooms 20, 21, 18 and corridor | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2023-01-02 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01095 |  |  | Construction
. | EGAT-RFI-HV-JW-01095.08 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct installation | To be corrected location of duct with register due of collision with cable tray | C | EL | HEC EL Construction | Mr. Jerzy Wegner | 2022-10-12 | 2023-05-09 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01095 |  |  | Construction
. | EGAT-RFI-HV-JW-01096.01 | 800.00 | 1304-12-22 | 1000-WS-42 | 1000-WS-42 | To be sealed duct going thru a partition according to approval | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-02-16 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01096.02 | 800.00 | 1304-12-22 | 1000-WS-42 | 1000-WS-42 | To be sealed duct going thru a partition according to detail | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-03-24 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01096.03 | 800.00 | 1304-12-22 | 1000-WS-42 | 1000-WS-42 | To be corrected connection of ducts in a partition/walls | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-03-14 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01096.04 | 800.00 | 1304-12-22 | 1000-WS-42 | 1000-WS-42 | To be leveled duct-62 room | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-03-01 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01096.05 | 800.00 | 1304-12-22 | 1000-WS-42 | 1000-WS-42 | To be provided as-built including all changes | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-01-24 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01097.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct support installation | To be corrected and adjusted supports | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2022-12-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01097 |  |  | Construction
. | EGAT-RFI-HV-JW-01097.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct support installation | To be corrected/ replaced threaded rods | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2022-12-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01097 |  |  | Construction
. | EGAT-RFI-HV-JW-01097.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct support installation | To be cut too long threaded rods under profiles | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2022-12-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01097 |  |  | Construction
. | EGAT-RFI-HV-JW-01097.04 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct support installation | To be added support in corridor | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2022-12-27 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01097 |  |  | Construction
. | EGAT-RFI-HV-JW-01097.05 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct support installation | To be removed entire supports from walls | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2022-12-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01097 |  |  | Construction
. | EGAT-RFI-HV-JW-01097.06 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct support installation | To be corrected adjustment of rubber under duct | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-12 | 2022-12-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01097 |  |  | Construction
. | EGAT-RFI-HV-JW-01098.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct and support | To be adjusted/level at support of ducts | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-08 | 2022-12-27 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01124.01 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be assembled seconds nuts on rods under fans | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-01-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01124 |  |  | Construction
. | EGAT-RFI-HV-JW-01124.02 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be corrected position of fan in line to ducts | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-01-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01124 |  |  | Construction
. | EGAT-RFI-HV-JW-01124.03 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be connected power and instrumental cables, devices, etc. | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01124 |  |  | Construction
. | EGAT-RFI-HV-JW-01125.01 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be removed traces of corrosion from fans | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01125 |  |  | Construction
. | EGAT-RFI-HV-JW-01125.02 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be corrected flexible connections | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-02-10 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01125 |  |  | Construction
. | EGAT-RFI-HV-JW-01125.03 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be installed rubbers washer under fans | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-18 | 2023-02-03 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01125 |  |  | Construction
. | EGAT-RFI-HV-JW-01141.01 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be added additional nuts on rods | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01141 |  |  | Construction
. | EGAT-RFI-HV-JW-01141.02 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be connected electrical and instruments cables | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01141 |  |  | Construction
. | EGAT-RFI-HV-JW-01141.03 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be installed bottom covers | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-01-26 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01141 |  |  | Construction
. | EGAT-RFI-HV-JW-01141.04 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be leveled and adjusted for ceiling | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-02-07 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01141 |  |  | Construction
. | EGAT-RFI-HV-JW-01141.05 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be installed remote controls on walls | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01141 |  |  | Construction
. | EGAT-RFI-HV-JW-01142.01 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be added additional nuts on rods | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01142 |  |  | Construction
. | EGAT-RFI-HV-JW-01142.02 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be connected electrical and instruments cables | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01142 |  |  | Construction
. | EGAT-RFI-HV-JW-01142.03 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be installed bottom covers | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01142 |  |  | Construction
. | EGAT-RFI-HV-JW-01142.04 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be leveled and adjusted for ceiling | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-02-07 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01142 |  |  | Construction
. | EGAT-RFI-HV-JW-01142.05 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be installed remote controls on walls | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01142 |  |  | Construction
. | EGAT-RFI-HV-JW-01143.01 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be removed traces of corrosion from units | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-24 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01143 |  |  | Construction
. | EGAT-RFI-HV-JW-01143.02 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be connected earthing to units | C | EL | HEC EL Construction | Mr. Jerzy Wegner | 2022-10-24 | 2023-04-11 | Construction |  | 'Discipline' changed HV -> EL (2022-11-25) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-01143 |  |  | Construction
. | EGAT-RFI-HV-JW-01143.03 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be removed mechanical damages from units | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-24 | 2023-05-22 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01143 |  |  | Construction
. | EGAT-RFI-HV-JW-01143.04 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be installed covers for RL/RG pipes entering to units | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-24 | 2023-02-10 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01143 |  |  | Construction
. | EGAT-RFI-HV-JW-01143.05 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be assembly stickers with description on units | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-10-24 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01143 |  |  | Construction
. | EGAT-RFI-HV-JW-01146.01 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be installed local panels | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01146 |  |  | Construction
. | EGAT-RFI-HV-JW-01146.02 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be connected electrical, instrumental and earthing cables | C | EL | HEC EL Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-04-11 | Construction |  | 'Discipline' changed HV -> EL (2022-11-25) evidence attached |  | SCAN CAT | V | EGAT-RFI-HV-JW-01146 |  |  | Construction
. | EGAT-RFI-HV-JW-01146.03 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be removed traces of corrosion from UH | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-02-03 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01146 |  |  | Construction
. | EGAT-RFI-HV-JW-01165.01 | 800.00 | 1304-12-22 | 1000-WS-42 | PW Pipe Insulation | To be cleaned entire insulation on PW | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01165 |  |  | Construction
. | EGAT-RFI-HV-JW-01165.02 | 800.00 | 1304-12-22 | 1000-WS-42 | PW Pipe Insulation | To be added sleeves on missing places | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01165 |  |  | Construction
. | EGAT-RFI-HV-JW-01166.01 | 800.00 | 1304-12-22 | 1000-WS-42 | PW Pipe Insulation | To be cleaned entire insulation on PW | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01166 |  |  | Construction
. | EGAT-RFI-HV-JW-01166.02 | 800.00 | 1304-12-22 | 1000-WS-42 | PW Pipe Insulation | To be added sleeves on missing places | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-01 | 2023-01-25 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01166 |  |  | Construction
. | EGAT-RFI-HV-JW-01211.01 | 800.00 | 1304-12-22 | 1000-WS-42 | 1000-WS-42 | To be installed stikers on VD | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-03-14 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01211.02 | 800.00 | 1304-12-22 | 1000-WS-42 | 1000-WS-42 | To be installed access doors according to PN/EN | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-03-27 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01211.03 | 800.00 | 1304-12-22 | 1000-WS-42 | 1000-WS-42 | To be installed MFD on wall in corridor due of fire rated wall | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-02-07 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01211.04 | 800.00 | 1304-12-22 | 1000-WS-42 | 1000-WS-42 | To be corrected installation of VD in a wall corridor | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-02-03 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01211.05 | 800.00 | 1304-12-22 | 1000-WS-42 | 1000-WS-42 | To be corrected installation of duct laying down on ED installation | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-02-07 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01211.06 | 800.00 | 1304-12-22 | 1000-WS-42 | 1000-WS-42 | To be corrected duct due of collision with RL/RG and ED installation 57 room | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-02-07 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01211.07 | 800.00 | 1304-12-22 | 1000-WS-42 | 1000-WS-42 | To be moved VD from a wall 22 room | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-08 | 2023-02-03 | Construction |  |  |  | SCAN CAT | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01212.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct Accessory Installation | To be installed stickers open/close on VD | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-02-09 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01212 |  |  | Construction
. | EGAT-RFI-HV-JW-01212.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct Accessory Installation | To be installed AW on EA ductworks | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-03-30 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01212 |  |  | Construction
. | EGAT-RFI-HV-JW-01212.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct Accessory Installation | To be removed rust from AD | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-02-10 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01212 |  |  | Construction
. | EGAT-RFI-HV-JW-01225.01 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Control Panel Installation | To be cleaned HVAC control panel | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-06-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01225 |  |  | Construction
. | EGAT-RFI-HV-JW-01226.01 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Cabling Work | To be sealed installation going thru a partition acc. to detail | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-04-17 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01226 |  |  | Construction
. | EGAT-RFI-HV-JW-01226.02 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Cabling Work | To be sealed installation going thru a partition acc. to approval | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-02-16 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01226 |  |  | Construction
. | EGAT-RFI-HV-JW-01226.03 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Cabling Work | To be installed remote controlers on a walls | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01226 |  |  | Construction
. | EGAT-RFI-HV-JW-01226.04 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Cabling Work | To be completed remaining tags on cabling | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-02-23 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01226 |  |  | Construction
. | EGAT-RFI-HV-JW-01226.05 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Cabling Work | To be extended flexible conduict on instrument cables from device to wall | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-02-07 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01226 |  |  | Construction
. | EGAT-RFI-HV-JW-01227.01 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Cabling Work | To be sealed installation going thru a partition acc. to detail | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-02-27 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01227 |  |  | Construction
. | EGAT-RFI-HV-JW-01227.02 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Cabling Work | To be sealed installation going thru a partition acc. to approval | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-02-16 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01227 |  |  | Construction
. | EGAT-RFI-HV-JW-01227.03 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Cabling Work | To be relocated remote controlers on walls in Room No. 69, 51, 54 | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01227 |  |  | Construction
. | EGAT-RFI-HV-JW-01227.04 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Cabling Work | To be completed remaining tags on cabling | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-02-23 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01227 |  |  | Construction
. | EGAT-RFI-HV-JW-01227.05 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Cabling Work | To be extended flexible conduict on instrument cables from device to wall | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-02-07 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01227 |  |  | Construction
. | EGAT-RFI-HV-JW-01227.06 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Cabling Work | To be fixed damage cable - Room No. 72 | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-02-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01227 |  |  | Construction
. | EGAT-RFI-HV-JW-01227.07 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Cabling Work | To be leveled cable tray - Room No. 73 | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-03-02 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01227 |  |  | Construction
. | EGAT-RFI-HV-JW-01228.01 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Cabling Work | To be provided stickers on sensors | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-18 | 2023-02-02 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01228 |  |  | Construction
. | EGAT-RFI-HV-JW-01238.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Vent Pipe Installation | To be provided as-built dwg of vent pipe detail | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-11-16 | 2023-01-24 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01238 |  |  | Construction
. | EGAT-RFI-HV-JW-01260.01 | 800.00 | 1304-12-22 | 1000-WS-42 | RL/RG Pipe Installation | To be fixed support of RL/RG next to SAC | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-29 | 2023-01-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01260 |  |  | Construction
. | EGAT-RFI-HV-JW-01262.01 | 800.00 | 1304-12-22 | 1000-WS-42 | ED Pipe Installation | To be sealed pipe going thru a wall acc. to detail | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-29 | 2023-01-05 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01262 |  |  | Construction
. | EGAT-RFI-HV-JW-01264.01 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be installed handle on SAC 002B | B | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-29 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01264 |  |  | Construction
. | EGAT-RFI-HV-JW-01264.02 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be removed mechanical damages from units | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-29 | 2023-02-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01264 |  |  | Construction
. | EGAT-RFI-HV-JW-01264.03 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be removed traces of corrosion from SAC | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-29 | 2023-02-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01264 |  |  | Construction
. | EGAT-RFI-HV-JW-01264.04 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be connected power and instrumental cables | A | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-29 | 2023-01-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01264 |  |  | Construction
. | EGAT-RFI-HV-JW-01264.05 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be tighten thru nuts of air supply box | C | HV | HEC HV Construction | Ms. Daria Pliszka | 2022-11-29 | 2023-02-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01264 |  |  | Construction
. | EGAT-RFI-HV-JW-01277.01 | 800.00 | 1304-12-22 | 1000-WS-42 | PW Pipe Insulation | To be provided access for strainer, insulation to be cut | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-05 | 2023-02-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01277 |  |  | Construction
. | EGAT-RFI-HV-JW-01283.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct Accessory Installation | To be sealed MFD acc. to approval | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 | 2023-06-26 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01283 |  |  | Construction
. | EGAT-RFI-HV-JW-01283.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct Accessory Installation | To be installed stickers open/close on VD | B | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 | 2022-12-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01283 |  |  | Construction
. | EGAT-RFI-HV-JW-01283.03 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct Accessory Installation | To be provided access to handle of VD | A | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 | 2022-12-30 | Construction |  |  |  |  | V | EGAT-RFI-HV-JW-01283 |  |  | Construction
. | EGAT-RFI-HV-JW-01284.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct Insulation | To be cleaned insulation on ducts | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 | 2023-02-28 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01284 |  |  | Construction
. | EGAT-RFI-HV-JW-01284.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Duct Insulation | To be removed mechanical damages | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 | 2023-03-01 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01284 |  |  | Construction
. | EGAT-RFI-HV-JW-01285.01 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be removed transport protection from fans | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 | 2023-02-09 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01285 |  |  | Construction
. | EGAT-RFI-HV-JW-01285.02 | 800.00 | 1304-12-22 | 1000-WS-42 | HVAC Equipment Installation | To be provided access to door on east side of AHU | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2022-12-10 |  | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01285 |  |  | Construction
. | EGAT-RFI-HV-JW-01347.01 | 800.00 | 1304-12-22 | 1000-WS-42 | PW Pipe Insulation | Jacketing should be done | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-05-22 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01347 |  |  | Construction
. | EGAT-RFI-HV-JW-01348.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Fire Extinguisher Installation | To be fixed supporting of F.E. in Room No. 4/F8 | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-02-17 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01348 |  |  | Construction
. | EGAT-RFI-HV-JW-01348.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Fire Extinguisher Installation | To be corrected mechanical damage i Room No. 29/F3 | C | HV | HEC HV Construction | Mr. Jerzy Wegner | 2023-01-25 | 2023-02-17 | Construction |  |  |  | SCAN CAT | V | EGAT-RFI-HV-JW-01348 |  |  | Construction
. | EGAT-RFI-HV-JW-01409.01 | 800.00 | 1304-12-22 | 1000-WS-42 | Hvac Acceptance Inspection | Smoke system is not connected to Fas | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-03-15 |  | Construction | [8 empty] | Construction
. | EGAT-RFI-HV-JW-01409.02 | 800.00 | 1304-12-22 | 1000-WS-42 | Hvac Acceptance Inspection | Provide start-up report (point 11) | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-03-15 | 2023-04-14 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01503.01 | 800.00 | 1304-12-22 | AUX | HVAC-Equipment | Electric radiator is damaged | C | HV | HEC HV Construction | Mr. Tomasz Ulatowski | 2023-05-16 | 2023-05-22 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-HV-JW-01503.02 | 800.00 | 1304-12-22 | AUX | Hvac Equipment | Lack of electric supply to electric radiators | C | EL | HEC EL Construction | Mr. Tomasz Ulatowski | 2023-05-16 | 2023-05-19 | Construction |  |  |  |  | V |  |  |  | Construction
. | EGAT-RFI-SS-MK-01121.01 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 Axis 10-11/A-D | Touch up painting | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-03 | 2022-03-23 | Construction | 2022-02-05 | 'Punch Category' changed A -> C (2022-02-20) evidence attached |  |  | V | EGAT-RFI-SS-MK-01121 |  |  | Construction
. | EGAT-RFI-SS-MK-01121.02 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 Axis 10-11/A-D | 23 elements are excluded | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-03 | 2022-03-23 | Construction | 2022-02-05 |  |  |  | V | EGAT-RFI-SS-MK-01121 |  |  | Construction
. | EGAT-RFI-SS-MK-01122.01 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 Axis 10-11/A-D | Gap between grating and the toe board | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-03 |  | Construction | 2022-02-04 | 'Punch Category' changed A -> C (2022-02-20) evidence attached |  |  | V | EGAT-RFI-SS-MK-01122 |  |  | Construction
. | EGAT-RFI-SS-MK-01122.02 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 Axis 10-11/A-D | Touch up painting | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-03 | 2023-06-21 | Construction | 2022-02-04 | 'Punch Category' changed A -> C (2022-02-20) evidence attached |  |  | V | EGAT-RFI-SS-MK-01122 |  |  | Construction
. | EGAT-RFI-SS-MK-01122.03 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 Axis 10-11/A-D | The circular lader rungs | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-03 | 2023-05-17 | Construction | 2022-02-04 | 'Punch Category' changed A -> C (2022-02-20) evidence attached |  |  | V | EGAT-RFI-SS-MK-01122 |  |  | Construction
. | EGAT-RFI-SS-MK-01133.01 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 | Touch up painting only under cladding shelter | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-02-08 | 2022-03-23 | Construction | 2022-02-08 | 'Punch Category' changed A -> C (2022-02-20) evidence attached |  |  | V | EGAT-RFI-SS-MK-01133 |  |  | Construction
. | EGAT-RFI-SS-MK-01251.01 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 | Closing not secure of slipping | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-22 | 2022-06-24 | Construction | 2022-03-22 |  |  |  | V | EGAT-RFI-SS-MK-01251 |  |  | Construction
. | EGAT-RFI-SS-MK-01251.02 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 | No support for ladder | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-03-22 | 2023-06-05 | Construction | 2022-03-22 |  |  | SCAN CAT | V | EGAT-RFI-SS-MK-01251 |  |  | Construction
. | EGAT-RFI-SS-MK-01251.03 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 | Coating damages | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-22 | 2023-06-21 | Construction | 2022-03-22 |  |  |  | V | EGAT-RFI-SS-MK-01251 |  |  | Construction
. | EGAT-RFI-SS-MK-01256.01 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 | Gap between grating and toe board (EGAT-RFI-SS-MK-01122.01) | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-23 | 2022-12-29 | Construction | 2022-03-24 |  |  |  | V | EGAT-RFI-AR-GS-01256 |  |  | Construction
. | EGAT-RFI-SS-MK-01256.02 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 | Touch up painting (EGAT-RFI-SS-MK-01122.02) | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-23 | 2022-12-29 | Construction | 2022-03-24 |  |  |  | V | EGAT-RFI-AR-GS-01256 |  |  | Construction
. | EGAT-RFI-SS-MK-01256.03 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 | Circular ladder rungs (EGAT-RFI-SS-MK-01122.03) | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-23 | 2022-12-29 | Construction | 2022-03-24 |  |  |  | V | EGAT-RFI-AR-GS-01256 |  |  | Construction
. | EGAT-RFI-SS-MK-01256.04 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 | Coating damages due to other branches work | C | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-23 | 2023-06-21 | Construction | 2022-03-24 |  |  |  | V | EGAT-RFI-AR-GS-01256 |  |  | Construction
. | EGAT-RFI-SS-MK-01256.05 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 | Closing not secure of slipping | A | SS | HEC SS Construction | Mr. Slawomir Nasilowski | 2022-03-23 | 2022-06-24 | Construction | 2022-03-24 |  |  |  | V | EGAT-RFI-AR-GS-01256 |  |  | Construction
. | EGAT-RFI-SS-MK-01256.06 | 800.00 | 1304-12-22 | AUX | 1000-WS-42 | No support for ladder | C | AR | HEC AR Construction | Mr. Slawomir Nasilowski | 2022-03-23 | 2023-06-05 | Construction | 2022-03-24 | discipline changed SS-> AR (2022-04-15) evidence attached |  | SCAN CAT | V | EGAT-RFI-AR-GS-01256 |  |  | Construction