## Comments
ANMA-DO Offshore Wind Farm Project
DOCUMENT/DRAWING REVIEW SHEET
SUBJECT : |  | AMMA OWF Feed Proposal_Draft
Dwg/Doc No. : -
HEC's Comments | [5 empty] | ARUP’s Response | HEC's Comments | ARUP’s Response | HEC's Comments
No. | Part | Rev. | Draft | Status | - | TRANSMITTAL NO. : |  | TRANSMITTAL NO. :
1 | General | 1.1 Background ----> Please revise the contents to conform to the FEED design and include EQUIS as a consortium member. ---> The gross capacity shall be revised to 528MW considering phase 1 & 2 |  |  |  | Noted and addressed. | 1. Please revise Section 1.1 considering the fact that Equis has joined since 2021. 2. Please, rearrange the order of shareholders. (KWC, EQUIS, etc) 3. Change the wording for Owner's Engineer Services to avoid the ambuiguity with Sponsors's Owners Engineers. | Noted and addressed. | Noted. 1 Introduction 1.1 Background HEC (“the Client”) engaged Arup, supported by ODE, to participate in the Project to provide Engineering services as their Technical Advisors for the project. The underlined phrase should be revised later according to final decision.
2 | General | 1.3 Project Description Table 1 Project Summary ----> Please revise the contents to conform to the FEED design and include EQUIS as a consortium member. (KWC : Korea Wind Energy Company) |  |  |  | Noted and addressed. | Noted. | - | -
3 | General | 1.4 Design Requirements • One type of WTG: The information on type and technical data of one WTG would be available at the start of FEED and will be given to Arup. • One type of substructure (Jacket). • One type of substation (Onshore Anma Inland -> Juk-do Island) • One export cable route (via Songi-do). Minimize the program through intensive resource input and application of automation tools to shorten the analysis time. |  |  |  | Noted and addressed. | The island monitoring house will be located on the Juk-do of Anma island -> The island monitoring house will be located on the Juk-do of Anma island (To be discussed) | Noted. | Noted.
4 | General | 1.5.1 Assumptions, Exclusions and Limitations • Physical fieldworks of any kind, including site investigation and surveys, are beyond the scope of this Contract. ----> Constructability review and construction plan establishment should be included as feed design service, and accordingly, site survey service for site review required for land construction such as assembly yards and yards such as hinterlands, sub-stations, monitoring houses, and Songi-do pylon route should be performed when necessary. In addition, if necessary, on-site investigation service shall be performed to check whether there is any interference in construction when carrying out this project by investigating and organizing the port and water area related plans and construction sites in the OWF and surrounding areas. |  |  |  | Please note that we can conduct necessary site inspections and visits but not any kinds of physical fieldworks including surveys and ground investigations. See revised text | 1.7 Assumptions, Exclusions and Limitations • We will conduct general engineering inspection and site visits as appropriate as necessary. However, physical fieldworks of any kind, including site investigation (e.g. borehole drilling, field and laboratory tests, geophysics tests) and surveys (e.g topographical survey and utilities survey), are beyond the scope of this Contract. We shall identify the need for those works as soon as practicable in the beginning of the FEED stage and provide technical support to HEC for procurement of those works. We assume the contractual work and supervision work (if any) will be hanlded by HEC. 1. However, the HEC's mentioned reply shall be reflected to scope of FEED clearly. In addition, please explain what is general site inspections and visits for. 2. Please revise HEC to SPC. | 1. Noted. Both Constructability Review and etablishment of construction plan has been added in the new section 3.10.4 of WP08 (Transporation and Installation). In undertaking the FEED design works, we are willing to visit the site as required to better understand the local site conditions and make any ad-hoc inspections of any fieldworks that may be ongoing during the FEED programme to satsify ourselves of the works quality. These site visits would be undertaken to clarify any issues to facilitate the FEED design process. 2. Noted. and revised "HEC" to "SPC". | 1. 사업팀 확인 필요. T&I Scope이므로 ARUP뿐만 아니라 신규ISU Scope에도 관련 Scope 일부 추가할지 확인 필요. 2. Noted.
5 | General | 1.5.1 Assumptions, Exclusions and Limitations • All technical documents required for the FEED is expected to be available at the commencement of our engineering services. We will review and interpret the available reports / received data and provide our recommendation on the use of data and derivation of design parameters. When we spot errors in those reports such that we cannot further proceed with our work, we expect the Client will assist in requesting and obtaining the rectification / explanation from the report originator. -----> Most of the reports and data to be provided to ARUP when Feed designing are the Concept Design Report which has been performed by ARUP. If an error occurs in the Concept Design Report, ARUP must resolve it by itself and share the content with the client. If there is a significant error (Feed design cannot proceed) in the data that could not be confirmed during Concept Design or the data additionally provided during feed design (Additional geo-technical & geo-physical survey results, Metocean Study Report, newly received WTG data, etc.) ARUP must notify client within 2 weeks of receiving the data, and provide an appropriate method to solve the problem and perform the service according to the results of mutual consultation. In addition, please show what kinds of technical document are necessary in order to prepare in advance by our side since ARUP already knows what HEC has through concept design stage - Please submit required data list & schedule for feed design in advance with revised proposal. |  |  |  | Noted. For documents previously produced by Arup, we shall take responsibility in accordance with our contract with HEC for the concept design service. We will notify HEC any errors spotted in other external reports once identified. We understand the FEED stage will start in March 2022. In terms of the list of technical documents required, in addition to those produced by Arup, we suggest pre-meetings be held prior to the start of the FEED stage, such that we can understand what information HEC may have. The list can then be developed with actions planned. This will facilitate a smooth start of the FEED work. | Note. First, please provide a draft list of technical documents and their due dates which are nomally required in FEED stage. After that, we can have a practical discussion with the draft list. This will facilitate a smooth start of the FEED work. | The initial draft of the FEED proposal was issued to clarify the scope of works that would be expected for the FEED design stage. Having gained confirmation of the FEED scope, a draft list of technical documents has been included in the revised proposal (section 4.1) and programme (section 4.2). However, it is still difficult to make detailed list of deliverable and its dates as ISC is not selected and we don't know how ISC will propose. For the timebeing, Arup will developing its own project programme and once ISC is selected we wil further develop it combining both programme. | At this moment, the technical document lists which are normally required in FEED design stage should be provided with their due date. In addtion, please submit the input data or document list & its due date which are needed to produce the FEED technical documents mentioned above.
6 | General | 1.5.1 Assumptions, Exclusions and Limitations • One layout will be prepared for the selected turbine. Please change the sentence above into the following one. - After conducting WTG layout optimization considering various site conditions and AEP, the best one layout will be prepared for the selected turbine. |  |  |  | Please refer to Section 2.3.5 | 2.3.5 AEP and WTG Layout Report Such findings and the finalised layout will be documented and presented in AEP and WTG Layout Report. Not only the finalised layout but also detail optimization process should be provided in the beginning, middle and end of the optimization process. | It is not usual to document the optimisation process as it is an iterative procedure starting from an initial single turbine, followed by a preliminary layout, followed by discrete changes to optimise the finalised layout. We can provide relevant snap shots of the process followed to achieve an optimised layout. | The original intention is to check whether, during the optimization process, ARUP and HEC are on the same page regarding the direction or way of optimization. If we receive the opmization results only, additional revision time is required when we do not accept the results. Therefore, please share the optimization process and discuss the direction of optimization.
7 | General | 1.5.1 Assumptions, Exclusions and Limitations • All survey and experiment including geotechnical survey and interpretation, numerical analysis experiment, will be performed and provided by SPC and Arup will review the HEC’s result and complete the review report. • Local permit and authority approvals are not in cluded in Arup’s scope and such permit and approvals will be taken care by HEC. ----> HEC will provide to ARUP a report on the geotechnical investigation, geophysical survey and metocean study currently being carried out by the owner. ----> Support for the preparation of authorizations, licenses and permits for project implementation shall be included in ARUP scope. ----> Support for various tasks for design basis certification by professional organizations shall be included in ARUP scope.. ----> Please revise the wording from HEC to SPC |  |  |  | We are pleased to offer the support service to certification as an optional service. Please see Section 2.14.5 on our service for certification. | Noted | - | -
8 | General | 1.5.1 Assumptions, Exclusions and Limitations • We assume there is no international certification required. --> Please define the international certification and it is mandatory or not for FEED work |  |  |  | We assume no international certification required in our FEED base scope. We are happy to offer relevant support work as an optional service. See our reply to item 7. | Please add a description which explains what the international certification means and when it is required. | In section 3.4 We have added a description to explain international certification which is essentially an independent body or organisation that will check and certify the design to ensure that the final products meet the requirements and specifications for wind farm engineering and the processes followed meet industry standards. | Including ARUP's response, please add a description which explains what the international certification means and when it is required.
9 | General | 1.5.1 Assumptions, Exclusions and Limitations • All deliverables provided by Arup shall be revised as per HEC’s comments, but not more than two rounds of comments. Extra fee and time shall be provided for additional round of comments. ----> Not Accepted. This matter should be decided according to the quality of each deliverable, whether HEC Comment is reflected, or the content of an appropriate reply to the case. |  |  |  | Noted. This has been revised to capture your comment given. | 1.7 Assumptions, Exclusions and Limitations • All deliverables provided by Arup shall be revised as per HEC’s comments. Extra fee and time shall be provided for additional round of comments involving changing of scope / requirements or providing details that are beyond what FEED stage may reasonably entail. Please revise the above as follows. • All deliverables provided by Arup shall be revised as per HEC’s comments. Extra fee and time shall be provided for additional round of comments involving changing of scope / requirements or providing details that are beyond what FEED stage may reasonably entail. In addition, the list of drawings should be sumbitted at the beginning. | Noted and addressed. | Noted.
10 | General | 1.5.1 Assumptions, Exclusions and Limitations • Any update and revision of the design in FEED stage is due to late provision of the updated or additional information. Extra fee and time shall be provided. ----> This matter may occur in the any design process, and if changes or additional data are provided during the design process, the additional cost and period will be decided through mutual consultation according to the relevant content. |  |  |  | Noted and revised the clause. | 1.7 Assumptions, Exclusions and Limitations • Any update and revision of the design in FEED stage is due to late provision of the updated or additional information. Extra fee and time shall be decided through mutual consultation according to the relevant content. Please revise the above as follows. • Any update and revision of the design in FEED stage is due to late provision of the updated or additional information. When necessary, extra fee and time shall be decided through mutual consultation according to the relevant content. | Noted and addressed. | Noted.
11 | General | 2.2 Work Package 1 - Project Management 2.2.1 Project management Team The proposal includes local project management in Seoul provided by Arup and supported by the technical design teams from Arup and ODE to manage all design works. ----> 1. Please inform us whether ODE will participate in Feed design or not. 2. Collaboration with domestic engineering company as a sub-contractor of ARUP for onshore design (Substation, Monitoring house, Warehouse, Switching station, Inland cable route, O&M port, etc.) and support for the preparation of local authorizations, licenses and permits for project implementation. 3. If there are services necessary for FEED in addition to the services being performed by the owner (Geotechnical investigation, Geophysical survey, Metocean study), it is included in the ARUP's feed design work scope |  |  |  | 1. Yes, ODE will participate in FEED design. 2. Yes, where necessary, Arup will engage sub-consultants in Korea to undertake tasks that require significant local inputs and/or interfacing. 3. Our proposed scope for the FEED service is given in Section 2 of the proposal. FEED may include different range of services depending on the particular project setting, client's requirement and project procurement arrangement. We are happy to discuss with HEC should they be interested in Arup providing services outside what has been described in the proposal | 1. Noted. However, ARUP to select the foundation design company through the competitive bidding process. 2. Noted. This should be discussed further. 3. This should be discussed further with the list of technical documents and their due dates which mentioned in No.5. 4. The participants of the Project Team should be agreed by AWC. | Noted. | Noted.
12 | General | 2.2 Work Package 1 - Project Management 2.2.2 Procedures and Documentation Project management procedures and documentation would be adopted as established early in concept design stage to ensure efficient and timely delivery. The following documents are proposed to be delivered: -----> ~ The following documents are proposed to be delivered but not limited to ; |  |  |  | Please refer to our response to item 14. | Noted. | - | -
13 | General | 2.0 Scope of Work ----> The results of additional geotechnical investigations, geophisical survey and Metocean study currently in progress should be reflected in the Feed design. In particular, the optimal WTG layout selection that secures economic feasibility according to site condition(water depth, soil condition etcs) should be added. In addition, Energy Yield Assessment Study of selected WTG shall be conducted. ----> The conference, presentations and meeting requested by HEC and/or SPC shall be conducted. |  |  |  | Noted. Please see the revised Work Package 2 for your consideration. | Noted. | - | -
14 | General | 2.2.2 Procedures and Documentation • Project Execution Plan and Schedule • Review of Site Investigation Report and Site Data (including additional geotechnical investigation, geophisical survey, metocean study) • T&I Method Study • Design Criteria Report (ME, CV, EL, Arch, C&I, etc.) • Subsea Cable Routing Study Report • Basic Design Report (WTG Substructure and Foundation) • Basic Design Report (Electrical System and Others) • Basic Design Report (OSS Topside, Substructure and Foundation) ---> Onshore( Juk-do Inland) Substation, Foundation, and onshore switching station(in yeonggwang-gun). • Basic Design Report (Monitoring House) • Bill of Materials ----> Please add the corresponding work package number(applied in table in section 3.1) for the documents above. ----> In case of onshore scope of work(Elec, Arch, Civil and all relevant disciplines), it apprear to be not reflected. Therefore, HEC would like to propose that it shall be added clearly and its work would be carried out by domestic(Korea) consultant, not ARUP since there are lots of constraints when designing considering local conditions |  |  |  | To allow better reading and avoid misunderstanding, Section 2.2.2 is revised and referring documents to be submitted to other Sections of this proposal. For "Review of Site Investigation Report and Site Data", it is absorbed in Work Package 2 now. For Design Criteria Report, please refer to the revised Work Package 3. Please also see the work package 9 and 11 for onshore scope of works. We shall engage local consultants, if necessary and appropriate, for works that may require particular local input. | 2.3 Work Package 2 – Site Conditions Please include subsections of review for geophysical survey and metocean study in Section 2.3. 2.4 Work Package 3 - Design Basis Please add a description which explains that design basis includes all the relevant contents required for ME, EL, CV, Arch, C&I, HVAC, etc. 2.10 Work Package 9 – Substation (Onshore / Island) 2.10.3 Other Disciplines Please add C&I, HVAC, etc. in Section 2.10.3. | The evaluations of site conditions will include a review of geophysical. Review of metocean studies was added as new section (3.3.3) The design basis documents will include all the relevant contents required for ME, EL, CV, Arch, C&I, HVAC, etc Noted. C&I and HVAC will be included in Work Package 9 and text in seciont 3.11.3 was revised accordingly | Noted. Please add ARUP's response in Section 3.4. And this shoud be notified to ISC as well. Please add ME in Section 3.12.3.
15 | General | 2.2.2 Procedures and Documentation ----> Please add the following documents. - Technical Note on Evaluation of Site Conditions(Environmentally Sensitive Area, Coral Reefs, Fishery Activities, Migratory Birds and Bird Habitats, Military Affairs, Cultural Properties, Nearby Large Infrastructure and Construction Projects, Shipping Routes, Proximity to Manufacturing Bases, etc.) - WTG Design Basis - Basic Design Report (WTG) - Micro-siting Study and Energy Yield Study - O&M Strategy - CAPEX and OPEX Estimate Report - RFQ (for Site Investigation for Detail Design Stage) |  |  |  | Noted. Apart from WTG Design Basis and Basic Design Report (WTG), reports requested in this comments are included in the revised proposal. Please see Section 2 of the proposal for details. WTG Design Basis and Basic Design Report (WTG) shall be developed by the WTG supplier. | 2.3.6 Technical Note on Evaluation of Site Conditions Preliminary review on site conditions was conducted in the concept design stage. A further review will be carried out on the available data of the follow items: Please revise the above as follows. Preliminary review on site conditions was conducted in the concept design stage. A further review will be carried out on the available data of the follow items but not limited to ; Please add 'Cultural Properties' in Section 2.3.6. Regarding WTG Design Basis and Basic Design Report(WTG), please add a relevant scope which can be priovided by ARUP as an optional service. | Noted and addressed. We don't have any item to propose as option service related with Design Basis. | Noted. Regarding WTG Design Basis and Basic Design Report(WTG), please add a relevant scope which can be priovided by ARUP. It is expected that there will be some scope by ARUP, even if WTG Design Basis and Basic Design Report (WTG) may be developed by the WTG supplier.
16 | General | 2.2.3 Execution Plan and Schedule Upon start of the project, execution plan and project schedule will be prepared and submitted to client. ----> The service execution plan should include at least the following documents. a. Service schedule. (용역 예정 공정표) b. Service detailed implementation plan. (용역 세부 시행계획) c. Service performing organization and Engineer’s personal information (list of participating engineers, duties, etc.). (용역 수행조직 및 기술자 인적사항(참여기술자 명단, 담당업무 등)) d. Engineer mobilization plan by field and grade. (분야별, 등급별 기술자 동원계획) e. Participating Engineer Security Memorandum. (참여기술자 보안각서) f. Security maintenance measures and detailed implementation plan. (보안유지 대책 및 세부 이행계획서) |  |  |  | Noted and addressed. | 2.2.3 Execution Plan and Schedule Upon the commencement of the project, the execution plan and project schedule will be prepared and submitted to client. The service execution plan should include but limited to the following documents: Please revise the above as follows. Upon the commencement of the project, the execution plan and project schedule will be prepared and submitted to client. The service execution plan should include but not limited to the following documents: In terms of service performing organization, please be noted that the involved engineers in this FEED stage shall have a experience in working with Siemens(WTG supplier) in order to conduct the relevant design smoothly without any delay. | Noted and addressed. | Noted. Regarding the experience requirement in working with Siemens, this shoud be notified to ISC as well.
17 | CV | 2.5 Work Package 4 - Primary steel Limit states will be considered in this stage for primary steel as follows: • Ultimate limit states (ULS) corresponding to the maximum load-carrying resistance. • Fatigue limit states (FLS) corresponding to failure due to the effect of cyclic loading throughout the entire worklife. • Serviceability limit states (SLS) for WTG foundation. • Seismic Limit State (ALS). • On Bottom Stability. ----> Please add a description with a table which clearly shows the number of design cases(limit state analysis cases) combined with conditions such as water depths, soil propiles, soil parameters, etc. |  |  |  | Please see revised text for Package 4 for your review. | Please add a description with a table which clearly shows the number of design cases(limit state analysis cases) combined with conditions such as water depths, soil propiles, soil parameters, etc. | WP04 is now under ISC's scope and this comment is included in section 3.19 to be addressed by iSC. | Noted.
18 | General | 2.5 Work Package 4 - Primary steel • On Bottom Stability. ----> Please change the phrase above into the following one. - On Bottom Stability for pre-piling template |  |  |  | Noted and addressed. | Noted. | - | -
19 | General | 2.5 Work Package 4 - Primary steel 2.6 Work Package 5 - Secondary steel ----> Please clarify whether boat impact anlaysis is required in FEED design stage. |  |  |  | Noted. Vessel impact assessment is now included in Work Package 4. | Please add a description which explains whether boat impact anlaysis is required or not in FEED design stage. Please clarify whether the actual structural design of secondary steel structure is conducted or not. | Boat (vessel) impact analysis is normally undertaken at the FEED stage to ensure sufficient robustness of the design to cater for such scenarios, although it is unlikely to govern the design. The structural design for the secondary steel will be undertaken to a FEED standard. This will include the general layouts and basic steel element sizing. However, it will not include the design details including connections. This sentence was added in section 3.6.1 Please note WP04 is now under ISC as client's request. so this will be further addressed by ISC | Please add ARUP's response in Section 3.5.5. - ARUP's response : Boat (vessel) impact analysis is normally undertaken at the FEED stage to ensure sufficient robustness of the design to cater for such scenarios, although it is unlikely to govern the design. Noted.
20 | General | 2.5 Work Package 4 - Primary steel 2.5.3 SLS Check The pile head rotation will be checked for jacket in FDDE design. ----> Please check the typo(FDDE -> FEED). |  |  |  | Noted and addressed. | 2.5.2.3 SLS Check SLS check for WTG jacket foundation is to check on natural frequency and the pile head rotation in FEED design. Please add an explanation for the reason why SLS is conducted for natural frequency and pile head rotation only and for whether it is enough in FEED desing stage. 2.5.2.4 ALS Check Following DNVGL’s definition of ALS, seismic load is considered as ALS. Besides seismic load, Tsunami, and accidental horizontal impact load by crew transfer vessel will also be considered as the event in ALS. At the FEED design stage, only the seismic check is considered. Please add an explanation for the reason why ALS is conducted for seismic check only and for whether it is enough in FEED desing stage. | WP04 is now under ISC's scope and this comment is included in section 3.19 to be addressed by ISC. | Noted.
21 | General | 2.5.5 Integrated Load Analysis In FEED design, ILA will be undertaken by WTG supplier, Arup will coordinate with WTG supplier for ILA and foundation design. ----> Please specify ARUP's detail scope in the ILA for FEED design. |  |  |  | Noted and addressed. | Noted. | - | -
22 | General | 2.5.5 Integrated Load Analysis Arup proposes to run 1 round of iteration based on the time constraint for FEED. If time allows, an additional round of iteration will be performed. Total of two iterations after Concept Design are assumed as follows. ----> Please confirm whether reasonable and necessary results for FEED design can be achieved by conducting just 1 round of iteraion. Compared to detail design stage, please specify each margin of error in the FEED design when conducting 1 round of iteration and 2 round, respectively. ----> Please check whether the underlined phrase is typo. |  |  |  | Noted and revised the typo. For the given time, it is anticipated only one round of iteration could be achieved. The margin of error depends on a number of factors and project specific, therefore it is difficult to provide such estimate. | Regardless of the given tight time schedule, please clarify whether reasonable and necessary results for FEED design can be achieved by conducting just one round of iteraion. If not, please suggest proper number of iteration and schedule which are required to get the reasonable and necessary results for FEED design. Based on ARUP-ODE's previous projects and relevant experience, please provide a generally expected margin of error in the FEED design when conducting one round of iteration. Through the experience in working with Siemens, please clarify that the process of ILA is matched with general procedure of Siemens and there is any specific requirement of Siemens during ILA period. In addition, please address the general duration of 1 round iteration and 1&2 round interation when cooperated with Siemens. | WP04 is now under ISC's scope and this comment is included in section 3.19 to be addressed by iSC. | Noted.
23 | General | 2.5.5 Integrated Load Analysis 1st Iteration Wind and wave loads in DLCs are simulated for a representative location with BLADED by WTG supplier. ----> In the concept design stage, three locations(three water depths(-16, -22, -27 mDL) with design soil profile 2(deep rockhead)) have been considered. Please specify whether ILA for all the three locations is conducted. If not, please add a reasonable explanation for considering a representative location only in ILA. |  |  |  | Noted. Please refer to the number of grouping suggested in the revised Work Package 4. | 2.5 Work Package 4 – WTG Supporting Structure (Primary steel) 2.5.1 General Given the tight time schedule, and the fact that WTG foundations will be individually optimised in the detailed design stage, WTG foundations will be grouped in the FEED design based on: • Geological conditions • Water depth A maximum of six groups will be developed to cater for the variation of the abovementioned factors. The number of groups should not be fixed here and it should be decided later according to site conditions. | Noted. | 3.5 Work Package 4 - WTG Supporting Structure (Primary steel) 3.5.1 General The number of groups shall be decided later in accordance with the site conditions. Please revise the above sentence as follows. - Some groups will be developed to cater for the variation of the abovementioned factors. The number of groups shall be decided later in accordance with the site conditions.
24 | CV | 2.5.6 Pile Driveability Assessment The following detailed procedure has been used for driveability assessment with GRLWeap: • Adopt the dimensions of the pile from concept design: pile length, diameter and wall thickness; • Establish the representative ground profile at the pile location; • Select the initial type of driving equipment; • Calculate the Soil Resistance to Driving (SRD); • Assess the ability to reach the required toe level. ----> Please add the following sentence in this section. - Pile driveability assessment shall be conducted at all the additionally-available actual boring locations. |  |  |  | Noted and addressed. | 2.5.3 Pile Driveability Assessment Please add the following sentence in this section. - Pile driveability assessment will be conducted at all the additionally-available actual boring locations. | Noted. Please advise how many boreholes should the assessment carried out. | They are is all the boreholes in the geotechnical investigation currently being held.
25 | General | 2.5.7 Cathodic Protection ----> All steel structural conponents which shall be applied of cathodic protection are clearly designed and expressed in this FEED documents with specification including BM sheet |  |  |  | Noted and addressed. | Noted. | - | -
26 | General | 2.6 Work Package 5 - Secondary steel 2.6.1.2 External Working Platform Definition of loading requirement from the client and WTG manufacturer will be required at an early stage. 2.6.1.3 Davit Crane Support The davit crane requirements in terms of crane capacity and outreach shall be agreed on at an early stage. 2.6.1.4 Internal Platforms and Access It is assumed that the internal platforms and access strategy has already been established within Stage 1. ----> Please rephrase the underlined phrases to show which stage they mean. |  |  |  | They are removed to avoid confusion. | 2.6.2.3 Davit Crane Support The davit crane requirements in terms of crane capacity and outreach shall be agreed on at an early stage. Please rephrase the underlined phrases to show which stage it means. | They are removed to avoid confusion. | Noted.
27 | General | 2.6.1.4 Internal Platforms and Access Arup notes that a poorly detailed support arrangement for airtight platforms can lead to high stress concentrations on the Jacket and additional fabrication costs. The nature and position of the airtight platform needs to be coordinated with the form of the Jacket-TP connection. Innovative approaches towards achieving the airtight seal could avoid welded details at sensitive locations which may drive the primary steel can thickness. This could include suspending the internal platforms from a higher elevation or consideration of innovative ring seal, depending on the preferred Jacket-TP connection solution. ----> Please add a description with a picture which explains what internal platform and airtight platform are. ----> Please clarify whether the internal plataforms mean the platforms inside of tower. |  |  |  | Please note that details will be developed during FEED stage. | Before contract, HEC needs to check what they are. Therefore, please add a description with a picture which explains what internal platform and airtight platform are. Please clarify whether the internal plataforms mean the platforms inside of tower. | The internal platforms refer to the platforms inside the wind turbine tower. The lower service platform does not need to be airtight. However, the upper platforms will need to be designed as airtight to protect the equipment inside the tower and turbine. These are different to the extrenal pltforms for boat landings and alike. This is all part of the overall secondary steel design. Please note that WP05 is now under ISC. | Please add ARUP's response in Section 3.6.2.4. - ARUP's response : The internal platforms refer to the platforms inside the wind turbine tower. The lower service platform does not need to be airtight. However, the upper platforms will need to be designed as airtight to protect the equipment inside the tower and turbine. These are different to the extrenal pltforms for boat landings and alike. This is all part of the overall secondary steel design.
28 | General | 2.6.1.6 Inter Array Cable Entry and Support Cable hangoff locations will be agreed with the client and may be at airtight deck level or further above, dependent on the installation strategy. ----> Please add the definition of 'airtight deck' with a picture and specify the typical level or location of the airtight deck. |  |  |  | Please note that details will be developed during FEED stage. | Noted. | - | -
29 | CV | 2.6.1.6 Inter Array Cable Entry and Support No J-tubes will be proposed internally, and the array cable is expected to pass through the wall of the jacket, via a cable protection system and run internally up to the cable hangoff. ----> Please rephrase the sentence above for clear understanding. Please clarify whether the sentence above means that a typical external J-tubes are not used and the cable between seabed and hangoff at the bottom of TP is attached to the internal surface of jacket leg with a cable protection system. If our understanding is correct, please add the reason why the method mentioned above is adopted. ----> Please add the meaning of 'the wall of the jacket'(inside or outside of leg) and specify the typical level or location of the cable hangoff. |  |  |  | Please note that details will be developed during FEED stage. | Noted. | - | -
30 | General | 2.6.2 LV Electrical Design The foundation structure LV electrical detail design will consider the following systems: Value Statement: Arup acknowledges complexities of the LV and ELV system interfaces which we will proactively manage through Detail Design stage. Our knowledge of specialist electronic (ELV) systems, for example; Navigation Aids, CMS, ICCP, CCTV, Bird Strike, Radio Comms and interfaces with shore-based SCADA systems puts us in a good place to ensure systems integration is considered as part of the detail design process. ----> It seems that Section 2.6.2 is descriptions for detail design stage, not for FEED design stage, when considering not only the contents itself of Section 2.6.2 but also the sentences above. Please revise Section 2.6.2 for FEED design stage. |  |  |  | Noted. The description has been revised to fit with the level of details for FEED | Noted. | - | -
31 | General | 2.6.2 LV Electrical Design • Navigational Aids – including; marine lanterns, visibility meters and fog horns, AIS, ID marking floodlights etc. ----> Please add the meaning of AIS. |  |  |  | Relevant text has been revised to suit the level of detials for FEED. | Noted. | - | -
32 | General | 2.9 Work Package 8 - Review of available port ----> It is necessary to check whether this Work Package is necessary. It has already been confirmed that "Mokpo New Port" is being applied. Figure 2.4 Example of potential suitable Ports in Korea ----> Please specify the meaning of OSW. |  |  |  | Noted and revised. "OSW" means "offshore wind". | Noted. | - | -
33 | General | 2.9.1 Port & Hinterland Review The role of the Foundations Marshalling Port (FMP) is shown in above figure and the requirements are based on ----> Please add the figure mentioned above. Figure 2.4 does not show FMP. |  |  |  | Figures have been deleted to avoid confusion. Those graphical representations are not required for the propose of FEED proposal. | Noted. | - | -
34 | General | 2.9.1 Port & Hinterland Review • HEC to confirm whether the responsibility of the FMP is drafted into tendering contractors ITT or remain the responsibility of the HEC • HEC to confirm whether the WTAP Port responsibility is handed down to the WT supplier or would it not be included in the ITT. ----> Please confirm that the assessment of FMP & WTAP shall be conducted by ARUP during feed design stage. |  |  |  | Please see the revised text in Work Package 8 | 2.9.2 Preparation of Available Port Plan for OWF Construction In this proposal, we assume the responsibility of the FMP will be drafted into tendering contractors. Please clearly show who 'tendering contractors' are. Please clarify the meaning of WTGP Port responsibility. For reference, EPC contractor will lease the WTGP(Mokpo new Port) based upon the requirement of WTG supplier. Depend on your reply, its scope of work may be included to Arup. | WP08 is now under ISC's scope and this comment is included in section 3.19 to be addressed by iSC. | Noted.
35 | General | 2.9.1 Port & Hinterland Review HEC to confirm whether the WTAP Port responsibility is handed down to the WT supplier or would it not be included in the ITT. ----> Please check the typo(WTAP -> WTGP). |  |  |  | Noted and addressed. | Noted. '2.9.3 Preparation of Hinterland Plan for Equipment & Substructure Assembly We propose the scope of works includes Foundation Mashalling Port (FMP) but excludes Wind Turbine Assembly Port (WTAP). At this stage we assume the WTGP Port responsibility is handed down to the WTG supplier. Comment not addressed. Please use one word(WTAP or WTGP) uniformly if its meaning is same. | Apology for the typo. It is revised now. | Noted.
36 | General | 2.9.3 Preparation of Hinterland Plan for Equipment & Substructure Assembly Arup will exclude costing and cost estimates at this stage. ----> Reference data for cost estimate should be provided at FEED stage. |  |  |  | This has been revised. | Noted. '2.9.3 Preparation of Hinterland Plan for Equipment & Substructure Assembly We propose the scope of works includes Foundation Mashalling Port (FMP) but excludes Wind Turbine Assembly Port (WTAP). At this stage we assume the WTGP Port responsibility is handed down to the WTG supplier. 1. Abovementioned services(2.9.3) shall be include the Wind Turbine Assembly Port(WTAP) with WTG assembly data and assembly port data 2. Comment not addressed. Please use one word(WTAP or WTGP) uniformly if its meaning is same. | 1. Noted. 2. Apology for the typo. It is revised now. | Noted. 3.11 Work Package 9 – Installation and O&M Ports 3.11.1 Installation Port: Preparation of Hinterland Plan for Equipment & Substructure Assembly In this proposal, we are assumuing that our responsibility is limited to the layout of the installation port, warehouse and the FEED of the construction management office (WP12) but ~. 3.11.2 O&M Ports: Preparation of Available Port Plan for OWF Construction In this proposal, we assume our responsibility is limited to preliminary sizing and layout of the port, warehouse and FEED of O&M offices (WP12). Please check whether the underlined phrases are typo. If they are not typo, please add the relevant description in WP12(Monitoring Houses).
37 | General | 2.10 Work Package 9 - Substation (onshore) • Proposal of basic direction for OSS operation plan. • Review of plans to establish power control system for OSS • Review scale and necessary facilities of OSS • Ground connection, lightning protection system and corrosion proof system plan for OSS • Fire protection and fire escape facilities plan for OSS • Review of load and structure of OSS ----> Please check whether 'OSS' in the phrases above is typo(OSS -> SS). |  |  |  | Noted and addressed. | Noted. | - | -
38 | General | 2.10 Work Package 9 - Substation (onshore) Arup understands that the general purpose of the SS topside scope of work is to screen the main electrical architecture options and propose best trade off to HEC, in terms of operability, reliability, losses, cost, planning and risks on the OSS topside system. Arup will produce the electrical Single Line Diagram (SLD) of the overall electrical infrastructure from the OSS to the onshore grid interface point. ----> Please clarify the reason why the terms such as topside, OSS are used in the sentences above, even though it is assumed to adopt an island onshore substation in this proposal for FEED design. |  |  |  | Noted. Relevant text has been revised in Work Package 9 | Noted. | - | -
39 | General | 2.10 Work Package 9 - Substation (onshore) From the main equipment list, Arup will extract the information applicable to the OSS and compile a separate list focusing on the main equipment, utilities and other functionalities that we deem necessary for the SS FEED design. Arup will issue a weight/size estimate of the equipment. The Electrical team will work together with the structural teams, through weekly design meetings to identify gaps and opportunities on the topside weight/size and refine the overall design. Arup will add value to the project by searching ways to optimize the substation footprint for example by arranging the transformer compound, switchgear rooms, control room etc. in such a way to reduce space requirements whilst ensuring practical operation. The outcome will include the following:- • An overall equipment layout (in high-level blocks of drawing) at the OSS • The weight & size (length, width and height) of main equipment • The weight of bulk (via the use of ratio) • The weight of structure (via the use of ratio) Arup notes that the weight estimate shall not include contingencies. ----> It seems that the paragraph above is descriptions for OSS and detail design stage, not for Onshore Substation and FEED design stage, because of underlined phrases. Please revise whole contents properly for Onshore Substation and FEED design stage. |  |  |  | See our reply to item 38 | Noted. | - | -
40 | General | 2.10 Work Package 9 - Substation (onshore) In estimating equipment size and weight, Arup will rely on publicly available information and our internal benchmarks. We may also engage main equipment OEMs as appropriate to understand the potential and limitations of a given technology and consider the technological developments and room for innovation for the project. The figure shows an example of the OSS main deck substation layout. Figure: Example of main equipment layout for OSS main deck ---> It seems that the paragraph above is descriptions for OSS, not for Onshore Substation, because of underlined phrases. Please revise whole contents properly for Onshore Substation. |  |  |  | See our reply to item 38 | Noted. | - | -
41 | General | 2.10 Work Package 9 - Substation (onshore) Separately, Arup will define the anticipated surface of the onshore substation, using the bottom-up approach similar to the OSS approach. Arup will produce preliminary layout drawings for the onshore substation. ----> Please add detail description for both onshore substation(in jukdo island) and onshore switching station(in yeonggwang-gun). |  |  |  | See our reply to item 38 | Noted. | - | -
42 | General | 2.11 Work Package 10 - Monitoring House 2.11.3 Refinement of Conceptual Facilities The facilities provided in this report shall be refined upon the receipt of WTG supplier requirements on O&M facilities. ----> Please specify what 'this report' above is. |  |  |  | The paragraph is revised as follows: "The facilities provided in the report mentioned in Section 2.11 shall be refined upon the receipt of WTG supplier requirements on O&M facilities." | Noted. 2.12.4 Reference Design for Monitoring Houses In the FEED stage, we will develop the reference design for monitoring houses, to the level that is sufficient for EPC tendering and facilitate subsequent detailed design work. The following aspect will be covered: • Architecture • Civil • Structure and geotechnics • Building services In addition to the above, please add EL, C&I, HVAC, etc. From the revise work package 11 - Monitoring house, please clarify whether the switching station(located in mainland) design is also considered to this work package or not. | EL, C&I and HVAC etc will be included in the FEED The switching station will be included in this package as required. | Please add ME, EL, C&I and HVAC, etc in this section(Section 3.14.5). Please clarify whether the switching station is included in WP10 Substation(Onshore/Island) or in WP12(Monitoring Houses).
43 | General | 2.12 Work Package 11 - Transporation and Installation Preliminary transportation and installation (T&I) assessment had been performed based on the preliminary design and selection of WTGs and their foundations, inter-array cables, offshore sub-station, export cables, onshore cable and onshore sub-station as in the below deliverable of concept design stage. • AWF-ARUP-V-09-002 Transportation & Installation Method Study Report In FEED design stage, T&I assessment will fouce on one WTG and one foundation type based on updated site-specific data and the results from ILA. ----> In addition to the above, Case for Island Onshore Substaion should be considered in T&I assessment for FEED design. |  |  |  | It has already been mentioned in the same sentence, extracted below for easy reference: "Preliminary transportation and installation (T&I) assessment had been performed based on the preliminary design and selection of WTGs and their foundations, inter-array cables, offshore sub-station, export cables, onshore cable and onshore sub-station as in the below deliverable of concept design stage." | 2.9 Work Package 8 – Transportation and Installation In our understanding, the 'onshore sub-station' is SS on mainland, not on island. That is why we made the original comment. Therefore, please add the following sentence in this section. - Case for Island Onshore Substaion will be considered in T&I assessment for FEED design. | Noted and addressed. | Noted.
44 | General | 2.13 Work Package 12 - Bill of Material The general items and approximate quantity for foundations, electrical systems and subsea cables, and WTGs were estimated in concept design stage as in the below deliverable. • AWF-ARUP-V-21-001 Bill of Material In FEED design stage, detailed estimation will be made based on one WTG and one foundation type. ----> In addition to the above, Case for Island Onshore Substaion should be considered in FEED design. ----> In case of work for onshore(Juk-do and mainland), relevant RFQ will be quoted to domestic(local) vendor or subcontrator. Accordingly, related BM(BOM) shall be prepared and provided by domestic design company and let them handle ----> If possible, please send the reference BM sheet for FEED stage in advance in order to check whether the provided reference will be useful or not |  |  |  | The paragraph is revised as follows: "The general items and approximate quantity for foundations, electrical systems, sub-stations, and subsea cables, and WTGs were estimated in concept design stage as in the below deliverable." Noted your comment on onshore work. We shall take note of that during our FEED work. Reference BM will be provided in the early stage of the FEED service for HEC's review. | The paragraph should be revised as follows: "The general items and approximate quantity for foundations, electrical systems, sub-stations, and subsea cables, and WTGs were estimated in concept design stage as in the below deliverable. • AWF-ARUP-V-21-001 Bill of Material In addition to the above, Case for Island Onshore Substaion will be considered in FEED design. In FEED design stage, FEED level estimation will be made based on one WTG and one foundation type." Noted. Noted. BOM(Bill of Material) Arup made in concept design stage is quite insufficient for quotation, especially there is no BOM for onshore work. Therefore, in this FEED stage, its BOM shall be prepared upto FEED level estimatation in detail to all parts. In addition, as HEC mentioned and your reply, please keep in mind that all BOM(civil, architecture, HVAC etc.) by LSC(local sub consultant) shall be prepared for quotation to korea vendor(market) with korean standard BOM form. Furthermore, some of Arup's work scope(e.g. monitoring house in view of architecture design) also shall be considered likewise. | Noted. This will be notified in the proposal and will be develped by ISC | Noted. Noted.
45 | General | 3 Deliverables and Timescales 3.1 Proposed Deliverables Some of the deliverables are available in modifiable format (e.g. .doc, .dwg). ----> Please change the sentence above into the following one. - All of the deliverables are available in modifiable format (e.g. .doc, .dwg). ----> Please add the timescale for clarity |  |  |  | Noted and addressed. The proposed delivery programme is given in Section 3.2 | Noted. Timescale(Appendix A) is still not reflected in this proposal. Please add it | Timescale as Appendix is provided. | Noted.
46 | General | 3 Deliverables and Timescales 3.1 Proposed Deliverables Table ----> Please add the following documents. - RFQ (for Site Investigation for Detail Design Stage both offshore and onshore) ----> Please add the following sentence as note. - All the design reports shall include the corresponding drawings, calculation reports, bill of materials, etc. ----> Please add the Site data review report which shall include the additional site data(geotechnical investigation, metocean study etc.) and project overall schedule |  |  |  | Noted and addressed. | Noted. | - | -
47 | General | 3 Deliverables and Timescales 3.1 Proposed Deliverables Table ----> Please fill the blank in 'Refers to Scope of Services Item' for No.13.1. |  |  |  | Noted and addressed. | Noted. Please check whether the column 'Refers to Scope of Services Item' in Table include all the subsections of Section 2. | Correct. It should include all subsections of Section 2. | Noted.
48 | General | 4 Fee 4.1 Remuneration 4.1.1 General we assume that the contract for the Design Services will be formed between the Dohwa Engineering and Arup. Our Client will be Dohwa Engineering during the whole course of the services. ----> Please check typo error. |  |  |  | Noted and revised to "Hyundai Engineering Co.". | Noted. | - | -
49 | General | 4 Fee 4.1 Remuneration 4.1.2 Lump Sum Fee Commencement of the work shall be upon receipt of written confirmation to proceed from the client and receipt of the mobilisation fee. ----> To be discussed later. (During the contract negotiation stage) |  |  |  | Noted. | 4 Fee 4.1.2 Lump Sum Fee 8. Our reports will be prepared in English --> In terms of report by LSC(Local sub consultant), some reports or deliverables may be written in Korean and English. It will be further discussed later (During the contract negotiation stage) 4 Fee 4.4 Expense 1) Fees for any local consultants. 2) Fees associated with the purchase of data, maps and satellite images etc. as required. The client will be invoiced at cost for the purchase of this data. 1) If the indicated fee is related to LSC(local sub consultants), it shall be included. 2) To avoid the expense during FEED stage by client, Arup should consider the fee associated the purchase of mentioned information in advance | Noted. | Language for document should be dicussed further. The relevant descriptions in this proposal have not been revised yet in Section 5.4.
50 | EL | 1.4 Design Requirements One type of substation (Onshore Anma Island) ----> It shall be changed from One type of substation (Onshore Anma Island) to One type of substation (Onshore Jukdo Island) |  |  |  | Please refer to our response to item 3. | Noted. | - | -
51 | EL | 2.2.2 Procedures and documentation • Basic Design Report (OSS Topside, Substructure and Foundation) ----> "Basic design report for island substation" shall be considered for the feed design stage. As previously noted, HEC and the owner are considering an onshore(in jukdo island) substation rather than an offshore substation. |  |  |  | Please refer to our response to item 14. | Noted. | - | -
52 | EL | 2.5.7 Cathodic Protection ----> Arup must select the final CP system method(GACP or ICCP) for each type of steel structure item in the feed design stage. When applying GACP, appropriate capacity and quantity of anode must be presented, and when applying ICCP, system configuration must be presented. |  |  |  | Noted. | Noted. | - | -
53 | EL | 2.6.1.6 Inter Array Cable Entry and Support ----> Please present a drawing which including plan, section, detail view for this matter at the feed design stage. |  |  |  | Noted. | Noted. | - | -
54 | EL | 2.6.2 LV Electrical Design Our knowledge of specialist electronic (ELV) systems, for example; Navigation Aids, CMS, ICCP, CCTV, Bird Strike, Radio Comms and interfaces with shore-based SCADA systems puts us in a good place to ensure systems integration is considered as part of the detail design process ----> Even though ELV systems are considered as part of the detail design process, HEC request Arup to submit typical schematic, block diagram for each ELV system for our project. |  |  |  | Noted. Revised text is given in Section 2.6.3. | Noted. | - | -
55 | EL | 2.8.3 Export Cable routing study ----> For your reference, HEC and owner are considering O/H transmission line about 1.4 km Within Songi Island. |  |  |  | Noted. | 2.8 Work Package 7 - Electrical Cables --> In this revised work package 7, please confirm that onshore cable route (juk-do island and switching station to Younggwang No2 SS) civil design(layout and section drawings etc) also shall be added. | We confirm that the onshore cable route (Juk-do island and switching station to Younggwang No2 SS) civil design (layout and section drawings etc) also shall be included within the scope of works. | Please add ARUP's response in this section.
56 | EL | 2.10 Work Package 9 - Substation (onshore) ----> HEC understand that this item includes both onshore substation(in jukdo island) and onshore switching station(in yeonggwang-gun). |  |  |  | Please see our revised text for Work Package 9 | Noted. | - | -
57 | [6 empty] | 1. Introduction 1.5 Structure of this Proposal 1. FEED Structure Team needs to be re-discussed with HEC. The most competent foundation design company who have the sufficent capability and track records should be selected. ARUP shall select the foundation design company through the competitive bidding process 2. Deliverables and Timescale need to be re-discussed with HEC 3. Arup's Fee should be broken down for each work package. | 1. Noted. we would like to use this opportunity to stress both Arup and ODE are competent foundation design companies who have designed numerous foundations for offshore structures including many offshore wind farms around the world. Both companies pride themselves on quality and design excellence with sufficient depth of experienced staff to deliver the project with a good mix of local and international staff. Tendering for an alternative foundation design company through a competitive bidding process runs the risk of destabilising the flow of the design process which has been achieved through close cooperation between the respective parties. Notwithstanding this, the FEED document has been divided into sections with clear divisions of work scope to allow for competitive bidding of the foundation works by a foundation design company on the basis that Arup maintains the overall lead project design role. 2. Noted. 3. Noted. When we have clear visibility of scope, timescale we will propose the fee nad its breakdown | 1. 사업팀 확인 필요. 2. Noted. 3. Noted.
58 | [6 empty] | 1.7 Assumptions, Exclusions and Limitations 1. The Certification Process for Design Basis will be performed by AWC and its consultants separately. 2. Please define clearly the additional round of comments. | 1. Ceritifation process will be led by AWC while consultants will support AWC. Details of consultant's activities are shown in section 3.19 2. Setence was revised and "additonal rounds of comments" was deleted | 1. Noted. (사업팀 확인 필요). 2. Noted.
59 | General | [5 empty] | 2.3 Work Package 2 – Site Conditions 2.3.2 Geotechnical Interpretative Report -> Additonally, ground investigation of Island Substation and Onshore faiclities shall be carried out for GI information. After the location of the structures ares confirmed, ARUP should prepare an RFQ for ground investigation.. | Noted. In Section 3.3.7, we stated "We shall prepare ground investigation plans and the associated RFQ for both island substation and onshore facilities for HEC’s tendering purposes. We assume the tendering and contract work will be handled by HEC." | Tendering and contract work will be handled by SPC. (사업팀 확인 필요)
60 | General | [5 empty] | 2.3 Work Package 2 – Site Conditions 2.3.4 Seabed Mobility and Scour Study Report Review on Metocean study's report, currently being conducted by DHI should be included in arup's work. Similarly, scour study will be conducted to confirm the possible scouring depth that would be developed around the WTG foundation. Please confirm whether it is a normal practice not to consider scour protection in jacket design. If correct, please be noted that scour study should be conducted properly for jacket design. | We understand both Seabed mobility and scour study is being conducted by DHI and Arup will review the report. Related wording was revised in section 3.3.4 Scour should be checked for all sub-sea foundations although this is usually less critical for jacket foundations. | Noted. Please confirm whether it is a normal practice not to consider scour protection in jacket design. And add the relevant contents in this section.
61 | General | [5 empty] | 2.4 Work Package 3 - Design Basis Based on the above, design basis will be prepared in the FEED stage for the following items: 1. Wind turbines and their supporting structures; 2. Substations; 3. Power cables; The development of design basis shall follow the relevant DNVGL guidance: • DNVGL-SE-0073 Project Certification of Wind Farms According to IEC 61400-22 For item 1 – wind turbines and their supporting structures, given the project will be procured under an EPC arrangement, the development of the design basis will be up to Part A as defined in DNVGL-SE-0073. Where appropriate, Arup will support and provide necessary input to the turbine supplier for their development of the Part B design basis. Arup will also develop the necessary background information for the future development of Part C design basis under the EPC detailed design stage. 1. Please add a brief description which explains what the Part A, B and C in DNVGL-SE-0073 mean. 2. Need to describe the further detail of design basis of foundation package, electrical package and certification package. | 1. Item 1 (wind turbines and their supportin structures) of WP 3 is ISC's scope and this comment is included in section 3.19 to be addressed by iSC. 2. Description of Item 1 will be further elaborated by ISC. Arup will elaborate item 2 and 3 in the next revision, say, 18 Feb. | WP3(Design Basis) is not included in Section 3.19(Client’s Requirements on ODE’s scope) yet. Please revise it properly. Please add a brief description which explains what the Part A, B and C in DNVGL-SE-0073 mean.
62 | General | [5 empty] | 2.5 Work Package 4 – WTG Supporting Structure (Primary steel) 1. HEC prefers single engineering company which can design primary steel & secondary steel simultaneously. 2. The timeline and R&R matrix should be defined for Integrated Load Analysis and Foundation Design Loop. | 1. Noted. the Secondary steel design is now under ISC. 2. WP4 is now under ISC's scope and this comment is included in section 3.19 to be addressed by iSC. | 1. Noted. 2. Please add the following comment in Section 3.19(Client’s Requirements on ODE’s scope). - The timeline and R&R matrix should be defined for Integrated Load Analysis and Foundation Design Loop.
63 | General | [5 empty] | 2.5 Work Package 4 – WTG Supporting Structure (Primary steel) 2.5.2 Pile Design & Integrated Analysis Please change the title of Section 2.5.2 properly. | Noted. The title is changed to 3.5.2 Foundation Design and Integrated Analysis | Noted.
64 | General | [5 empty] | 2.5 Work Package 4 – WTG Supporting Structure (Primary steel) 2.5.2.5 Integrated Load Analysis In FEED design, ILA will be undertaken by WTG supplier, and Arup will coordinate with WTG supplier for ILA and foundation design. In ILA, Arup will check and update the foundation design based on the updated design loads from WTG supplier, and provide required design information (e.g. foundation geometry, adopted masses, soil springs, modal results, etc.) to WTG supplier for next round of ILA. Arup proposes to run one round of iteration given the time constraint for FEED. Selected loadcases that are considered most influential to the design will be chosen for this ILA process. This will be jointly agreed with the WTG supplier. The purpose of this round of ILA (known as ILA0) is to set up the mechanism of data input and transfer between WTG supplier and foundation designer, and ensure smooth iterative design process in the subsequent rounds, which is likely to happen in the detailed design stage. 1. Please provide a detail description for "ILA0" where the scope and work flow of WTG supplier and ARUP should be clearly explained. At this moment, it is not clear. 2. We request the cost by breaking down the primary round base and the secondary round option. | WP4 is now under ISC's scope and this comment is included in section 3.19 to be addressed by iSC. | Noted.
65 | General | [5 empty] | 2.5.6 Ground Investigation for Detailed Design We shall prepare ground investigation plan and the associated RFQ for tendering process. We assume the tendering and contract procurement work will be handled by HEC. Please move this section into Section 2.3 Work Package 2 - Site Conditions. And add 'both offshore and onshore' in the title of section. | Noted. The section has moved to 3.3.8 under WP 3 Site Conditions | Noted.
66 | General | [5 empty] | 2.7 Work Package 6 - Grid conneciton plan 1. The competent local company should be recommended to HEC and approved. 2. Need to add the specific sub-consultant who will do Grid connection works 3. The number of modelling and calculation should be discussed further. 4. Need to describe the further detail of SCADA in the broader view inclduing LV works at WTG to KEPCO's substation | 1. we are contacting several local power design company to advise us and its name will be shared to HEC. 2. Electrical design will be carried out by Arup but local consultant will advise the code and local practice. 3. The method of modelling shall be further elaborated by 18 Feb. 4. Further details of the LV SCADA connections shall also be included by 18 Feb. | 1. Noted. 2. Noted. (사업팀, 전기 확인 필요) 3. Noted. 4. Noted.
67 | General | [5 empty] | 2.8. Work Package 7 - Electrical Cables 1. Dynamic Cable? We don't use any floating structure for the Anma project. Please elaborate for the need of dynamic cable. 2. Landfall(landing point) study should be included as optional service. 3. CBRA(Cable Burial Risk Assessment) for export and IAC should be included. | 1. We confirm this is a typographical error. Deleted from sentence 2. The landfall landing point study is included in FEED as basic scope (see Section 3.9.4). 3. The CBRA shall be included. | 1. Noted. 2. 사업팀, 전기 확인 필요 3. Noted.
68 | General | [5 empty] | 2.9 Work Package 8 - Transportation and Installation 1. Need to describe the further detail of the foundation intallation plan 2. Installation scenario study should be included. 3. Deliverables of installation study (such as Gantt chart) should be specified. Simulation using Shoreline's Construction Design or equivalent should be used. 4. Method Statement should be included. MS should cover risk assessment. Documentation support for MWS(Marine Warrannty Survey) should be covered. 5. Recommendation of Installation vessel should be specified. | WP8 is now under ISC's scope and this comment is included in section 3.19 to be addressed by ISC. | Noted.
69 | General | [5 empty] | 2.11 Work Package 10 - Operation and Mainrnance 1. Please elaborate further detail on O&M package. 2. Simulation based O&M strategy to be refined. As noted in the report, Shoreline O&M Design should be used. - OPEX study in associated with failure rate - LTSA T&C strategy - O&M organisation - etc | WP10 (now WP11) is now under ISC's scope and this comment is included in section 3.19 to be addressed by ISC. | Noted.
70 | General | [5 empty] | 2.14 Work Package 13 - Tender packages (ITT) support 1. No need to prepare RfP for Wind Turbine Generators 2. Need to describe the clear division of matrix between WTG contractor and EPC contractor. | 1. Noted and removed. 2. WP13 (now WP14) is now under ISC's scope and this comment is included in section 3.19 to be addressed by ISC. | 1. Noted. 2. Noted.
71 | General | [5 empty] | 2.14 Work Package 13 - Tender packages (ITT) support 2.14.2 Technical Specifications 2.14.3 Request for Proposal In case of 2.14.2 & 2.14.3 which will be conducted by LSC(local sub consultant), some deliverables may be prepared both in English and Korean It will be further discussed later (During the contract negotiation stage) | Noted. | Language for document should be dicussed further.
72 | General | [5 empty] | 2.16 Work Package 15 – Support to Certifications (Optional) If requested, we will provide the technical support to HEC to gain certifications, such as DNVGL. The supporting activities include: • Additional packaging of report for submission to certifier • Response to certifier’s comments • Attend meetings with certifiers to explain design rationale and analysis methodologies to facilitate the certification process Notwithstanding the above, we will not be responsible for provide any local professional engineer (or similar) signatory / endorsement for permit applications. 1. Support to Certifications shall be include in base offer. 2. Support for technical documentation for CB(Certification Body) should be included. | Agreed. WP15 (WP16) is now changed to basic scope | Noted.
73 | General | [5 empty] | 3. Diliverables and Timescales 3.1 Proposwd Deliverables 1. Please recheck whether all deliverables are sufficient for EPC contract and EPC's detailed design 2. O&M Strategy Report should be sufficiently specific to meet Lenders' expectation. | We consider that all major deliverables required by the EPC to understand the project risks are included in the FEED proposal which also takes consideration of the time available. If there are specific studies that are deemed necessary to reduce any perceived risks, these may be considered for inclusion. 2. Noted. This comments was included in section 3.19 to be addressed by international sub consultant when submitting the proposal. | 1. This should be discussed further. 2. Noted.
74 | General | [5 empty] | 4. Fee 4.3 Additional Scope of Works Addional Scope of Works should be minimized. | Noted | Noted.
75 | General | [5 empty] | FEED Team Structure Please Include a top frontier company for the substructure design. | Added in the chapter 2 | Noted. (사업팀 확인 필요)
76 | General | [5 empty] | Projects with Siemens -->Please address the additional experiences in working with Siemens as well as asia projects. In this experience, project name, country, total & unit WTG capacity and ILA conducted or not etc. shall be addressed. | This comment is included in section 3.19 to be addressed by ISC. | Noted.
77 | AR | 3.11 Work Package 13B - Bill of Material 3.11.1 Exclusion • BoM of Primary and Secondary steel ----> What structure is primary and secondary steel for?
78 | AR
78 | AR