## 팀 표준 Finish Style No 체계
Interior Finish - Finish Style Name & Numbering
* 동일 Finish Material 의 두께, Size, 높이가 다른 경우 => 별도 구분 않함.
Floor | Finish Style Number | Finish Style Name (Key Name) | Ref. Size, Thickness | Base Material | Finish 1 (Work Master) | Finish 2 (Work Master) | Finish 3 (Work Master) | Finish 4 (Work Master) | Remark
Painting | F01 | Acrylic Emulsion Paint on Steel Trowel Finish |  | Concrete Slab | Steel Trowel Finish |  | Acrylic Emulsion Paint
| F02 | Water Emulsion Paint on Steel Trowel Finish |  | Concrete Slab | Steel Trowel Finish |  | Water Emulsion Paint
| F03 | Acid Resistant Paint on Steel Trowel Finish |  | Concrete Slab | Steel Trowel Finish |  | Acid/Alkaline Resistant Paint
| F04 | Oil Based Paint on Steel Trowel Finish |  | Concrete Slab | Steel Trowel Finish |  | Oil Based Paint
| F05 | Anti-Dust Paint on Steel Trowel Finish |  | Concrete Slab | Steel Trowel Finish |  | Anti-Dust Paint
| F06A | Non-Slip Epoxy Paint on Steel Trowel Finish |  | Concrete Slab | Steel Trowel Finish |  | Epoxy Paint |  | Epoxy Paint (용제형, 0.1mm 이하) : epoxy resin + polyamine hardener(경화제)
| F06B | Non-Slip Epoxy Paint on Screed |  | Concrete Slab | Screed |  | Epoxy Paint |  | Epoxy Paint (용제형, 0.1mm 이하) : epoxy resin + polyamine hardener(경화제)
| F06C | Non-Slip Epoxy Paint on Fair Faced Concrete | Gray APCS-12 | Concrete Slab |  |  | Epoxy Paint |  | Epoxy Paint (용제형, 0.1mm 이하) : epoxy resin + polyamine hardener(경화제)
| F07A | Epoxy Based Sealer |  | Concrete Slab | Steel Trowel Finish |  | Epoxy Based Sealer |  | Epoxy Coating (무용제형, 3mm 전후), : epoxy resin + polyamine hardener(경화제)
| F07B | Epoxy Coating on Steel Trowel Finish |  | Concrete Slab | Steel Trowel Finish |  | Epoxy Based Sealer |  | Epoxy Coating (무용제형, 3mm 전후), : epoxy resin + polyamine hardener(경화제)
| F07C | Epoxy Screed and Seal Coat on Steel Trowel Finish |  | Concrete Slab | Steel Trowel Finish |  | Epoxy Based Sealer |  | Epoxy Screed (Mortar 5~20mm), : epoxy resin mortar+ polyamine hardener
| F08 | Heavy Duty Self-Leveling Epoxy on Steel Trowel Finish | 5mm | Concrete Slab | Steel Trowel Finish |  | Epoxy Lining |  | Self-Leveling Epoxy Floors
| F09 | Road Marker Paint |  | Concrete Slab | Steel Trowel Finish |  | Road Marker Paint
| F10 | White Strips for Parking Place |  | Concrete Slab | Steel Trowel Finish |  | White Strips for Parking Place
| F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish |  | Concrete Slab | Steel Trowel Finish |  | Chemical Resistant Paint
Tile | F31A | Non-Slip Unglazed Ceramic Tile on Screed |  | Concrete Slab | Screed |  | Ceramic Tile
| F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing |  | Concrete Slab | Screed | Liquid Waterproofing | Ceramic Tile
| F31C | Non-Slip Unglazed Ceramic Tile on Screed + Waterproof Membrane |  | Concrete Slab | Screed | Waterproof Membrane | Ceramic Tile
| F32 | Acid Resistant Ceramic Tile on Screed |  | Concrete Slab | Screed |  | Acid/Alkaline Resistant Tile
| F33 | Terrazzo Tile on Cement Screed |  | Concrete Slab | Screed |  | Terrazzo Tile
| F34A | Vinyl Tile on Screed |  | Concrete Slab | Screed |  | Vinyl Tile
| F34B | Vinyl Tile on Steel Trowel Finish |  | Concrete Slab | Steel Trowel Finish |  | Vinyl Tile
| F35 | Anti-Static Vinyl Tile on Steel Trowel Finish |  | Concrete Slab |  |  | Anti-Static Vinyl Tile
| F36 | Granite Tile |  | Concrete Slab |  |  | Granite Tile
| F37A | Marble Tile on Screed |  | Concrete Slab | Screed |  | Marble Tile
| F37B | Natural Stone / Marble on Screed |  | Concrete Slab | Screed |  | Marble Tile
| F38 | Stone Tile |  | Concrete Slab |  |  | Stone Tile
| F39 | Concrete Tile |  | Concrete Slab |  |  | Concrete Tile
| F40 | Mosaic Tile |  | Concrete Slab |  |  | Mosaic Tile
| F41 | Porcelain Tile on Steel Trowel Finish |  | Concrete Slab |  |  | Porcelain Tile
| F42 | Rubber Tile on Screed |  | Concrete Slab | Screed |  | Rubber Tile
Hardener | F51 | Steel Trowel Finish |  | Concrete Slab | Steel Trowel Finish
| F52 | Brushed(Broom) Finish |  | Concrete Slab | Steel Trowel Finish |  | Brushed(Broom) Finish
| F53A | Hardener Finish(Powder Type) |  | Concrete Slab | Steel Trowel Finish |  | Hardener Finish(Powder Type)
| F53B | Hardener Finish(Powder Type) |  | Concrete Slab | Steel Trowel Finish |  | Hardener Finish(Powder Type) | Epoxy Paint
| F54A | Hardener Finish(Liquid Type) on Steel Trowel Finish |  | Concrete Slab | Steel Trowel Finish |  | Hardener Finish(Liquid Type)
| F54B | Non-Slip Epoxy Paint with Epoxy Hardener on Steel Trowel Finish |  | Concrete Slab | Steel Trowel Finish |  | Hardener Finish(Liquid Type) | Epoxy Paint
Mat | F71 | Carpet |  | Concrete Slab |  |  | Carpet
| F72 | Carpet Tile on Screed |  | Concrete Slab | Screed |  | Carpet Tile
| F73 | Matwell |  | Concrete Slab |  |  | Recess Floor Mat
| F74 | Entrance Floor Mats and Frame |  | Concrete Slab |  |  | Entrance Floor Mats and Frame
Raised Floor | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | 600x600, H=1000 | Concrete Slab | Steel Trowel Finish | Anti-Dust Paint | Raised Floor_Anti-Static Vinyl Tile
| F92 | Raised Floor |  | Concrete Slab | Steel Trowel Finish | Anti-Dust Paint | Raised Floor_Carpet Tile
| F93 | Raised Floor |  | Concrete Slab | Steel Trowel Finish | Anti-Dust Paint | Raised Floor_Marble
| N.A | N.A
기준 | Screed 적용 기준 |  |  | 구배가 필요한 바닥마감에만 적용
| Hardener위 Epoxy 기준 |  |  | Hardener위 Epoxy 작업 어려움
| Epoxy Paint / Epoxy Based Sealer / Epoxy Lining 기준 |  |  | 두께 : Epoxy Paint < Epoxy Coating < Self-Leveling Epoxy
| Tile on Screed 적용 기준 |  |  | Screed : 구배용 WM 별도 구분, Tile 자체 Work Master에 Mortar Bond Coat or Adhesive 포함
Skirting | Finish Style Number | Finish Style Name |  | Base Material | Finish 1 (Work Master) | Finish 2 (Work Master) | Finish 3 (Work Master) | Finish 4 (Work Master) | Remark
Painting | B01 | Acrylic Emulsion Paint |  | Concrete Wall / Masonry Wall / Dry Wall |  |  | Acrylic Emulsion Paint
| B02 | Acid Resistant Paint |  | Concrete Wall / Masonry Wall / Dry Wall |  |  | Acid/Alkaline Resistant Paint
| B03 | Epoxy Paint |  | Concrete Wall / Masonry Wall / Dry Wall |  |  | Epoxy Paint |  | SACE
| B04 | Chemical Resistant Epoxy Paint |  | Concrete Wall / Masonry Wall / Dry Wall |  |  | Chemical Resistant Paint
Tile | B31 | Unglazed Ceramic Tile |  | Concrete Wall / Masonry Wall |  |  | Unglazed Ceramic Tile
| B32 | Coved Ceramic Tile |  | Concrete Wall / Masonry Wall |  |  | Glazed Ceramic Tile
| B33 | Acid Resistant Ceramic Tile |  | Concrete Wall / Masonry Wall |  |  | Acid/Alkaline Resistant Tile
| B34 | Terrazzo Tile |  | Concrete Wall / Masonry Wall |  |  | Terrazzo Tile
| B35A | Coved Vinyl Tile |  | Concrete Wall / Masonry Wall |  |  | Vinyl Tile |  | Vinyl Tile = PVC Tile (polyvinyl chloride)
| B35B | PVC Coving (용어 통일) |  | Concrete Wall / Masonry Wall |  |  | Vinyl Tile |  | Vinyl Tile = PVC Tile (polyvinyl chloride)
| B35C | PVC Tile (용어 통일) |  | Concrete Wall / Masonry Wall |  |  | Vinyl Tile |  | Vinyl Tile = PVC Tile (polyvinyl chloride)
| B36 | Anti-Static Vinyl Tile |  | Concrete Wall / Masonry Wall |  |  | Anti-Static Vinyl Tile
| B37 | Granite Tile |  | Concrete Wall / Masonry Wall |  |  | Granite Tile
| B38 | Marble Tile |  | Concrete Wall / Masonry Wall |  |  | Marble Tile
| B39 | Stone Tile |  | Concrete Wall / Masonry Wall |  |  | Stone Tile
| B40 | Concrete Tile |  | Concrete Wall / Masonry Wall |  |  | Concrete Tile
| B41 | Porcelain Tile |  | Concrete Wall / Masonry Wall |  |  | Porcelain Tile
| B42 | Coved Rubber Skirting |  | Concrete Wall / Masonry Wall |  |  | Coved Rubber Skirting
| B43 | Painted Timber Skirting |  |  |  |  | No- WM
| N.A | N.A
기준 | Skirting의 Base Material 표현 |  |  | Skirting의 Base Material은 Wall과 동일하므로 Skirting Style Name에서 생략
Wall | Finish Style Number | Finish Style Name |  | Base Material | Finish 1 (Work Master) | Finish 2 (Work Master) | Finish 3 (Work Master) | Finish 4 (Work Master) | Remark
Painting | W01A | Acrylic Emulsion Paint on Fair Faced Concrete |  | Concrete Wall |  |  | Acrylic Emulsion Paint
| W01B | Acrylic Emulsion Paint on Cement Plaster | T13 Plaster | Masonry Wall | Plastering |  | Acrylic Emulsion Paint
| W01C | Acrylic Emulsion Paint on Gypsum Board |  | Gypsum Board Wall |  |  | Acrylic Emulsion Paint
| W02 | Water Emulsion Paint |  | Concrete Wall |  |  | Water Emulsion Paint
Masonry Wall
Gypsum Board Wall
| W03A | Latex Paint on Fair Faced Concrete |  | Concrete Wall | Fair Faced Concrete |  | Latex Paint
| W03B | Latex Paint on Cement Plaster |  | Masonry Wall | Plastering |  | Latex Paint
Gypsum Board Wall
| W04A | Acid Resistant Paint on Fair Faced Concrete |  | Concrete Wall | Fair Faced Concrete |  | Acid/Alkaline Resistant Paint
| W04B | Acid Resistant Paint on Cement Plaster | T13 Plaster | Masonry Wall | Plastering |  | Acid/Alkaline Resistant Paint
Gypsum Board Wall
| W05A | Epoxy Paint on Fair Faced Concrete |  | Concrete Wall | Fair Faced Concrete |  | Epoxy Paint
| W05B | Epoxy Paint on Cement Plaster |  | Masonry Wall | Plastering |  | Epoxy Paint
Gypsum Board Wall
| W06 | Stucco Finish |  | Concrete Wall / Masonry Wall / Dry Wall |  |  | Stucco Finish
| W07 | Anti-Dust Paint |  | Concrete Wall / Masonry Wall / Dry Wall |  |  | Anti-Dust Paint
| W08 | Epoxy Based Sealer |  | Concrete Wall / Masonry Wall / Dry Wall |  |  | Epoxy Based Sealer
| W09A | Chemical Resistant Paint on Fair Faced Concrete | T13 Plaster | Concrete Wall | Fair Faced Concrete |  | Chemical Resistant Paint
| W09B | Chemical Resistant Paint on Cement Plaster |  | Masonry Wall | Plastering |  | Chemical Resistant Paint
Gypsum Board Wall
| W11 | 2 Coats of Non-Conductive & Fire Retardant White Color Paint on Thk.13 Cement Plaster |  |  |  |  | No- Work Master
Tile | W31 | Unglazed Ceramic Tile |  | Concrete Wall / Masonry Wall |  |  | Unglazed Ceramic Tile
| W32A | Glazed Ceramic Tile(≤C.H+100) / No Paint (>C.H+100) on Cement Plaster | Below Suspended Ceiling | Concrete Wall / Masonry Wall | Plastering (Tile Work에 포함) | No Waterproofing | Glazed Ceramic Tile
| W32B | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) on Cement Plaster | H=1200 | Concrete Wall / Masonry Wall | Plastering (Tile Work에 포함) | No Waterproofing | Glazed Ceramic Tile
| W32C | Glazed Ceramic Tile on Cement Plaster | No Ceiling Full Height | Concrete Wall / Masonry Wall | Plastering (Tile Work에 포함) | No Waterproofing | Glazed Ceramic Tile
| W32D | Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100) on Cement Plaster | Below Suspended Ceiling | Concrete Wall / Masonry Wall | Plastering (Tile Work에 포함) | Liquid Waterproofing | Glazed Ceramic Tile
| W32E | Glazed Ceramic Tile + Liquid Waterproofing (≤1200) / Acrylic Emulsion Paint (>1200) on Cement Plaster | H=1200 | Concrete Wall / Masonry Wall | Plastering (Tile Work에 포함) | Liquid Waterproofing | Glazed Ceramic Tile
| W32F | Glazed Ceramic Tile on Cement Plaster + Liquid Waterproofing | No Ceiling Full Height | Concrete Wall / Masonry Wall | Plastering (Tile Work에 포함) | Liquid Waterproofing | Glazed Ceramic Tile
| W32G | Glazed Ceramic Tile(≤C.H+100) + Waterproof Membrane / No Paint (>C.H+100) on Cement Plaster | Below Suspended Ceiling | Concrete Wall / Masonry Wall | Plastering (Tile Work에 포함) | Waterproof Membrane | Glazed Ceramic Tile
| W32H | Glazed Ceramic Tile + Waterproof Membrane (≤1200) / Acrylic Emulsion Paint (>1200) on Cement Plaster | H=1200 | Concrete Wall / Masonry Wall | Plastering (Tile Work에 포함) | Waterproof Membrane | Glazed Ceramic Tile
| W32I | Glazed Ceramic Tile on Cement Plaster + Waterproof Membrane | No Ceiling Full Height | Concrete Wall / Masonry Wall | Plastering (Tile Work에 포함) | Waterproof Membrane | Glazed Ceramic Tile
| W33A | ACID Resistant Ceramic Tile (≤CH+100) / Acrylic Emulsion Paint (>CH+100) on Cement Plaster | H=1200 | Concrete Wall / Masonry Wall | Plastering (Tile Work에 포함) |  | Acid/Alkaline Resistant Tile
| W33B | ACID Resistant Ceramic Tile on Cement Plaster | No Ceiling Full Height | Concrete Wall / Masonry Wall | Plastering (Tile Work에 포함) |  | Acid/Alkaline Resistant Tile
| W34 | Granite Tile |  | Concrete Wall / Masonry Wall |  |  | Granite Tile
| W35 | Marble Tile |  | Concrete Wall / Masonry Wall |  |  | Marble Tile
| W36 | Stone Tile |  | Concrete Wall / Masonry Wall |  |  | Stone Tile
| W37 | Mosaic Tile |  | Concrete Wall / Masonry Wall |  |  | Mosaic Tile
| W38 | Acoustic Tile |  | Concrete Wall / Masonry Wall |  |  | Acoustic Tile
| W39 | Porcelain Tile |  | Concrete Wall / Masonry Wall |  |  | Porcelain Tile
| N.A | N.A
기준 | Tile Plastering 적용 기준? |  |  | Style Name에 Plaster가 명기 되지만, Tile 자체 Work Master에 Mortar Bond Coat or Adhesive 포함 되어 있으므로 Plastering WM 미적용
Acrylic Emulsion / Water Emulsion / Latex Paint 기준
Ceiling | Finish Style Number | Finish Style Name |  | Base Material | Finish 1 (Work Master) | Finish 2 (Work Master) | Finish 3 (Work Master) | Finish 4 (Work Master) | Remark
Painting | C01 | Acrylic Emulsion Paint on Fair Faced Concrete |  | Concrete Slab |  |  | Acrylic Emulsion Paint |  | SACE
| C02 | Water Emulsion Paint on Fair Faced Concrete |  | Concrete Slab |  |  | Water Emulsion Paint
| C03 | Latex Paint on Fair Faced Concrete |  | Concrete Slab |  |  | Latex Paint
| C04 | Acid Resistant Paint on Fair Faced Concrete |  | Concrete Slab |  |  | Acid/Alkaline Resistant Paint
| C05 | Anti-Dust Paint |  | Concrete Slab |  |  | Anti-Dust Paint
| C06 | Epoxy Paint on Fair Faced Concrete |  | Concrete Slab |  |  | Epoxy Paint
System Ceiling | C91 | Fiber Board Ceiling System |  | Concrete Slab |  |  | Fiber Board Ceiling System
| C92 | Gypsum Plaster Board Ceiling System |  | Concrete Slab |  |  | Gypsum Plaster Board Ceiling System
| C93 | Moisture Resistant Gypsum Plaster Board Ceiling System |  | Concrete Slab |  |  | Moisture Resistant Gypsum Plaster Board Ceiling System
| C94 | Cement Board Ceiling System |  | Concrete Slab |  |  | Cement Board Ceiling System
| C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | 600x600 T Bar | Concrete Slab |  |  | Acoustic Tiled Ceiling System (T-Bar)
| C95B | Suspended Acoustic Tiled Ceiling (M-Bar) |  |  |  |  | Acoustic Tiled Ceiling System (M-Bar)
| C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | 600x600 T bar | Concrete Slab |  |  | Moisture Resistant Tiled Ceiling System (T-Bar)
| C96B | Suspended Moisture Resistant Tiled Ceiling (M-Bar) |  |  |  |  | Moisture Resistant Tiled Ceiling System (M-Bar)
| C97 | Aluminum Spandrel Ceiling System |  | Concrete Slab |  |  | Aluminum Spandrel Ceiling System
| C98 | Metal Open Cell Ceiling |  | Concrete Slab |  |  | Metal Open Cell Ceiling
| N.A | N.A
기준
Exterior Finish - 미확정
Roof | Finish Style Number | Finish Style Name (Key Name) | Ref. Size, Thickness | Base Material | Finish 1 (Work Master) | Finish 2 (Work Master) | Finish 3 (Work Master) | Finish 4 (Work Master) | Remark
Concrete Roof | ER01 | Acrylic Emulsion Paint |  | Concrete Slab | Steel Trowel Finish |  | Acrylic Emulsion Paint
| ER02 | Water Emulsion Paint |  | Concrete Slab | Steel Trowel Finish |  | Water Emulsion Paint
| ER03 | Acid/Alkaline Resistant Paint |  | Concrete Slab | Steel Trowel Finish |  | Acid/Alkaline Resistant Paint
Steel Roof | ER31 | Non-Slip Unglazed Ceramic Tile on Screed |  | Concrete Slab | Screed |  | Ceramic Tile
| ER32 | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing |  | Concrete Slab | Screed | Liquid Waterproofing | Ceramic Tile
기준
Exterior Wall | Finish Style Number | Finish Style Name (Key Name) | Ref. Size, Thickness | Base Material | Finish 1 (Work Master) | Finish 2 (Work Master) | Finish 3 (Work Master) | Finish 4 (Work Master) | Remark
Painting | EW01 | Acrylic Emulsion Paint |  | Concrete Slab | Steel Trowel Finish |  | Acrylic Emulsion Paint |  | SACE-CCB
| EW02 | Water Emulsion Paint |  | Concrete Slab | Steel Trowel Finish |  | Acrylic Emulsion Paint (Textured Type)
| EW03 | Acid/Alkaline Resistant Paint |  | Concrete Slab | Steel Trowel Finish |  | Water Emulsion Paint
Latex Paint
Latex Paint (Textured Type)
Epoxy Paint
Stucco Finish
Chemical Resistant Paint
Cladding | EW31 | Non-Slip Unglazed Ceramic Tile on Screed |  | Concrete Slab | Screed |  | Ceramic Tile
| EW32 | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing |  | Concrete Slab | Screed | Liquid Waterproofing | Ceramic Tile
기준

## 팀 표준 마감기준-Int
팀 기준 사양 | [11 empty] | 프로젝트 적용 현황
* 동일 Finish Material 의 두께, Size, 높이가 다른 경우 => 별도 구분 않함.
Building | Room | Description | Floor |  | Base |  | Wall |  | Ceiling |  | Remark | Project | Building | Room | Description | Floor | Base | Wall | Ceiling | Remark
|  |  |  | 기준:Concrete Slab |  | 기준:Masonry Wall |  | 기준:Masonry Wall |  | 기준:Concrete Slab
| Office |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Shift Superintendent |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | OPS Shift Co-Ordinator |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | OPS Shift Co-Ordinator |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Library |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Visitor Office |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Visitor Office |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Day Shift Co-Ordinator |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Day Shift Co-Ordinator |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Relief Foreman |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Relief Foreman |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Warehouse (ST) | Office |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B31 | Unglazed Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | ALOM | ALOM | Warehouse (ST) | Office |  | Unglazed Ceramic Tile on Cement Screed | Unglazed Ceramic Tile on THK.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete or THK.15 Cement Plaster | Suspended Acoustic Ceiling
Workshop(ST) | Office |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | Vung Ang | Vung Ang | Workshop(ST) | Office |  | Ceramic Tile | Ceramic Skirting | Emulsion Paint | Suspended Acoustic Mineral Panel
Trainign Center & First Aid Room | Manager Room, Office, Corridor, First Aid Room, Meeting Room |  | F33 | Terrazzo Tile on Cement Screed | B34 | Terrazzo Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | ZAWA | ZAWA | Trainign Center & First Aid Room | Manager Room, Office, Corridor, First Aid Room, Meeting Room |  | Terrazzo Tile on Cement Screed | Terrazzo Tile on thk15 Cement Screed | Emulsion Paint on Thk.15 Cement Mortar | Suspended Mineral Fiber Board Panel
Control Building(RC) | Office |  | F34B | Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Control Building(RC) | Office |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Warehouse & Workshop (RC) | Manager Office |  | F34B | Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Warehouse & Workshop (RC) | Manager Office |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Warehouse & Workshop (RC) | Office |  | F34B | Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Warehouse & Workshop (RC) | Office |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Admin & Control Building(RC) | General Office |  | F34B | Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | RAPO | RAPO | Admin & Control Building(RC) | General Office |  | PVC Tile | Thk2 PVC Skirting on Cement Mortar (H=100) | Emulsion Paint on Thk.15 Cement Mortar | Suspended Mineral Board (CH=3150)
Admin Building | General Office |  | F34B | Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Admin Building | General Office |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Water Treatment Building | Office, Corridor |  | F41 | Porcelain Tile on Steel Trowel Finish | B41 | Porcelain Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | ZAWA | ZAWA | Water Treatment Building | Office, Corridor |  | Gres Pine Porcelain on Steel Trowel Finish | Gres Pine Porcelain on thk15 Cement Plaster | Emulsion Paint on Thk.15 Cement Mortar | Suspended Mineral Fiber Board Panel
Warehouse (ST) | Manager Office |  | F41 | Porcelain Tile on Steel Trowel Finish | B41 | Porcelain Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | ALOM | ALOM | Warehouse (ST) | Manager Office |  | Porcelain Stoneware Tile | Porcelain Stoneware Tile | Emulsion Paint | Suspended Acoustic Ceiling
Warehouse (ST) | Office |  | F41 | Porcelain Tile on Steel Trowel Finish | B41 | Porcelain Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | ALOM | ALOM | Warehouse (ST) | Office |  | Porcelain Stoneware Tile | Porcelain Stoneware Tile | Emulsion Paint | Suspended Acoustic Ceiling
Admin Building | Manager Office |  | F72 | Carpet Tile on Screed | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Admin Building | Manager Office |  | Carpet Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
CCB, Workshop Building | Office, Inspection Room, Reception Room |  | F72 | Carpet Tile on Screed | B34 | Terrazzo Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KUSU | KUSU | CCB, Workshop Building | Office, Inspection Room, Reception Room |  | Carpet Tile on thk30 Terrazzo Tile | Terrazzo Tile | Acrylic Latex Paint on thk15 Cement Plaster | Suspended Al. Strip Panel w/ thk25 Acoustic Blanket
| Meeting Room |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
Control Building(RC) | Meeting Room |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Meeting Room |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Meeting Room |  | F34B | Vinyl Tile on Steel Trowel Finish | B42 | Coved Rubber Skirting | W03B | Latex Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | TVEP | TVEP | Control Building(RC) | Meeting Room |  | PVC Tile w/ Adhesive on Steel Troweled Concrete Slab | Rubber Base (H=100) | Latex Paint on Thk15 Cement Plaster | Suspended Mineral Fiberboard Panel(600x600)
| Break Room |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
Control Building(RC) | Break Room |  | F34A | Vinyl Tile on Screed | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Break Room |  | Vinyl Tile on Screed | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Moisture Resistant Tiled Ceiling (600x600)
| Prayer Room |  | F72 | Carpet Tile on Screed | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
Control Building(RC) | Prayer Room |  | F72 | Carpet Tile on Screed | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Prayer Room |  | Carpet Tile on Screed | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Prayer Room |  | F72 | Carpet Tile on Screed | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Control Building(RC) | Prayer Room |  | Carpet Tile on Screed | Coved Vinyl (H=100) | Acrylic Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
| Corridor |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
Control Building(RC) | Corridor |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Corridor |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Corridor |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Control Building(RC) | Corridor |  | Ceramic Mosaic Tile on Screed | Ceramic Tile (H=600) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Warehouse (ST) | Corridor |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B31 | Unglazed Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | ALOM | ALOM | Warehouse (ST) | Corridor |  | Unglazed Ceramic Tile on Cement Screed | Unglazed Ceramic Tile on THK.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete or THK.15 Cement Plaster | Suspended Acoustic Ceiling
Substation(RC) | Corridor |  | F42 | Rubber Tile on Screed | B42 | Coved Rubber Skirting | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | BONE | BONE | Substation(RC) | Corridor-B |  | THK.3mm Rubber Tile on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
| Stair Case |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Stair Case |  | F42 | Rubber Tile on Screed | B42 | Coved Rubber Skirting | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | BONE | BONE | Substation(RC) | Stair Case |  | THK.3mm Rubber Tile on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
Fire Station | Stair Case |  | F34B | Vinyl Tile on Steel Trowel Finish | N.A | N.A | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Fire Station | Stair Case |  | Vinyl Composition Tile on Screed | - | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
| Air Lock Room |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | *연계된 Room마감과 연속 적용
Substation(RC) | Air Lock |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Substation(RC) | Air Lock |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Control Building(RC) | Air Lock |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Air Lock |  | Non-Slip Unglazed Ceramic Tile on Screed + Matwell | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Air Lock |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Control Building(RC) | Air Lock |  | Ceramic Mosaic Tile on Screed + Matwell | Ceramic Tile (H=600) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Substation(RC) | Air Lock Lobby |  | F42 | Rubber Tile on Screed | B42 | Coved Rubber Skirting | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | BONE | BONE | Substation(RC) | Air Lock Lobby |  | THK.3mm Rubber Tile on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Air Lock |  | F42 | Rubber Tile on Screed | B42 | Coved Rubber Skirting | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | BONE | BONE | Substation(RC) | Air Lock |  | THK. 6mm Rubber Tile (Anti Static Surface, Chemical and Slip Resistant) on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
| Lobby |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
Control Building(RC) | Reception/Waiting Area |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Reception/Waiting Area |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Lobby |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Lobby |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Admin & Control Building | Reception (Lobby) |  | F37A | Marble Tile on Screed | B38 | Marble Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | RAPO | RAPO | Admin & Control Building | Reception (Lobby) |  | Thk20 Marble Floor Tile | Marble Tile (H=100) | Emulsion Paint on Thk.15 Cement Mortar | Suspended Mineral Board (CH=3150)
Admin Building | Reception (Air Lock) |  | F37A | Marble Tile on Screed | B38 | Marble Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Admin Building | Reception (Air Lock) |  | Marble Tile on Screed | Marble Tile (H=200) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
| Locker Room |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W32A | Glazed Ceramic Tile(≤C.H+100) / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | *바닥+벽 방수 미적용
Control Building(RC) | Locker Room |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W32A | Glazed Ceramic Tile(≤C.H+100) / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Locker Room |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile | Glazed Ceramic Tile(≤2100) / Acrylic Emulsion paint (>2100) on Cement Plaster | Suspended Moisture Resistant Tiled Ceiling (600x600)
Warehouse (ST) | Changing Room |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B31 | Unglazed Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | ALOM | ALOM | Warehouse (ST) | Changing Room |  | Unglazed Ceramic Tile on Cement Screed | Unglazed Ceramic Tile on THK.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete or THK.15 Cement Plaster | Suspended Moisture Resistant Acoustic Ceiling
Workshop(ST) | Changing Room |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | N.A | N.A | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | Vung Ang | Vung Ang | Workshop(ST) | Changing Room |  | Ceramic Tile on Cement Screed | - | Emulsion Paint on Fair Faced Concrete or THK.15 Cement Plaster | Suspended Acoustic Mineral Panel
Warehouse & Workshop (RC) | Locker Room |  | F34B | Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Warehouse & Workshop (RC) | Locker Room |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
| Shower Room |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | N.A | N.A | W32D | Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | *바닥+벽 방수 적용
Warehouse (ST) | Shower Room |  | F31C | Non-Slip Unglazed Ceramic Tile on Screed + Waterproof Membrane | N.A | N.A | W32I | Glazed Ceramic Tile on Cement Plaster + Waterproof Membrane | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | ALOM | ALOM | Warehouse (ST) | Shower Room |  | Unglazed Ceramic Tile on Cement Screed on Waterproof Membrane | - | Glazed Ceramic Tile on Cement Plaster on Waterproof Membrane | Suspended Moisture Resistant Acoustic Ceiling
Workshop(ST) | Shower Room |  | F31C | Non-Slip Unglazed Ceramic Tile on Screed + Waterproof Membrane | N.A | N.A | W01B | Acrylic Emulsion Paint on Cement Plaster | C97 | Aluminum Spandrel Ceiling System | Vung Ang | Vung Ang | Workshop(ST) | Shower Room |  | Unglazed Ceramic Tile on Cement Screed on Waterproof Membrane | - | Emulsion Paint on Fair Faced Concrete or THK.15 Cement Plaster | Suspended AL. Panel
Warehouse & Workshop (RC) | Shower Room |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | N.A | N.A | W32D | Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | KLNG | KLNG | Warehouse & Workshop (RC) | Shower Room |  | Non-Slip Ceramic Tile on Screed + Liquid Waterproofing | - | Ceramic Tile + Liquid Waterproofing (H=1800) on Cement plaster | Suspended Acoustic Tile Ceiling (600x600, Sag and Humidity Resistant)
| Ablution |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W32D | Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | *바닥+벽 방수 적용
Control Building(RC) | Hamman/Ablutions |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W32A | Glazed Ceramic Tile(≤C.H+100) / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Hamman/Ablutions |  | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | Coved Ceramic Tile | Glazed Ceramic Tile(≤2100) / Acrylic Emulsion paint (>2100) on Cement Plaster | Suspended Moisture Resistant Tiled Ceiling (600x600)
Control Building(RC) | Ablution Room |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | N.A | N.A | W32D | Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | KLNG | KLNG | Control Building(RC) | Ablution Room |  | Non-Slip Ceramic Tile on Screed + Liquid Waterproofing | - | Ceramic Tile + Liquid Waterproofing (H=1200) on Cement plaster | Suspended Acoustic Tile Ceiling (600x600, Sag and Humidity Resistant)
| Toilet |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W32A | Glazed Ceramic Tile(≤C.H+100) / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | *바닥만 방수 적용
Control Building(RC) | Ladies/Disabled Toilet |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W32A | Glazed Ceramic Tile(≤C.H+100) / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Ladies/Disabled Toilet |  | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | Coved Ceramic Tile | Glazed Ceramic Tile(≤2100) / Acrylic Emulsion paint (>2100) on Cement Plaster | Suspended Moisture Resistant Tiled Ceiling (600x600)
Control Building(RC) | Shift Superintendent Toilet |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W32A | Glazed Ceramic Tile(≤C.H+100) / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Shift Superintendent Toilet |  | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | Coved Ceramic Tile | Glazed Ceramic Tile(≤2100) / Acrylic Emulsion paint (>2100) on Cement Plaster | Suspended Moisture Resistant Tiled Ceiling (600x600)
Control Building(RC) | Toilet (M & F) |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | N.A | N.A | W32D | Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | KLNG | KLNG | Control Building(RC) | Toilet (M & F) |  | Non-Slip Ceramic Tile on Screed + Liquid Waterproofing | - | Ceramic Tile + Liquid Waterproofing (H=1200) on Cement plaster | Suspended Acoustic Tile Ceiling (600x600, Sag and Humidity Resistant)
Warehouse & Workshop (RC) | Toilet (M & F) |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | N.A | N.A | W32D | Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | KLNG | KLNG | Warehouse & Workshop (RC) | Toilet (M & F) |  | Non-Slip Ceramic Tile on Screed + Liquid Waterproofing | - | Ceramic Tile + Liquid Waterproofing (H=1200) on Cement plaster | Suspended Acoustic Tile Ceiling (600x600, Sag and Humidity Resistant)
Warehouse (ST) | Toilet |  | F31C | Non-Slip Unglazed Ceramic Tile on Screed + Waterproof Membrane | N.A | N.A | W32I | Glazed Ceramic Tile on Cement Plaster + Waterproof Membrane | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | ALOM | ALOM | Warehouse (ST) | Toilet (M & F) |  | Unglazed Ceramic Tile on Cement Screed on Waterproof Membrane | - | Glazed Ceramic Tile on THK.15 Cement Plaster on Waterproof Membrane | Suspended Moisture Resistant Acoustic Ceiling
Workshop(ST) | Toilet (M & F) |  | F31C | Non-Slip Unglazed Ceramic Tile on Screed + Waterproof Membrane | N.A | N.A | W01B | Acrylic Emulsion Paint on Cement Plaster | C97 | Aluminum Spandrel Ceiling System | Vung Ang | Vung Ang | Workshop(ST) | Toilet (M & F) |  | Unglazed Ceramic Tile on Cement Screed on Waterproof Membrane | - | Emulsion Paint | Suspended AL. Panel
| Janitor |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W32A | Glazed Ceramic Tile(≤C.H+100) / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | *바닥만 방수 적용
Control Building(RC) | Janitor |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W32A | Glazed Ceramic Tile(≤C.H+100) / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Janitor |  | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | Coved Ceramic Tile | Glazed Ceramic Tile(≤2100) / Acrylic Emulsion paint (>2100) on Cement Plaster | Suspended Moisture Resistant Tiled Ceiling (600x600)
Control Building(RC) | Janitor |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | N.A | N.A | W32D | Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | KLNG | KLNG | Control Building(RC) | Janitor |  | Non-Slip Ceramic Tile on Screed + Liquid Waterproofing | - | Ceramic Tile + Liquid Waterproofing (H=1200) on Cement plaster | Suspended Acoustic Tile Ceiling (600x600, Sag and Humidity Resistant)
| First Aid Room |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W32A | Glazed Ceramic Tile(≤C.H+100) / No Paint (>C.H+100) on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | *바닥+벽 방수 미적용
Main Building(ST) | First Aid Room |  | F34B | Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | UTCC | UTCC | Main Building(ST) | First Aid Room |  | 1. THK 3 Heavy Duty PVC Tile 2. Steel Trowel Finish | PVC Skirting | Emulsion Paint on Gypsum Board 12.5mm 2 Piles | Suspended Acoustic Mineral Board
Admin Building | Emergency Treatment |  | F34B | Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Admin Building | Emergency Treatment |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
| Dining Room | *별도의 식당동 | F34B | Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
Canteen(RC) | Dining Room |  | F34B | Vinyl Tile on Steel Trowel Finish | B42 | Coved Rubber Skirting | W03B | Latex Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | TVEP | TVEP | Canteen(RC) | Dining Room |  | PVC Tile on Steel Trowel Finish | Rubber Base (H=100) | Latex Paint on Thk15 Cement Plaster | Suspended Mineral Fiberboard Panel(600x600)
| Cooking Room |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W32D | Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | *바닥+벽 방수 적용
Canteen(RC) | Cold Food Area (Cooking Area) |  | F31C | Non-Slip Unglazed Ceramic Tile on Screed + Waterproof Membrane | B32 | Coved Ceramic Tile | W32H | Glazed Ceramic Tile + Waterproof Membrane (≤1200) / Acrylic Emulsion Paint (>1200) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | TVEP | TVEP | Canteen(RC) | Cold Food Area |  | Unglazed Ceramic Tile on Cement Screed w/ Water Proofing Mambrane |  | Glazed Ceramic Tile on Thk15 Cement Plaster w/ Water Proofing(≤1200) / Latex Paint on Cement Plaster (>1200) | Suspended Moisture Resistant Panel(600x600)
Canteen(RC) | Hot Food Area (Cooking Area) |  | F31C | Non-Slip Unglazed Ceramic Tile on Screed + Waterproof Membrane | B32 | Coved Ceramic Tile | W32H | Glazed Ceramic Tile + Waterproof Membrane (≤1200) / Acrylic Emulsion Paint (>1200) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | TVEP | TVEP | Canteen(RC) | Cold Food Area |  | Unglazed Ceramic Tile on Cement Screed w/ Water Proofing Mambrane |  | Glazed Ceramic Tile on Thk15 Cement Plaster w/ Water Proofing(≤1200) / Latex Paint on Cement Plaster (>1200) | Suspended Moisture Resistant Panel(600x600)
| Dish Washing Area |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W32D | Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | *바닥+벽 방수 적용
Canteen(RC) | Dish Washing Area |  | F31C | Non-Slip Unglazed Ceramic Tile on Screed + Waterproof Membrane | B32 | Coved Ceramic Tile | W32H | Glazed Ceramic Tile + Waterproof Membrane (≤1200) / Acrylic Emulsion Paint (>1200) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | TVEP | TVEP | Canteen(RC) | Dish Washing Area |  | Unglazed Ceramic Tile on Cement Screed w/ Water Proofing Mambrane |  | Glazed Ceramic Tile on Thk15 Cement Plaster w/ Water Proofing(≤1200) / Latex Paint on Cement Plaster (>1200) | Suspended Moisture Resistant Panel(600x600)
| Food Receiving & Preparation Area |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | *바닥만 방수 적용
Canteen(RC) | Food Receiving & Preparation Area |  | F31C | Non-Slip Unglazed Ceramic Tile on Screed + Waterproof Membrane | B31 | Unglazed Ceramic Tile | W03B | Latex Paint on Cement Plaster | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | Canteen(RC) | Receiving & Preparation Area |  | Unglazed Ceramic Tile on Cement Screed w/ Water Proofing Mambrane | Unglazed Ceramic Tile (H=100) | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
| Food Storage |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | *바닥만 방수 적용
Canteen(RC) | Food Storage |  | F31C | Non-Slip Unglazed Ceramic Tile on Screed + Waterproof Membrane | B31 | Unglazed Ceramic Tile | W03B | Latex Paint on Cement Plaster | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | Canteen(RC) | Food Storage |  | Unglazed Ceramic Tile on Cement Screed w/ Water Proofing Mambrane | Unglazed Ceramic Tile (H=100) | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
| Store (Document) | *문서용도 | F34A | Vinyl Tile on Screed | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
Control Building(RC) | Store | 문서 | F34A | Vinyl Tile on Screed | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Store |  | Vinyl Tile on Screed | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Record Room |  | F34A | Vinyl Tile on Screed | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Control Building(RC) | Record Room |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Control Building(RC) | PPE Store | 안전장비 | F34A | Vinyl Tile on Screed | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | PPE Store |  | Vinyl Tile on Screed | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
| Store (Material) | *자재용도 | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | 자재보관실 |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | LECO | LECO | Substation(RC) | 자재보관실 |  | Steel Trowel Finish w/ Epoxy Paint | Epoxy Paint | Emulsion Paint on Gypsum Board | Emulsion Paint on Fair Faced Concrete
Warehouse (ST) | Storage Area |  | F07B | Epoxy Coating on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | ALOM | ALOM | Warehouse (ST) | Storage Area |  | Resin coating | Resin coating | Emulsion Paint (Up to FL.+1.6M) | Exposed Thermal Insulated Metal Cladding
Warehouse (ST) | Hazardous Material Store |  | F07B | Epoxy Coating on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | ALOM | ALOM | Warehouse (ST) | Hazardous Material Store |  | Resin coating | Resin coating | Emulsion Paint | Exposed Thermal Insulated Metal Cladding
Warehouse (ST) | Instrument Spare Part Room |  | F07B | Epoxy Coating on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | ALOM | ALOM | Warehouse (ST) | Instrument Spare Part Room |  | Resin coating | Resin coating | Emulsion Paint | Exposed Thermal Insulated Metal Cladding
Warehouse (ST) | Perishiable Material Room |  | F07B | Epoxy Coating on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | ALOM | ALOM | Warehouse (ST) | Perishiable Material Room |  | Resin coating | Resin coating | Emulsion Paint | Exposed Thermal Insulated Metal Cladding
Warehouse & Workshop (RC) | Warehouse |  | F07B | Epoxy Coating on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Warehouse & Workshop (RC) | Warehouse |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
Workshop(ST) | KHO Store |  | F53A | Hardener Finish(Powder Type) | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | Vung Ang | Vung Ang | Workshop(ST) | KHO Store |  | Hardener Finish | Epoxy Paint | Emulsion Paint | Exposed Thermal Insulated Metal Cladding
| Tool Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A
Workshop(ST) | Tool Room |  | F54A | Hardener Finish(Liquid Type) on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | Vung Ang | Vung Ang | Workshop(ST) | Tool Room |  | Hardener Finish | Epoxy Paint | Emulsion Paint | Exposed Thermal Insulated Metal Cladding
Warehouse & Workshop (RC) | Tool Store |  | F07B | Epoxy Coating on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Warehouse & Workshop (RC) | Tool Store |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
| Mechanical Workshop |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A
Workshop(ST) | Workshop |  | F54A | Hardener Finish(Liquid Type) on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | Vung Ang | Vung Ang | Workshop(ST) | Workshop |  | Hardener Finish | Epoxy Paint | Emulsion Paint | Exposed Thermal Insulated Metal Cladding
Warehouse (ST) | Mechanical Workshop Area |  | F06B | Non-Slip Epoxy Paint on Screed | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | ALOM | ALOM | Warehouse (ST) | Workshop Area |  | Epoxy Paint on Cement Screed | Epoxy Paint on Fairfaced concrete or THK.15 Cement Plaster | Emulsion Paint on THK.15 Cement Plaster (Up to FL.+1.6M) | Exposed Thermal Insulated Metal Cladding
Warehouse & Workshop (RC) | Mechanical Workshop |  | F06B | Non-Slip Epoxy Paint on Screed | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Warehouse & Workshop (RC) | Mechanical Workshop |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
| Instrument Workshop |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A
Warehouse (ST) | Instrument Workshop |  | F06B | Non-Slip Epoxy Paint on Screed | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | ALOM | ALOM | Warehouse (ST) | Instrument Workshop |  | Epoxy Paint on Cement Screed | Epoxy Paint on Fairfaced concrete or THK.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete or THK.15 Cement Plaster | Exposed Metal Deck
Warehouse & Workshop (RC) | Instrument Workshop |  | F06B | Non-Slip Epoxy Paint on Screed | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Warehouse & Workshop (RC) | Instrument Workshop |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
| Control Room | *계장 | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
Control Building(RC) | Main Control Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Main Control Room |  | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000) | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Control Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Control Building(RC) | Control Room |  | Epoxy Coating on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1030) | Coved Vinyl (H=100) | Above Raised Floor : Emulsion Paint on Thk.15 Cement Plaster Under Raised Floor : Epoxy Paint | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
| Control Room | *환경 | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
WTB(RC) | Control Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W03B | Latex Paint on Cement Plaster | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | WTB(RC) | Control Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
Anti-Static Vinyl Tile 사례 추가
화공 Access FL 사례 추가
| Engineering Room | *CCR연속배치 | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
Control Building(RC) | Engineering Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Engineering Room |  | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000) | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | OTS Training Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | OTS Training Room |  | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000) | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | OTS Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Control Building(RC) | OTS Room |  | Epoxy Coating on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1030) | Coved Vinyl (H=100) | Above Raised Floor : Emulsion Paint on Thk.15 Cement Plaster Under Raised Floor : Epoxy Paint | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
| Telecom Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | *CCR연속배치시 CCR과 동일 마감
Control Building(RC) | Telecoms Room |  | F34A | Vinyl Tile on Screed | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | SACE | SACE | Control Building(RC) | Telecoms Room |  | Vinyl Tile on Screed | Coved Vinyl H=100 | 2 Coats of Non-Conductive & Fire Retardant White Color Paint on Thk.13 Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Telecom Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | BONE | BONE | Substation(RC) | Telecom Room |  | Steel Trowel Finish w/ Dust Proof Coating (Epoxy) + 600x600 Access Floor System w/Noncombustible Laminated Plastic Finish (H=600) | Laminated Plastic Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
Control Building(RC) | Telecoms Equipment Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | SACE | SACE | Control Building(RC) | Telecoms Equipment Room |  | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000) | Coved Vinyl H=100 | 2 Coats of Non-Conductive & Fire Retardant White Color Paint on Thk.13 Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
Control Building(RC) | Communication Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Control Building(RC) | Communication Room |  | Epoxy Coating on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1030) | Coved Vinyl (H=100) | Above Raised Floor : Emulsion Paint on Thk.15 Cement Plaster Under Raised Floor : Epoxy Paint | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
| Rack Room (CCB) |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | *CCR연속배치시 CCR과 동일 마감
Control Building(RC) | Rack Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | Rack Room |  | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000) | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | OTS Rack Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | OTS Rack Room |  | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000) | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Server Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | KLNG | KLNG | Control Building(RC) | Server Room |  | Epoxy Coating on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1030) | Coved Vinyl (H=100) | Above Raised Floor : Emulsion Paint on Thk.15 Cement Plaster Under Raised Floor : Epoxy Paint | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
| Rack Room (Local) |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Rack Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | LECO | LECO | Substation(RC) | Rack Room |  | Epoxy Paint + Raised Floor W/Conductive Tile | PVC Tile | Emulsion Paint on Gypsum Board | Emulsion Paint on Fair Faced Concrete
Substation(RC) | Rack Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Substation(RC) | Rack Room |  | Epoxy Coating on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000, H=1100) | Coved Vinyl (H=100) | Above Raised Floor : Emulsion Paint on Thk.15 Cement Plaster Under Raised Floor : Epoxy Paint | Emulsion Paint on Fair Faced Concrete
Substation(RC) | Rack Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | IKAN | IKAN | Substation(RC) | Rack Room |  | Epoxy Paint + Raised Floor | PVC Tile | Arcylic Emulsion Paint on Fair Faced Concrete | Suspended Acoustic Ceiling
| Relay & Control Panel Room | *Local | F35 | Anti-Static Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Relay & Control Panel Room |  | F42 | Rubber Tile on Screed | B42 | Coved Rubber Skirting | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | BONE | BONE | Substation(RC) | Relay & Control Panel Room |  | THK. 6mm Rubber Tile (Anti Static Surface, Chemical and Slip Resistant) on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
*Access FL사례 조사
| Electrical Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
Control Building(RC) | Electrical Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | SACE | SACE | Control Building(RC) | Electrical Room |  | Non-Slip Epoxy Paint on Screed | Epoxy Paint H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
Workshop(ST) | Electrical Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | Vung Ang | Vung Ang | Workshop(ST) | Electrical Room |  | Epoxy Paint | Epoxy Paint | Emulsion Paint | Suspended Acoustic Mineral Panel
WTB(RC) | Electrical Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W03B | Latex Paint on Cement Plaster | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | WTB(RC) | Equipment Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
Warehouse & Workshop (RC) | Electrical Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Warehouse & Workshop (RC) | Electrical Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
Warehouse (ST) | Electrical Room |  | F06B | Non-Slip Epoxy Paint on Screed | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | ALOM | ALOM | Warehouse (ST) | Electrical Room |  | Epoxy Paint on Cement Screed | Epoxy Paint on Fairfaced concrete or THK.15 Cement Plaster | Emulsion Paint on THK.15 Cement Plaster (Up to FL.+1.6M) | Exposed Metal Deck
Substation(RC) | Electrical Room |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Substation(RC) | Electrical Room |  | Epoxy Coating on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1030) | Coved Vinyl (H=100) | Above Raised Floor : Emulsion Paint on Thk.15 Cement Plaster Under Raised Floor : Epoxy Paint | Emulsion Paint on Fair Faced Concrete
| Switchgear Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Switchgear Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Substation(RC) | Switchgear Room |  | Epoxy Coating on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
Central Control Building(RC) | Switchgear Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W03B | Latex Paint on Cement Plaster | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | Central Control Building(RC) | Switchgear Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Fair Faced Concrete | Latex Paint on Fair Faced Concrete
Substation(RC) | Switchgear Room |  | F42 | Rubber Tile on Screed | B01 | Acrylic Emulsion Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | IKAN | IKAN | Substation(RC) | Switchgear Room |  | Steel Trowel Finish w/ Rubber Flooring Tile (THK. 6mm) | Acrylic Emulsion Paint | Arcylic Emulsion Paint on Cement Plaster (THK. 16mm) | Arcylic Emulsion Paint
Substation(RC) | HV Switchgear Room |  | F42 | Rubber Tile on Screed | B42 | Coved Rubber Skirting | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | BONE | BONE | Substation(RC) | HV Switchgear Room |  | THK. 6mm Rubber Tile (Anti Static Surface, Chemical and Slip Resistant) on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | LV Switchgear Room |  | F42 | Rubber Tile on Screed | B42 | Coved Rubber Skirting | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | BONE | BONE | Substation(RC) | LV Switchgear Room |  | THK. 6mm Rubber Tile (Anti Static Surface, Chemical and Slip Resistant) on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
| MCC Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | MCC Room (type-1) |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | LECO | LECO | Substation(RC) | MCC Room (type-1) |  | Steel Trowel Finish w/ Epoxy Paint | Epoxy Paint | Emulsion Paint on Gypsum Board | Emulsion Paint on Fair Faced Concrete
Substation(RC) | MCC Room (type-2) |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | LECO | LECO | Substation(RC) | MCC Room (type-2) |  | Epoxy Paint + Raised Floor W/Conductive Tile | Epoxy Paint | Emulsion Paint on Gypsum Board | Emulsion Paint on Fair Faced Concrete
| UPS Room |  | F35 | Anti-Static Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | UPS Room |  | F42 | Rubber Tile on Screed | B42 | Coved Rubber Skirting | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | BONE | BONE | Substation(RC) | UPS Room |  | THK. 6mm Rubber Tile (Anti Static Surface, Chemical and Slip Resistant) on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
*Access FL사례 조사
| Battery Room |  | F03 | Acid Resistant Paint on Steel Trowel Finish | B02 | Acid Resistant Paint | W04B | Acid Resistant Paint on Cement Plaster | C04 | Acid Resistant Paint on Fair Faced Concrete | *바닥 Drain 구배 필요시 : 구체 구배
Control Building(RC) | Battery Room |  | F32 | Acid Resistant Ceramic Tile on Screed | B33 | Acid Resistant Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | SACE | SACE | Control Building(RC) | Battery Room |  | Acid Resistant Ceramic Tile on Screed | Acid Resistant Ceramic Tile H=100 | Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Battery Room |  | F32 | Acid Resistant Ceramic Tile on Screed | B33 | Acid Resistant Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | BONE | BONE | Substation(RC) | Battery Room |  | Steel Trowel Finish w/ Acid Resistant Stone Ware Gres Tile + 2coat Water Proofing | Acid Resistant Stone Ware Gres Tile | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Battery Room |  | F03 | Acid Resistant Paint on Steel Trowel Finish | B02 | Acid Resistant Paint | W04B | Acid Resistant Paint on Cement Plaster | C04 | Acid Resistant Paint on Fair Faced Concrete | IKAN | IKAN | Substation(RC) | Battery Room |  | Steel Trowel Finish w/ Acid Resistant Paint | Acid Resistant Paint | Acid Resistant Paint on Cement Plaster (THK. 16mm) | Acid Resistant Paint
Central Control Building(RC) | Battery Room |  | F03 | Acid Resistant Paint on Steel Trowel Finish | B02 | Acid Resistant Paint | W04B | Acid Resistant Paint on Cement Plaster | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | Substation(RC) | Battery Room |  | Acid Resistant Paint on Steel Trowel Concrete Slab | Acid Resistant Paint (H=100) | H=1.5m Acid Resistant Paint on Thk15 Cement Plaster Above 1.5m Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
Substation(RC) | Battery Room |  | F32 | Acid Resistant Ceramic Tile on Screed | B33 | Acid Resistant Ceramic Tile | W33A | ACID Resistant Ceramic Tile (≤CH+100) / Acrylic Emulsion Paint (>CH+100) on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Substation(RC) | Battery Room |  | Acid Resistant Tile on Screed | - | H=2m Acid Resistant Tile on Thk15 Cement Plaster Above 2m Epoxy Paint on Thk15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
| Cable Cellar (Open type) |  | F51 | Steel Trowel Finish | N.A | N.A | N.A | N.A | N.A | N.A | *바닥 Concrete Paving 적용
Substation(RC) | Cable Cellar |  | F51 | Steel Trowel Finish | N.A | N.A | N.A | N.A | N.A | N.A | LECO | LECO | Substation(RC) | Cable Cellar |  | Steel Trowel Finish |  |  | insulation
Substation(RC) | Cable Cellar |  |  | Clean Sand Filling |  |  |  | Cement Plaster (THK. 16mm) |  |  | IKAN | IKAN | Substation(RC) | Cable Cellar |  | Clean Sand Filling |  | Cement Plaster (THK. 16mm)
Substation(RC) | Cable Cellar |  |  | Sand Filling |  |  | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | BONE | BONE | Substation(RC) | Cable Cellar |  | Sand Filling |  | Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Cable Cellar |  |  | Sand Filling |  |  | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Substation(RC) | Cable Cellar |  | Sand Filling | - | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
| Cable Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | *바닥 Drain 구배 필요시 : 구체 구배
GIS Building(RC) | Cable Basement |  | F07C | Epoxy Screed and Seal Coat on Steel Trowel Finish | B03 | Epoxy Paint | W01A | Acrylic Emulsion Paint on Fair Faced Concrete | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | RAPO | RAPO | GIS Building(RC) | Cable Basement |  | 5mm Epoxy Screed and Seal Coat on Concrete Slab | Epoxy Paint (H=100) | Emulsion Paint on Fair Faced Concrete | Emulsion Paint on Fair Faced Concrete
Central Control Building(RC) | Cable Room(Basement) |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W03A | Latex Paint on Fair Faced Concrete | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | Central Control Building(RC) | Cable Room(Basement) |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Fair Faced Concrete | Latex Paint on Fair Faced Concrete
| EDG Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | EDG Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | LECO | LECO | Substation(RC) | EDG Room |  | Steel Trowel Finish w/ Epoxy Paint | Epoxy Paint | Emulsion Paint | Fair Faced Concrete
| Fire Gas Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | 소화약제실 |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | LECO | LECO | Substation(RC) | 소화약제실 |  | Steel Trowel Finish w/ Epoxy Paint | Epoxy Paint | Emulsion Paint on Gypsum Board | Emulsion Paint on Fair Faced Concrete
Substation(RC) | Fire Fighting Room |  | F07B | Epoxy Coating on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | BONE | BONE | Substation(RC) | Fire Fighting Room |  | THK.1 Epoxy Resin on Sceed | THK.1 Epoxy Resin on Sceed | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Clean Agent Cylinder Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Substation(RC) | Clean Agent Cylinder Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
WTB(RC) | Fire Fighting Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | WTB(RC) | Fire Fighting Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
| Fire Water Pump Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
Fire Water Pump BLDG(RC) | Fire Water Pump Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W03B | Latex Paint on Cement Plaster | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | Fire Water Pump BLDG(RC) | Fire Water Pump Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
| GIS Equipment Room |  | F07B | Epoxy Coating on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | *발주처 Hardener 요구 확인
400kV GIS Building(RC) | GIS Room |  | F08 | Heavy Duty Self-Leveling Epoxy on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | RAPO | RAPO | 400kV GIS Building(RC) | GIS Room |  | 5mm Heavy Duty Self Leveling Epoxy | 100mm High Meranti Skirting | Emulsion Paint on Cement Plaster | Emulsion Paint on Fair Faced Concrete | * 5mm Heavy Duty Self-Leveling Epoxy : 계약사양
400kV GIS Building(RC) | GIS Room |  | F07C | Epoxy Screed and Seal Coat on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | Jebel-D | Jebel-D | 400kV GIS Building(RC) | GIS Room |  | 5mm Epoxy Screed and Seal Coat on Steel Trowel Finish | 100mm High Meranti Skirting | Emulsion Paint on Cement Plaster | Emulsion Paint on Fair Faced Concrete
230kV GIS Main Receiving Substation(RC) | 230kV GIS Switchgear Room |  | F54B | Non-Slip Epoxy Paint with Epoxy Hardener on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | SACE | SACE | 230kV GIS Main Receiving Substation(RC) | 230kV GIS Switchgear Room |  | Non-Slip Epoxy Paint with Epoxy Hardener on Steel Trowel Finish | Epoxy Paint H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
| Gas Turbine Hall |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | *발주처 Hardener 요구 확인
Gas Turbine Building(ST) | Gas Turbine Hall |  | F54A | Hardener Finish(Liquid Type) on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | UTCC | UTCC | Gas Turbine Building(ST) | Gas Turbine Hall |  | 1. Hardener Finish 2. Steel Trowel Finish | Epoxy Paint | Emulsion Paint on Thk15 Cement Mortar Plastering (Up to 1200mm) | Exposed Structure
| Steam Turbine Hall |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | *발주처 Hardener 요구 확인
Steam Turbine Building(ST) | Steam Turbine Hall (only Laydown Area) |  | F07C | Epoxy Screed and Seal Coat on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | RAPO | RAPO | Steam Turbine Building(ST) | Steam Turbine Hall (only Laydown Area) |  | 5mm Epoxy Screed and Seal Coat on Concrete Slab | Epoxy Paint (H=100) | Emulsion Paint on Thk15 Cement Mortar (Up to 2500mm) | Exposed Roof | * 5mm Epoxy Screed and Seal Coat : 계약사양
Steam Turbine Building(ST) | Steam Turbine Hall (except Laydown Area) |  | F08 | Heavy Duty Self-Leveling Epoxy on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | RAPO | RAPO | Steam Turbine Building(ST) | Steam Turbine Hall (except Laydown Area) |  | 5mm Heavy Duty Self-Leveling Epoxy | Epoxy Paint (H=100) | Emulsion Paint on Thk15 Cement Mortar (Up to 2500mm) | Exposed Roof | * 5mm Heavy Duty Self-Leveling Epoxy : 계약사양
Steam Turbine Building(ST) | Steam Turbine Hall (Operating Floor) |  | F07C | Epoxy Screed and Seal Coat on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | RAPO | RAPO | Steam Turbine Building(ST) | Steam Turbine Hall (Operating Floor) |  | 5mm Epoxy Screed and Seal Coat on Concrete Slab | Exposed Exterior Wall | Emulsion Paint on Thk15 Cement Mortar (Up to 2500mm) | Exposed Roof | * 5mm Epoxy Screed and Seal Coat : 계약사양
Steam Turbine Building(ST) | Steam Turbine Hall |  | F54A | Hardener Finish(Liquid Type) on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | TVEP | TVEP | Steam Turbine Building(ST) | Steam Turbine Hall |  | Hardener Finish on Steel Trowel Finish | Epoxy Paint (H=100) | Latex Paint on Thk15 Cement Plaster | Exposed Roof
| HRSG Hall |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | *발주처 Hardener 요구 확인
HRSG Building(ST) | HRSG Hall |  | F54A | Hardener Finish(Liquid Type) on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | UTCC | UTCC | Gas Turbine Building(ST) | Gas Turbine Hall |  | 1. Hardener Finish 2. Steel Trowel Finish | Epoxy Paint | Emulsion Paint on Thk15 Cement Mortar Plastering (Up to 1200mm) | Exposed Roof
| Excitation Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A
Steam Turbine Building(ST) | Excitation Room |  | F07C | Epoxy Screed and Seal Coat on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | N.A | N.A | RAPO | RAPO | Steam Turbine Building(ST) | Excitation Room |  | 5mm Epoxy Screed and Seal Coat on Concrete Slab | Epoxy Paint (H=100) | Emulsion Paint on Thk15 Cement Mortar (Up to 2500mm) | Exposed Roof | * 5mm Epoxy Screed and Seal Coat : 계약사양
Steam Turbine Building(ST) | Excitation TR & Cubicle Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W03B | Latex Paint on Cement Plaster | N.A | N.A | TVEP | TVEP | Steam Turbine Building(ST) | Excitation TR & Cubicle Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Thk15 Cement Plaster | Exposed Deck
| Sampling Room |  | F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish | B04 | Chemical Resistant Epoxy Paint | W09B | Chemical Resistant Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | *바닥, 벽 Chemical 적용
Steam Turbine Building(ST) | Sampling Room |  | F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish | B04 | Chemical Resistant Epoxy Paint | W09B | Chemical Resistant Paint on Cement Plaster | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | Steam Turbine Building(ST) | Sampling Room |  | Chemical Resistant Paint on Steel Trowel Finish | Chemical Resistant Paint | Chemical Resistant Paint(≤3000) / Latex Paint (>3000) on Cement Plaster | Latex Paint on Fair Faced Concrete
| WT Equipment Room |  | F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish | B04 | Chemical Resistant Epoxy Paint | W09B | Chemical Resistant Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | *바닥, 벽 Chemical 적용
WTB(RC) | WT Equipment Room |  | F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish | B04 | Chemical Resistant Epoxy Paint | W03B | Latex Paint on Cement Plaster | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | WTB(RC) | WT Equipment Room |  | Chemical Resistant Paint on Steel Trowel Finish | Chemical Resistant Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
| Chemical Storage Room |  | F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish | B04 | Chemical Resistant Epoxy Paint | W09B | Chemical Resistant Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | *바닥, 벽 Chemical 적용
WTB(RC) | Chemical Storage Room |  | F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish | B04 | Chemical Resistant Epoxy Paint | W09B | Chemical Resistant Paint on Cement Plaster | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | WTB(RC) | Chemical Storage Room |  | Chemical Resistant Paint on Steel Trowel Finish | Chemical Resistant Paint | Chemical Resistant Paint(≤3000) / Latex Paint (>3000) on Cement Plaster | Latex Paint on Fair Faced Concrete
Laboratory & Inspection Building(RC) | Chemical Storage Room |  | F32 | Acid Resistant Ceramic Tile on Screed | B33 | Acid Resistant Ceramic Tile | W04B | Acid Resistant Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | SACE | SACE | Laboratory & Inspection Building(RC) | Chemical Storage Room |  | ACID Resistant Ceramic Tile on Screed | ACID Resistant Ceramic Tile | ACID Resistant Paint on THK13 on Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
| Dehydrator Room |  | F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish | B04 | Chemical Resistant Epoxy Paint | W09B | Chemical Resistant Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | *바닥, 벽 Chemical 적용
WTB(RC) | Dehydrator Room |  | F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish | B04 | Chemical Resistant Epoxy Paint | W03B | Latex Paint on Cement Plaster | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | WTB(RC) | Dehydrator Room |  | Chemical Resistant Paint on Steel Trowel Finish | Chemical Resistant Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
| Laboratory |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W32A | Glazed Ceramic Tile(≤C.H+100) / No Paint (>C.H+100) on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | *바닥+벽 방수 미적용
Control Building(RC) | Laboratory |  | F06B | Non-Slip Epoxy Paint on Screed | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Control Building(RC) | Laboratory |  | Epoxy Coating on Screed + Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
WTB(RC) | Laboratory |  | F32 | Acid Resistant Ceramic Tile on Screed | B33 | Acid Resistant Ceramic Tile | W33A | ACID Resistant Ceramic Tile (≤CH+100) / Acrylic Emulsion Paint (>CH+100) on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | TVEP | TVEP | WTB(RC) | Laboratory |  | ACID Resistant Ceramic Tile on Cement Screed w/ ACID Proofing Sealing |  | ACID Resistant Ceramic Tile on Cement Screed w/ ACID Proofing Sealing(≤1200) / Latex Paint (>1200) on Cement Plaster | Suspended Mineral Fiberboard Panel(600x600)
Laboratory & Inspection Building(RC) | Main Laboratory Testing Room |  | F32 | Acid Resistant Ceramic Tile on Screed | B33 | Acid Resistant Ceramic Tile | W33A | ACID Resistant Ceramic Tile (≤CH+100) / Acrylic Emulsion Paint (>CH+100) on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Laboratory & Inspection Building(RC) | Main Laboratory Testing Room |  | ACID Resistant Ceramic Tile on Screed | ACID Resistant Ceramic Tile | ACID Resistant Paint on THK13 on Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Laboratory & Inspection Building(RC) | Sample Receiving Room |  | F32 | Acid Resistant Ceramic Tile on Screed | B33 | Acid Resistant Ceramic Tile | W04B | Acid Resistant Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | SACE | SACE | Laboratory & Inspection Building(RC) | Sample Receiving Room |  | ACID Resistant Ceramic Tile on Screed | ACID Resistant Ceramic Tile | ACID Resistant Paint on THK13 on Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
| Fire Water Pump Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
Fire Water Pump BLDG(RC) | Fire Water Pump Room |  | F54A | Hardener Finish(Liquid Type) on Steel Trowel Finish | B03 | Epoxy Paint | W03B | Latex Paint on Cement Plaster | C03 | Latex Paint on Fair Faced Concrete | TVEP | TVEP | Fire Water Pump BLDG(RC) | Fire Water Pump Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
| HVAC Room |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
Control Building(RC) | Mechanical Room |  | F54B | Non-Slip Epoxy Paint with Epoxy Hardener on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | SACE | SACE | Control Building(RC) | Mechanical Room |  | Non-Slip Epoxy Paint with Epoxy Hardener on Steel Trowel Finish | Epoxy Paint H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
Control Building(RC) | HVAC Room |  | F06B | Non-Slip Epoxy Paint on Screed | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Control Building(RC) | HVAC Room |  | Epoxy Coating on Plain Concrete (w/wire mesh) + Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
Substation(RC) | HVAC Room |  | F06B | Non-Slip Epoxy Paint on Screed | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | KLNG | KLNG | Substation(RC) | HVAC Room |  | Epoxy Coating on Plain Concrete (w/wire mesh) + Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
Substation(RC) | HVAC Room |  | F07B | Epoxy Coating on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | BONE | BONE | Substation(RC) | HVAC Room |  | THK.1 Epoxy Resin on Sceed (Water Proofing Type) | THK.1 Epoxy Resin on Sceed | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
| Blast Chamber |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | *Non-Typical Room
Control Building(RC) | Blast Chamber |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | SACE | SACE | Control Building(RC) | Blast Chamber |  | Non-Slip Epoxy Paint on Steel Trowel Finish | Epoxy Paint H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
| EWH Room | *용도 확인 필요 | F34A | Vinyl Tile on Screed | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | *Non-Typical Room
Control Building(RC) | EWH Room |  | F34A | Vinyl Tile on Screed | B35A | Coved Vinyl Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) | EWH Room |  | Vinyl Tile on Screed | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
| VSD Room | *전기실? 용도 확인 필요 | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B01 | Acrylic Emulsion Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | *Non-Typical Room
Substation(RC) | VSD Room |  | F42 | Rubber Tile on Screed | B01 | Acrylic Emulsion Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | C01 | Acrylic Emulsion Paint on Fair Faced Concrete | IKAN | IKAN | Substation(RC) | VSD Room |  | Steel Trowel Finish w/ Rubber Flooring Tile (THK. 6mm) | Acrylic Emulsion Paint | Arcylic Emulsion Paint on Cement Plaster (THK. 16mm) | Arcylic Emulsion Paint
Shelter | Room |  | Floor |  | Base |  | Wall |  | Ceiling |  | Remark | Project | Building | Room |  | Floor | Base | Wall | Ceiling
| Chemical Tank Shelter |  | F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish
Chemical Tank Shelter(ST) | Chemical Tank Shelter |  | F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish | N.A | N.A | N.A | N.A | N.A | N.A | TVEP | TVEP | Chemical Tank Shelter(ST) | Chemical Tank Shelter |  | Chemical Resistant Paint on Steel Trowel Finish | N.A | N.A | N.A
| Chemical Dosing Skid Shelter |  | F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish
Chemical Dosing Skid Shelter(ST) | Chemical Dosing Skid Shelter |  | F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish | N.A | N.A | N.A | N.A | N.A | N.A | RAPO | RAPO | Chemical Tank Shelter(ST) | Chemical Tank Shelter |  | 1mm Epoxy + 0.2mm Chemical Resistant Epoxy Paint on Steel Trowel Finish | N.A | N.A | N.A
| Ash Compressor Shelter |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish
Ash Compressor Shelter(ST) | Ash Compressor Shelter |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | N.A | N.A | N.A | N.A | N.A | N.A | TVEP | TVEP | Ash Compressor Shelter(ST) | Ash Compressor Shelter |  | Epoxy Paint on Steel Trowel Finish | N.A | N.A | N.A
| Air Compressor Shelter |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish
Air Compressor Shelter(ST) | Air Compressor Shelter |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | N.A | N.A | N.A | N.A | N.A | N.A | RAPO | RAPO | Air Compressor Shelter(ST) | Air Compressor Shelter |  | 1mm Epoxy + 0.2mm Chemical Resistant Epoxy Paint on Steel Trowel Finish | N.A | N.A | N.A
| Fuel Gas ESD Shelter |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish
Fuel Gas ESD Shelter(ST) | Fuel Gas ESD Shelter |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | N.A | N.A | N.A | N.A | N.A | N.A | RAPO | RAPO | Fuel Gas ESD Shelter(ST) | Fuel Gas ESD Shelter |  | 1mm Epoxy + 0.2mm Chemical Resistant Epoxy Paint on Steel Trowel Finish | N.A | N.A | N.A

## Finish No. WM-Interior
Category | Finish Style Number | Finish Style Name | Main Spec. | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Remark
1 | Interior Finish - Floor
Paint | F03 | Acid Resistant Paint on Steel Trowel Finish | Steel Trowel Finish | A04AS173-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Acid Resistant Paint | A04AM080-00003 |  | M2 | Finishing Work | Painting Work | Floor Painting | Acid/Alkaline Resistant Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Paint | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | Steel Trowel Finish | A04AS173-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Epoxy Paint | A04AM080-00006 |  | M2 | Finishing Work | Painting Work | Floor Painting | Epoxy Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Paint | F06B | Non-Slip Epoxy Paint on Screed | Screed | A04AS168-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Screed | 0 | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Epoxy Paint | A04AM080-00006 |  | M2 | Finishing Work | Painting Work | Floor Painting | Epoxy Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Paint | F07B | Epoxy Coating on Steel Trowel Finish | Screed | A04AS173-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Epoxy Paint | A04AM080-00007 |  | M2 | Finishing Work | Painting Work | Floor Painting | Epoxy Based Sealer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Paint | F11 | Non-Slip Chemical Resistant Epoxy Paint on Steel Trowel Finish | Steel Trowel Finish | A04AS173-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Chemical Resistant Paint | A04AM080-00011 |  | M2 | Finishing Work | Painting Work | Floor Painting | Chemical Resistant Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tile | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | Liquid Waterproofing Floor | A04AP085-00001 |  | M2 | Finishing Work | Waterproofing Work | Liquid Waterproofing | 0 | 0 | 0 | 0 | for Internal Floor Area | Min. 2 Coats | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Unglazed Ceramic Tile Floor | A04AN083-00001 |  | M2 | Finishing Work | Tile Work | Floor Tile | Ceramic Tile | 0 | 0 | 0 | 0 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200x200xT40
Tile | F34B | Vinyl Tile on Steel Trowel Finish | Steel Trowel Finish | A04AS173-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Vinyl Tile Floor | A04AN083-00004 |  | M2 | Finishing Work | Tile Work | Floor Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300x300xT2
Hardener | F53A | Hardener Finish(Powder Type) | Hardener Finish(Powder Type) | A04AS173-00003 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Steel Trowel Finish | Hardener Finish(Powder Type) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Epoxy Paint | A04AM080-00006 |  | M2 | Finishing Work | Painting Work | Floor Painting | Epoxy Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Raised Floor | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | Steel Trowel Finish | A04AS173-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Anti-Dust Paint_Floor | A04AM080-00005 |  | M2 | Finishing Work | Painting Work | Floor Painting | Anti-Dust Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Raised Floor_Anti-Static Vinyl Tile | A04AS174-00001 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Raised Floor | Top Finish: Anti-Static Vinyl Tile | 0 | 0 | 0 | 0 | 0 | 0 | 600mm x 600mm / H≤600mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600x600xH600
| N.A | N.A
2 | Interior Finish - Wall Base
Paint | B02 | Acid Resistant Paint | Acid Resistant Paint | A04AM081-00004 |  | M | Finishing Work | Painting Work | Skirt Painting | Acid/Alkaline Resistant Paint | 0 | 0 | 0 | 0 | 0 | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=100
Paint | B03 | Epoxy Paint | Wall Base-Epoxy Painting | A04AM081-00007 |  | M | Finishing Work | Painting Work | Skirt Painting | Epoxy Paint | 0 | 0 | 0 | 0 | 0 | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=100
Paint | B04 | Chemical Resistant Epoxy Paint | Wall Base-Chemical Resistant Epoxy Painting | A04AM081-00010 |  | M | Finishing Work | Painting Work | Skirt Painting | Chemical Resistant Paint | 0 | 0 | 0 | 0 | 0 | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=100
Tile | B31 | Unglazed Ceramic Tile | Wall Base-Unglazed Ceramic Tile | A04AN084-00002 |  | M | Finishing Work | Tile Work | Skirt Tile | Unglazed Ceramic Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=150
Tile | B32 | Coved Ceramic Tile | Wall Base-Glazed Ceramic Tile | A04AN084-00005 |  | M | Finishing Work | Tile Work | Skirt Tile | Glazed Ceramic Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=150
Tile | B33 | Acid Resistant Ceramic Tile | Wall Base-Acid Resistant Ceramic Tile | A04AN084-00008 |  | M | Finishing Work | Tile Work | Skirt Tile | Acid/Alkaline Resistant Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 150mm≤H<200mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=150
Tile | B35A | Coved Vinyl Tile | Wall Base-Vinyl Tile | A04AN084-00013 |  | M | Finishing Work | Tile Work | Skirt Tile | Vinyl Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=100
Tile | B42 | Coved Rubber Skirting | Wall Base-Vinyl Tile | A04AS185-00001 |  | M | Finishing Work | Exterior/Interior Finish Work | Coved Rubber Skirting | 0 | 0 | 0 | 0 | for Skirt | w/ Adhesive | 0 | H<150mm | 0 | H=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H=100
| N.A | N.A
3 | Interior Finish - Wall
Paint | W01A | Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint_Int. Wall | A04AM078-00001 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Paint | W01B | Acrylic Emulsion Paint on Cement Plaster | Water Emulsion Paint_Int. Wall | A04AM078-00001 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Internal Wall Painting
|  |  | Int. Plaster Wall | A04AT198-00002 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for Internal Masonry Wall | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T12
Paint | W04B | Acid Resistant Paint on Cement Plaster | Acid/Alkaline Resistant Paint_Int. Wall | A04AM078-00004 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Acid/Alkaline Resistant Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Int. Plaster Wall | A04AT198-00002 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for Internal Masonry Wall | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T12
Paint | W05A | Epoxy Paint on Fair Faced Concrete | Epoxy Paint _Int. Wall | A04AM078-00005 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Epoxy Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Paint | W09B | Chemical Resistant Paint on Cement Plaster | Chemical Resistant Paint _Int. Wall | A04AM078-00009 |  | M2 | Finishing Work | Painting Work | Internal Wall Painting | Chemical Resistant Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Chemical Resistant Paint
|  |  | Int. Plaster Wall | A04AT198-00002 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for Internal Masonry Wall | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T12
Tile | W32F | Glazed Ceramic Tile on Cement Plaster + Liquid Waterproofing | Glazed Ceramic Tile Wall | A04AN082-00002 |  | M2 | Finishing Work | Tile Work | Wall Tile | Glazed Ceramic Tile | 0 | 0 | 0 | 0 | w/ Mortar Bond Coat or Adhesive | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200x200xT40
|  |  | Liquid Waterproofing Wall | A04AP085-00002 |  | M2 | Finishing Work | Waterproofing Work | Liquid Waterproofing | 0 | 0 | 0 | 0 | for Internal Wall Area | Min. 2 Coats | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tile | W34 | Granite Tile | Granite Tile | A04AN082-00004 |  | M2 | Finishing Work | Tile Work | Wall Tile | Granite Tile | 0 | 0 | 0 | 0 | w/ Wet Method (Mortar Bond Coat or Adhesive) or Dry Method (Steel or SST Frame, Angle, Bolt, etc.) | 0 | 0 | 0 | Tile Size=W( )mm x L( )mm x THK( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | w/ Wet Method (Mortar Bond Coat or Adhesive) or Dry Method (Steel or SST Frame, Angle, Bolt, etc.)
| N.A | N.A
4 | Interior Finish - Ceiling
| C01 | Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint_Ceiling | A04AM079-00001 |  | M2 | Finishing Work | Painting Work | Ceiling Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| C04 | Acid Resistant Paint on Fair Faced Concrete | Acid/Alkaline Resistant Paint_Ceiling | A04AM079-00004 |  | M2 | Finishing Work | Painting Work | Ceiling Painting | Acid/Alkaline Resistant Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| C06 | Epoxy Paint on Fair Faced Concrete | Epoxy Paint_Ceiling | A04AM079-00006 |  | M2 | Finishing Work | Painting Work | Ceiling Painting | Epoxy Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | Acoustic Tiled Ceiling | A04AS190-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Acoustic Tiled Ceiling System | T-Bar System | 0 | 0 | 0 | 0 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | 0 | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600x600
| C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | Moisture Resistant Tiled Ceiling | A04AS191-00002 |  | M2 | Finishing Work | Exterior/Interior Finish Work | Moisture Resistant Tiled Ceiling System | T-Bar System | 0 | 0 | 0 | 0 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | 0 | 0 | 0 | Tile Size=( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600x600
| N.A | N.A

## 팀 표준 마감기준-Ext
팀 기준 사양 | [11 empty] | 프로젝트 적용 현황
* 동일 Finish Material 의 두께, Size, 높이가 다른 경우 => 별도 구분 않함.
Building | Room | Description | Floor |  | Base |  | Wall |  | Ceiling |  | Remark | Project | Building | Description | Interior Finish | Base Material Int. | Base Material Insulation | Base Material Ext. | Exterior Finish |  | Remark
|  |  |  | 기준:Concrete Slab |  | 기준:Masonry Wall |  | 기준:Masonry Wall |  | 기준:Concrete Slab |  | Exterial Wall (RC Building)
| Office |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) |  | Gypsum + Concrete or Masonry
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE | Control Building(RC) |  | Acrylic Emulsion Paint | THK16 'Regular' Gypsum Board / THK110 Metal Stud | Non-combustible Insulation | THK0.25 Vapor Barrier / THK250 Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete (Textured)
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | LECO | Main Control Building(RC) |  | Emulsion Paint | THK12.5 Gypsum Board 2Ply | THK10 Air Space / THK135 Insulation ("가"등급) | THK150 Concrete Wall | Emulsion Paint on Fair Faced Concrete
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | LECO | ARG MCC Building(RC) |  | Emulsion Paint | THK12.5 Gypsum Board 2Ply | THK10 Air Space / THK135 Insulation ("가"등급) | THK190 Concrete Block | Emulsion Paint on THK24 Cement Plaster
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | UTCC | Fuel Gas Electrical Building(RC) |  | Emulsion Paint | Gypsum Board THK9.5mm 2 Plies | THK50 Fire Resistant Rigid Mineral Wool Insulation Board | THK380 Burnt Brick | Emulsion Paint on Cement Plastering
| Office |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) |  | Masonry + Masonry
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | KLNG | Administration Building(RC) |  | Acrylic Emulsion Paint on THK15 Cement Plaster | Concrete Block (390x90x190) | THK35 Air Gap / THK100 Fiberglass Insulation | Concrete Block (390x190x190) | Texture Paint on THK20 Cement Plaster
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | RAPO | CCB & Administration Building(RC) |  | Emulsion Paint on THK15 Cement Plaster | THK200 Hollow Concrete Block | THK20 Air Gap / THK50 Insulation | THK100 Hollow Concrete Block | Emulsion Paint on THK20 Cement Mortar
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | RAPO | GIS Building |  | THK15 Cement Render | THK200 Hollow Concrete Block | THK20 Air Gap / THK50 Insulation | THK100 Solid Block | THK20 Cement Render
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | TVEP | Administration Building(RC) |  | Latex Paint on THK15 Cement Plaster | THK190 Concrete Block | THK20 Air Gap / THK50 Insulation | THK100 Concrete Block | Latex Paint on THK15 Cement Plaster
| Office |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) |  | MISC
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | 안동 (남부발전) | 유지창고(RC) |  | THK18 시멘트몰탕 위 수성페인트 | 1.0B 시멘트 벽돌 |  | THK50 메탈판넬
|  |  |  | 기준:Concrete Slab |  | 기준:Masonry Wall |  | 기준:Masonry Wall |  | 기준:Concrete Slab |  | Skirt Wall (Steel Building)
| Office |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) |  | Masonry + Masonry
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | UTCC | Main Building (ST) | Insulated | Emulsion Paint on THK15 Cement Mortar Plastering | THK120 Burnt Brick | THK15 Air Gap / THK50 Fire Resistant Rigid Mineral Wool Insulation Board (40kg/m3 Density) | THK150 Concrete Wall | Emulsion Paint on Fair Faced Concrete
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | TVEP | Warehouse(ST) | Insulated | Latex Paint on THK15 Cement Plaster | THK100 Concrete Block | THK20 Air Gap / THK50 Insulation | THK190 Concrete Block | Latex Paint on THK15 Cement Plaster
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | RAPO | Gas Turbine Building(ST) | Insulated | Emulsion Paint on THK15 Cement Plaster | THK200 Hollow Concrete Block | THK20 Air Gap / THK50 Insulation | THK100 Hollow Concrete Block | Emulsion Paint on THK20 Cement Mortar
|  |  |  | 기준:Concrete Slab |  | 기준:Masonry Wall |  | 기준:Masonry Wall |  | 기준:Concrete Slab |  | Exterial Wall (Steel Building)
| Office |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | LECO | Extruder Building(ST) |  |  |  | THK100 Glasswool Panel w/ 불연강판
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | RAPO | Gas Turbine Building(ST) |  |  |  | THK50 Thermal Insulated Trapezoidal AL. Cladding
Building | Room | Description | Floor |  | Base |  | Wall |  | Ceiling |  | Remark | Project | Building | Description | Base Material Roof | Roof Finish 1 | Roof Finish 2 | Roof Finish 3 | Roof Finish 4 |  | Remark
|  |  |  | 기준:Concrete Slab |  | 기준:Masonry Wall |  | 기준:Masonry Wall |  | 기준:Concrete Slab |  | Concrete Roof (RC Building)
| Office |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | SACE |  |  | Concrete Slab | Min. THK50 Lightweight Screed w / WWF (150x150-MW9xMW9) *Slope : 2% | Nominally THK120 Rigid Insulation (R-30, Fully Adhered) | THK1.52 Single Ply EPDM Membrane (Fully Bonded)
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | LECO |  |  | Concrete Slab | THK3 복합방수시트 | THK.220 Roof Rigid Insulation ("가"등급) | THK.0.2 P.E Film | THK50(min) Plain Concrete *Slope : 1%
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | IKAN |  |  | Concrete Slab | Min. THK50 Cement Screed *Slope : 1% | THK.0.15mm P.E FILM | THK110mm Rigid Extruded Polystyrene Insulation | Fully Bonded THK1.5 Single Ply EPDM Sheet
Control Building(RC) | OPS Shift Co-Ordinator |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | UTCC |  |  | Concrete Slab / Steel Trowel Finish *Slope | Bituminous Water Proof Membrane (THK.4mm) | THK.100 Polystyrene Rigid Insulation (Compressive Strength Min.40 kPa) | THK.0.1 P.E Film (2 Plys) | THK.60 Protection Concrete (w/ #8-150x150 W.W.F)
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | TVEP |  |  | Concrete Slab / Steel Trowel Finish | Prime Coat / Built-up Water Proofing Membrane | THK.50 Rigid Insulation | THK.0.1 P.E Film (2 Plys) | Min.60 Protection Concrete (Slope 2/100) W/ #8-150x150 Wire Mesh *Slope 2%
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | TIPO |  |  | Concrete Slab / Steel Trowel Finish *Slope | Asphalt Primer / 2 Layers of Asphalt-Impregnated Roofing Felt | THK.50 Rigid Insulation | 2 Layers of P.E Film (THK.0.1mm) | Min. 15mm Cement Mortar / Concrete Roof Tile (300x300x30)
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | GULF |  | 터키업체 설계 | Concrete Slab / Steel Trowel Finish | Light Weight Celular Leveling Concrete (500~550 kg/m3) *Min. Slope 1.5% | Asphalt Primer / Double Layer Modified Bitumen Membrane Waterproofing Thk.3mm | THK.50mm Thermal Insulation Extruded Polystyrene Board (Density 32~35 kg/m3) | Filter Fabric / Gravel 50mm or Cement Paver (400x400x40 w/ Plastic Support)
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | RAPO |  |  | Concrete Slab / Steel Trowel Finish *Slope 1% (W.W.F #8 150x150) | THK.4 Waterproofing Membrane w/ Cold Worked Prime Coat | THK.75mm Rigid Insulation (Polystyrene) | THK.0.1mm P.E Film 2 Ply | Min. 20mm Bed Mortar / Precast Concrete Roof Tile (400x400x40)
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | RAPO (GIS) |  | 현지설계 | Concrete Slab / Steel Trowel Finish | Min.50 Thk. Lightweight Form Concrete, Laid to Fall *slope 1:80 (1.25%) | Bituminous primer - 2 Coats / Bituminous Membrane - 4mm Thick | THK.75mm Extruded Polystyrene Insulation Board | Geo-Textile Water Filtering Membrane - Terram / Precast Concrete Roof Tile (400x400x50)
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | Jebel-L |  |  | Concrete Slab | Min. THK.40 Slope Screed | THK.4 Waterproofing Membrane | 2 Layers of THK.50 Roofmate Sheet | 2 Layers of THK.0.1 Non-woven Polypropylene | THK.20 Sand / Building Paper / Concrete Roof Tile (400x400x40) w/ THK.20 Mortar Bedding
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | 평택탈황 (서부발전) |  |  | Concrete Slab | THK.3 Sheet 방수 | THK.50mm Insulation | THK.0.1mm P.E Film 2 Ply | THK.60 Lightweight Concrete w/ Wiremesh #8-150x150
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | 안동 (남부발전) |  |  | Concrete Slab / Steel Trowel Finish | 일체형 복합방수 | THK.110mm Insulation(압출보온판 "가"급) | THK.0.1mm P.E Film 2 Ply | THK.60(min) 무근콘크리트(25-24-12) w/ #8-150x150 W.W.F. *Slope 1%
Control Building(RC) | Library |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | KLNG |  |  | Concrete Slab | Min. THK50 Lightweight Concrete (Cement Screed on Lightweight Concrete for Surface Treatment) | Bituminous Coating / 4mm Bituminous Waterproofing Membrane | THK.50mm Extruded Polystyrene Rigid Board | THK.0.15mm Polyethylene Sheet | 50mm Concrete Topping with Welded Wire Fabric
|  |  |  | 기준:Concrete Slab |  | 기준:Masonry Wall |  | 기준:Masonry Wall |  | 기준:Concrete Slab |  | Cladding Roof (Steel Building)
| Office |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | LECO | Extruder Building(ST) |  |  | THK150 Glasswool Panel w/ 불연강판
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | LECO | Process Building(ST) |  |  | THK150 내화 Glasswool Panel (0.5HR) w/ 불연강판
Control Building(RC) | Shift Superintendent |  | F31A | Non-Slip Unglazed Ceramic Tile on Screed | B32 | Coved Ceramic Tile | W01B | Acrylic Emulsion Paint on Cement Plaster | C95A | Suspended Acoustic Tiled Ceiling (T-Bar) | SACE | RAPO | Gas Turbine Building(ST) |  |  | THK75 Thermal Insulated Trapezoidal AL. Cladding
2023-01-24
SACE

## Finish No. WM-Exterior
Category | Mark | Description | Main Spec. | Work Master Code | Gauge Code | Unit | Work Category-L1 | Work Category -L2 | Work Category -L3 | Spec. 1 - L4 | Spec. 2 - L5 | Spec. 3 - L6 | Spec. 4 - L7 | Spec. 5 - L8 | Spec. 6 - L9 | Spec. 7 - L10 | Spec. 8 - L11 | BOQ Spec1 | BOQ Spec2 | BOQ Spec3 | BOQ Spec4 | BOQ Spec5 | BOQ Spec6 | BOQ Spec7 | BOQ Spec8 | BOQ Spec9 | Remark-1
5B | Exterior Wall - Base Material
Masonry | EWB1 | Concrete Brick + Insulation + Concrete Brick | Exterior - Concrete Brick | A04AL073-00001 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5B Concrete Brick
|  |  | Air Gap | [23 empty] | T20 Air Gap
|  |  | Wall Insulation_Glass Wool | A04AL076-00005 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T50
|  |  | Interior - Concrete Brick | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0B Concrete Brick
|  |  | Exterior - Plaster | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T12 *Interior Plaster는 실내마감에서 산출
|  |  | Exterior - Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Masonry | EWB2 | Burnt Clay Brick + Insulation + Burnt Clay Brick | Exterior - Burnt Clay Brick | A04AL074-00001 |  | M2 | Finishing Work | Masonry Work | Burnt Clay Brick | 0 | 0 | 0 | 0 | 0 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5B Burnt Clay Brick
|  |  | Air Gap | [23 empty] | T20 Air Gap
|  |  | Wall Insulation_Glass Wool | A04AL076-00005 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T50
|  |  | Interior - Burnt Clay Brick | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0B Burnt Clay Brick
Masonry | EWB2 | Concrete Block + Insulation + Concrete Block | Exterior - Concrete Block | A04AL069-00001 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 50mm<THK≤100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 in. Concrete Block
|  |  | Air Gap | [23 empty] | T20 Air Gap
|  |  | Wall Insulation_Glass Wool | A04AL076-00005 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T50
|  |  | Interior - Concrete Block | A04AL073-00002 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 90mm<THK≤190mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 in. Concrete Block
|  |  | Exterior - Plaster | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T12 *Interior Plaster는 실내마감에서 산출
|  |  | Exterior - Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Masonry | EWB2 | Concrete Brick + Insulation + Concrete Wall | Exterior - Concrete Brick | A04AL073-00001 |  | M2 | Finishing Work | Masonry Work | Concrete Brick | 0 | 0 | 0 | 0 | 0 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5B Concrete Brick
|  |  | Air Gap | [23 empty] | T20 Air Gap
|  |  | Wall Insulation_Glass Wool | A04AL076-00005 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T50
Interior - Concrete Wall * Concrete 별도 산출
|  |  | Exterior - Plaster | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T12 *Interior Plaster는 실내마감에서 산출
|  |  | Exterior - Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Masonry | EWB3 | Burnt Clay Brick + Insulation + Concrete Wall | Exterior - Burnt Clay Brick | A04AL074-00001 |  | M2 | Finishing Work | Masonry Work | Burnt Clay Brick | 0 | 0 | 0 | 0 | 0 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | THK≤90mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5B Burnt Clay Brick
|  |  | Air Gap | [23 empty] | T20 Air Gap
|  |  | Wall Insulation_Glass Wool | A04AL076-00005 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T50
Interior - Concrete Wall * Concrete 별도 산출
Masonry | EWB2 | Concrete Block + Insulation + Concrete Wall | Exterior - Concrete Block | A04AL069-00001 |  | M2 | Finishing Work | Masonry Work | Reinforced Concrete Block | 0 | 0 | 0 | 0 | 0 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 0 | 50mm<THK≤100mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 in. Concrete Block
|  |  | Air Gap | [23 empty] | T20 Air Gap
|  |  | Wall Insulation_Glass Wool | A04AL076-00005 |  | M2 | Finishing Work | Masonry Work | Insulation | Glass Wool (Fiberglass) | 0 | 0 | 0 | 0 | Minimum Density of 50 kg/m3 | 0 | THK<50mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T50
Interior - Concrete Wall * Concrete 별도 산출
|  |  | Exterior - Plaster | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T12 *Interior Plaster는 실내마감에서 산출
|  |  | Exterior - Paint | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cladding | EWB5 | Cladding Wall -Galv. Steel | Cladding Wall FR-N/A -Mineral Wool (Rock Wool) | A05ZZ200-00001 |  | M2 | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | 0 | 0 | Mineral Wool (Rock Wool) | for Wall | w/ Accessories, Flashing | 0 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T50
Cladding | EWB6 | Cladding Wall -Galv. Steel | Cladding Wall FR-N/A -Glass Wool(Fiberglass) | A05ZZ200-00025 |  | M2 | Cladding Work | - | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | 0 | 0 | Glass Wool (Fiberglass) | for Wall | w/ Accessories, Flashing | 0 | 50mm≤THK<70mm | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T50
5 | Exterior Finish - Wall
Ext. Finish Wall -1 | EW1 | Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint_Ext. Wall | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | External Wall Painting
| Emulsion Paint on Cement Plaster |  | Ext. Plaster Wall_T18 | A04AT198-00001 |  | M2 | Finishing Work | Plastering Work | Plastering | 0 | 0 | 0 | 0 | for External Masonry Wall | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | for External Masonry Wall
Ext. Finish Wall -2 | EW2 | Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint_Ext. Wall | A04AM077-00001 |  | M2 | Finishing Work | Painting Work | External Wall Painting | Acrylic Emulsion Paint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | External Wall Painting
Emulsion Paint on Fair Faced Concrete
Ext. Finish Wall -3 | EW3 | Thk.50 Glass Wool Insulated Matal Cladding
Thk.50 Glass Wool Insulated Matal Cladding
Ext. Finish Wall -4 | EW4
Ext. Finish Wall -5 | EW5
N.A
6B | Roof - Base Material
Ext. Wall Base Material-1 | RFB1 | Concrete Roof Deck | Concrete, UG, Cement Type-1, 24MPa | A03AF032-00010 |  | M3 | Concrete Work | Superstructure Work | Structural Concrete | 0 | Cement Type-1 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cement Type-1
| Concrete Roof Deck |  | Re-bar, Fy=420 MPa - ASTM A615 GRADE 60 (Fy=420MPa) | A03AF037-00002 |  | TON | Concrete Work | Superstructure Work | Rebar Work | Deformed Bar (Non-Coat.) | 0 | 400MPa<Fy≤470MPa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400MPa<Fy≤470MPa
|  |  | Steel Deck Plate 600x200x75, THK=1.6mm (제작 Only) | S02AA024-00001 |  | M2 | Miscellaneous Steel Fabrication Work | Shelter/Building | Galvanized Steel Deck Plate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | Miscellaneous Steel Fabrication Work
|  |  | Steel Deck Plate 600x200x75, THK=1.6mm (시공 Only) | S04AA024-00001 |  | M2 | Miscellaneous Steel Erection Work | Shelter/Building | Galvanized Steel Deck Plate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | Miscellaneous Steel Erection Work
6 | Exterior Finish - Roof
Roof Finish -1 | RF1 | Protective Conc. on Water Proof Membrane with Rigid Insulation | Slope Mortar Min. THK=40mm, Slope 1:100 | A04AQ086-00004 |  | M3 | Finishing Work | Roof Work | Roof Screed | Bed Mortar Screed | 0 | 0 | 0 | 0 | w/o Welded Wire Fabric | 0 | 30mm≤Min. THK<50mm | 0 | Min. THK=( )mm, Slope=( ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Min. THK=( )mm, Slope=( )
| Protective Conc. on Water Proof Membrane with Rigid Insulation | For Concrete Roof | Roof_Wire Mesh_#8 (4mm) x150x150 for Slope Mortar | A04AQ038-00001 |  | M2 | Finishing Work | Roof Work | Welded Wire Fabric | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIA≤6mm | 0 | Mesh Size=DIA( )mm x ( )mm x ( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesh Size=DIA( )mm x ( )mm x ( )mm
|  |  | Waterproofing Membrane Roof_T2 | A04AQ310-00001 |  | M2 | Finishing Work | Roof Work | Waterproofing Membrane | EPDM(or Equivalent) | 0 | 0 | 0 | 0 | w/ Accessories | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EPDM(or Equivalent)
|  |  | Rigid Extruded Polystyrene Foam Insulation, THK=200mm | A04AQ088-00004 |  | M2 | Finishing Work | Roof Work | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation | 0 | 0 | 0 | 0 | 0 | 0 | 100mm≤THK | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rigid Extruded Polystyrene Foam Insulation
|  |  | THK.0.1 PE Sheet 2Ply | A04AQ012-00001 |  | M2 | Finishing Work | Roof Work | PE Sheet (Vapor Barrier) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THK=( )mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PE Sheet (Vapor Barrier)
|  |  | Protective Concrete w/ Steel Trowel Finish | A04AQ089-00001 |  | M3 | Finishing Work | Roof Work | Protective Concrete w/ Steel Trowel Finish | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Protective Concrete w/ Steel Trowel Finish
Roof Finish -2 | RF2 | Roof Tile on Water Proof Membrane with Rigid Insulation
Roof Tile on Water Proof Membrane with Rigid Insulation
Roof Finish -3 | RF3
Roof Finish -4 | RF4
Roof Finish -5 | RF5
Roof Finish -6 | RF6
N.A

## WM-AR
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
Work Master
As of 2022-02-11
Work Master Code | Discipline | Category(Large) |  | Category(Middle) |  | Category(Small) |  | Attributes Specifications | [15 empty] | BOQ Specifications | [8 empty] | UoM |  | Work Group Code | Work Master Code
|  | Code | Description | Code | Description | Code | Description | Code | L04 | Code | L05 | Code | L06 | Code | L07 | Code | L08 | Code | L09 | Code | L10 | Code | L11 | B01 | B02 | B03 | B04 | B05 | B06 | B07 | B08 | B09 | UoM1 | UoM2
A00ZZ000-00001 | AR | A00 | AR-Dummy | ZZ | - | 000 | - | [25 empty] | LOT | LOT | A00ZZ000 | A00ZZ000-00001
A01ZZ001-00001 | AR | A01 | Earth Work | ZZ | - | 001 | Excavation | 01 | Soil, Manual | [10 empty] | 01 | D ≤ 1.5M | [11 empty] | M3 | M3 | A01ZZ001 | A01ZZ001-00001
A01ZZ001-00002 | AR | A01 | Earth Work | ZZ | - | 001 | Excavation | 01 | Soil, Manual | [10 empty] | 02 | 1.5M < D ≤ 2.0M | [11 empty] | M3 | M3 | A01ZZ001 | A01ZZ001-00002
A01ZZ001-00003 | AR | A01 | Earth Work | ZZ | - | 001 | Excavation | 01 | Soil, Manual | [10 empty] | 03 | D > 2.0M | [11 empty] | M3 | M3 | A01ZZ001 | A01ZZ001-00003
A01ZZ001-00004 | AR | A01 | Earth Work | ZZ | - | 001 | Excavation | 02 | Soil, Mech. | [10 empty] | 04 | D ≤ 2.0M | [11 empty] | M3 | M3 | A01ZZ001 | A01ZZ001-00004
A01ZZ001-00005 | AR | A01 | Earth Work | ZZ | - | 001 | Excavation | 02 | Soil, Mech. | [10 empty] | 05 | 2.0M < D ≤ 4.0M | [11 empty] | M3 | M3 | A01ZZ001 | A01ZZ001-00005
A01ZZ001-00006 | AR | A01 | Earth Work | ZZ | - | 001 | Excavation | 02 | Soil, Mech. | [10 empty] | 06 | D > 4.0M | [11 empty] | M3 | M3 | A01ZZ001 | A01ZZ001-00006
A01ZZ001-00007 | AR | A01 | Earth Work | ZZ | - | 001 | Excavation | 03 | Weathered Rock | [14 empty] | RQD Value=( )% | [8 empty] | M3 | M3 | A01ZZ001 | A01ZZ001-00007
A01ZZ001-00008 | AR | A01 | Earth Work | ZZ | - | 001 | Excavation | 04 | Soft Rock | [14 empty] | RQD Value=( )% | [8 empty] | M3 | M3 | A01ZZ001 | A01ZZ001-00008
A01ZZ001-00009 | AR | A01 | Earth Work | ZZ | - | 001 | Excavation | 05 | Hard Rock | [14 empty] | RQD Value=( )% | [8 empty] | M3 | M3 | A01ZZ001 | A01ZZ001-00009
A01ZZ002-00001 | AR | A01 | Earth Work | ZZ | - | 002 | Blasting for Excavation | 04 | Soft Rock | [14 empty] | RQD Value=( )% | [8 empty] | M3 | M3 | A01ZZ002 | A01ZZ002-00001
A01ZZ002-00002 | AR | A01 | Earth Work | ZZ | - | 002 | Blasting for Excavation | 05 | Hard Rock | [14 empty] | RQD Value=( )% | [8 empty] | M3 | M3 | A01ZZ002 | A01ZZ002-00002
A01ZZ003-00001 | AR | A01 | Earth Work | ZZ | - | 003 | Backfill | 06 | Re-use, Soil | [19 empty] | Compaction=( )% |  |  |  | M3 | M3 | A01ZZ003 | A01ZZ003-00001
A01ZZ003-00002 | AR | A01 | Earth Work | ZZ | - | 003 | Backfill | 07 | Borrow Soil (Borrow Pit provided by Client, Free of Charge) | [17 empty] | Borrow Pit Distance=Appx. ( )km |  | Compaction=( )% |  |  |  | M3 | M3 | A01ZZ003 | A01ZZ003-00002
A01ZZ003-00003 | AR | A01 | Earth Work | ZZ | - | 003 | Backfill | 08 | Purchased, Soil | [19 empty] | Compaction=( )% |  |  |  | M3 | M3 | A01ZZ003 | A01ZZ003-00003
A01ZZ004-00001 | AR | A01 | Earth Work | ZZ | - | 004 | Disposal | 09 | Soil | [17 empty] | Disposal Distance=Appx. ( )km from Site | [5 empty] | M3 | M3 | A01ZZ004 | A01ZZ004-00001
A01ZZ004-00002 | AR | A01 | Earth Work | ZZ | - | 004 | Disposal | 03 | Weathered Rock | [17 empty] | Disposal Distance=Appx. ( )km from Site | [5 empty] | M3 | M3 | A01ZZ004 | A01ZZ004-00002
A01ZZ004-00003 | AR | A01 | Earth Work | ZZ | - | 004 | Disposal | 04 | Soft Rock | [17 empty] | Disposal Distance=Appx. ( )km from Site | [5 empty] | M3 | M3 | A01ZZ004 | A01ZZ004-00003
A01ZZ004-00004 | AR | A01 | Earth Work | ZZ | - | 004 | Disposal | 05 | Hard Rock | [17 empty] | Disposal Distance=Appx. ( )km from Site | [5 empty] | M3 | M3 | A01ZZ004 | A01ZZ004-00004
A01ZZ004-00005 | AR | A01 | Earth Work | ZZ | - | 004 | Disposal | 10 | Contaminated Soil | [17 empty] | Disposal Distance=Appx. ( )km from Site | [5 empty] | M3 | M3 | A01ZZ004 | A01ZZ004-00005
A01ZZ005-00001 | AR | A01 | Earth Work | ZZ | - | 005 | Base Course | [14 empty] | 01 | THK≤150mm |  | THK=( )mm |  |  | CBR=( )% |  |  |  |  | M2 | M2 | A01ZZ005 | A01ZZ005-00001
A01ZZ005-00002 | AR | A01 | Earth Work | ZZ | - | 005 | Base Course | [14 empty] | 06 | 150mm<THK≤250mm |  | THK=( )mm |  |  | CBR=( )% |  |  |  |  | M2 | M2 | A01ZZ005 | A01ZZ005-00002
A01ZZ005-00003 | AR | A01 | Earth Work | ZZ | - | 005 | Base Course | [14 empty] | 07 | 250mm<THK≤350mm |  | THK=( )mm |  |  | CBR=( )% |  |  |  |  | M2 | M2 | A01ZZ005 | A01ZZ005-00003
A01ZZ005-00004 | AR | A01 | Earth Work | ZZ | - | 005 | Base Course | [14 empty] | 08 | 350mm<THK |  | THK=( )mm |  |  | CBR=( )% |  |  |  |  | M2 | M2 | A01ZZ005 | A01ZZ005-00004
A01ZZ006-00001 | AR | A01 | Earth Work | ZZ | - | 006 | Subbase Course | [10 empty] | 01 | Including Compaction of Sub-Grade |  |  | 01 | THK≤150mm |  | THK=( )mm |  |  | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase |  |  |  | M2 | M2 | A01ZZ006 | A01ZZ006-00001
A01ZZ006-00002 | AR | A01 | Earth Work | ZZ | - | 006 | Subbase Course | [10 empty] | 01 | Including Compaction of Sub-Grade |  |  | 06 | 150mm<THK≤250mm |  | THK=( )mm |  |  | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase |  |  |  | M2 | M2 | A01ZZ006 | A01ZZ006-00002
A01ZZ006-00003 | AR | A01 | Earth Work | ZZ | - | 006 | Subbase Course | [10 empty] | 01 | Including Compaction of Sub-Grade |  |  | 07 | 250mm<THK≤350mm |  | THK=( )mm |  |  | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase |  |  |  | M2 | M2 | A01ZZ006 | A01ZZ006-00003
A01ZZ006-00004 | AR | A01 | Earth Work | ZZ | - | 006 | Subbase Course | [10 empty] | 01 | Including Compaction of Sub-Grade |  |  | 08 | 350mm<THK |  | THK=( )mm |  |  | CBR=( )% for Subgrade, ( )% for Subbase | Compaction=( )% for Subgrade, ( )% for Subbase |  |  |  | M2 | M2 | A01ZZ006 | A01ZZ006-00004
A01ZZ007-00001 | AR | A01 | Earth Work | ZZ | - | 007 | Fill Material (only for Module Base Frame) | [25 empty] | M3 | M3 | A01ZZ007 | A01ZZ007-00001
A01ZZ008-00001 | AR | A01 | Earth Work | ZZ | - | 008 | Gravel | [17 empty] | DIA=( )mm~( )mm or Max DIA=( )mm | [7 empty] | M3 | M3 | A01ZZ008 | A01ZZ008-00001
A01ZZ009-00001 | AR | A01 | Earth Work | ZZ | - | 009 | Crushed Stone | [17 empty] | DIA=( )mm~( )mm or Max DIA=( )mm | [7 empty] | M3 | M3 | A01ZZ009 | A01ZZ009-00001
A01ZZ010-00001 | AR | A01 | Earth Work | ZZ | - | 010 | Clean Sand for Cable Trench or UG Pipe | [25 empty] | M3 | M3 | A01ZZ010 | A01ZZ010-00001
A01ZZ011-00001 | AR | A01 | Earth Work | ZZ | - | 011 | Anti Termite Treatment | [25 empty] | M2 | M2 | A01ZZ011 | A01ZZ011-00001
A01ZZ012-00001 | AR | A01 | Earth Work | ZZ | - | 012 | PE Sheet (Vapor Barrier) | [17 empty] | THK=( )mm | [7 empty] | M2 | M2 | A01ZZ012 | A01ZZ012-00001
A01ZZ013-00001 | AR | A01 | Earth Work | ZZ | - | 013 | Sheet Pile | [10 empty] | 02 | To Comply with ASTM A 328, Including Dewatering | [5 empty] | H=( )m | [7 empty] | M2 | M2 | A01ZZ013 | A01ZZ013-00001
A02AA014-00001 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 11 | Direct Driving | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA014 | A02AA014-00001
A02AA014-00002 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 12 | Driving After Predrilling | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA014 | A02AA014-00002
A02AA014-00003 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 13 | Jacking | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA014 | A02AA014-00003
A02AA014-00004 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 14 | Soil Cement Injected Precast(S.I.P) Pile Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA014 | A02AA014-00004
A02AA014-00005 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 15 | Double Rod Auger(D.R.A) | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA014 | A02AA014-00005
A02AA014-00006 | AR | A02 | Pile Work | AA | Piling Work | 014 | Reinforced Concrete Pile (Round Type) | 16 | Percussion Rotary Drill(P.R.D) Pile Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA014 | A02AA014-00006
A02AA015-00001 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 11 | Direct Driving | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | Size=( )mm x ( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA015 | A02AA015-00001
A02AA015-00002 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 12 | Driving After Predrilling | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | Size=( )mm x ( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA015 | A02AA015-00002
A02AA015-00003 | AR | A02 | Pile Work | AA | Piling Work | 015 | Reinforced Concrete Pile (Square Type) | 13 | Jacking | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | Size=( )mm x ( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA015 | A02AA015-00003
A02AA016-00001 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 11 | Direct Driving | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA016 | A02AA016-00001
A02AA016-00002 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 12 | Driving After Predrilling | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA016 | A02AA016-00002
A02AA016-00003 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 13 | Jacking | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA016 | A02AA016-00003
A02AA016-00004 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 14 | Soil Cement Injected Precast(S.I.P) Pile Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA016 | A02AA016-00004
A02AA016-00005 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 15 | Double Rod Auger(D.R.A) | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA016 | A02AA016-00005
A02AA016-00006 | AR | A02 | Pile Work | AA | Piling Work | 016 | Pretensioned Concrete Pile (Type-A) | 16 | Percussion Rotary Drill(P.R.D) Pile Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA016 | A02AA016-00006
A02AA017-00001 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 11 | Direct Driving | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA017 | A02AA017-00001
A02AA017-00002 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 12 | Driving After Predrilling | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA017 | A02AA017-00002
A02AA017-00003 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 13 | Jacking | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA017 | A02AA017-00003
A02AA017-00004 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 14 | Soil Cement Injected Precast(S.I.P) Pile Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA017 | A02AA017-00004
A02AA017-00005 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 15 | Double Rod Auger(D.R.A) | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA017 | A02AA017-00005
A02AA017-00006 | AR | A02 | Pile Work | AA | Piling Work | 017 | Pretensioned Concrete Pile (Type-B) | 16 | Percussion Rotary Drill(P.R.D) Pile Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA017 | A02AA017-00006
A02AA018-00001 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 11 | Direct Driving | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA018 | A02AA018-00001
A02AA018-00002 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 12 | Driving After Predrilling | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA018 | A02AA018-00002
A02AA018-00003 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 13 | Jacking | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA018 | A02AA018-00003
A02AA018-00004 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 14 | Soil Cement Injected Precast(S.I.P) Pile Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA018 | A02AA018-00004
A02AA018-00005 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 15 | Double Rod Auger(D.R.A) | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA018 | A02AA018-00005
A02AA018-00006 | AR | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 16 | Percussion Rotary Drill(P.R.D) Pile Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA018 | A02AA018-00006
A02AA019-00001 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 11 | Direct Driving | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA019 | A02AA019-00001
A02AA019-00002 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 12 | Driving After Predrilling | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA019 | A02AA019-00002
A02AA019-00003 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 13 | Jacking | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA019 | A02AA019-00003
A02AA019-00004 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 14 | Soil Cement Injected Precast(S.I.P) Pile Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA019 | A02AA019-00004
A02AA019-00005 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 15 | Double Rod Auger(D.R.A) | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA019 | A02AA019-00005
A02AA019-00006 | AR | A02 | Pile Work | AA | Piling Work | 019 | Pretensioned High-strength Concrete Pile (Type-B) | 16 | Percussion Rotary Drill(P.R.D) Pile Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA019 | A02AA019-00006
A02AA020-00001 | AR | A02 | Pile Work | AA | Piling Work | 020 | Steel Pipe Pile Work | 11 | Direct Driving | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | D=( )mm / THK=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA020 | A02AA020-00001
A02AA021-00001 | AR | A02 | Pile Work | AA | Piling Work | 021 | H-Pile Work | 11 | Direct Driving | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [6 empty] | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA021 | A02AA021-00001
A02AA022-00001 | AR | A02 | Pile Work | AA | Piling Work | 022 | Micro Pile Work | [10 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA022 | A02AA022-00001
A02AA023-00001 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 18 | R.C.D Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA023 | A02AA023-00001
A02AA023-00002 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 19 | Beneto Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA023 | A02AA023-00002
A02AA023-00003 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 20 | Earth Drill Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA023 | A02AA023-00003
A02AA023-00004 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 21 | C.I.P Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA023 | A02AA023-00004
A02AA023-00005 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 22 | M.I.P Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA023 | A02AA023-00005
A02AA023-00006 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 23 | P.I.P Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA023 | A02AA023-00006
A02AA023-00007 | AR | A02 | Pile Work | AA | Piling Work | 023 | Cast-In-Place Pile Work | 24 | J.S.P Method | [8 empty] | 03 | Including Pile Connection and Joint Welding Work | [5 empty] | DIA=( )mm | Pile Length per Hole=( )M | [6 empty] | M | M | A02AA023 | A02AA023-00007
A02AB014-00001 | AR | A02 | Pile Work | AB | Pile Head Treatment | 014 | Reinforced Concrete Pile (Round Type) | [17 empty] | DIA=( )mm | [7 empty] | EA | EA | A02AB014 | A02AB014-00001
A02AB015-00001 | AR | A02 | Pile Work | AB | Pile Head Treatment | 015 | Reinforced Concrete Pile (Square Type) | [17 empty] | Size=( )mm x ( )mm | [7 empty] | EA | EA | A02AB015 | A02AB015-00001
A02AB016-00001 | AR | A02 | Pile Work | AB | Pile Head Treatment | 016 | Pretensioned Concrete Pile (Type-A) | [17 empty] | DIA=( )mm | [7 empty] | EA | EA | A02AB016 | A02AB016-00001
A02AB017-00001 | AR | A02 | Pile Work | AB | Pile Head Treatment | 017 | Pretensioned Concrete Pile (Type-B) | [17 empty] | DIA=( )mm | [7 empty] | EA | EA | A02AB017 | A02AB017-00001
A02AB018-00001 | AR | A02 | Pile Work | AB | Pile Head Treatment | 018 | Pretensioned High-strength Concrete Pile (Type-A) | [17 empty] | DIA=( )mm | [7 empty] | EA | EA | A02AB018 | A02AB018-00001
A02AB019-00001 | AR | A02 | Pile Work | AB | Pile Head Treatment | 019 | Pretensioned High-strength Concrete Pile (Type-B) | [17 empty] | DIA=( )mm | [7 empty] | EA | EA | A02AB019 | A02AB019-00001
A02AB020-00001 | AR | A02 | Pile Work | AB | Pile Head Treatment | 020 | Steel Pipe Pile Work | [17 empty] | D=( )mm / THK=( )mm | [7 empty] | EA | EA | A02AB020 | A02AB020-00001
A02AB021-00001 | AR | A02 | Pile Work | AB | Pile Head Treatment | 021 | H-Pile Work | [25 empty] | EA | EA | A02AB021 | A02AB021-00001
A02AB022-00001 | AR | A02 | Pile Work | AB | Pile Head Treatment | 022 | Micro Pile Work | [17 empty] | DIA=( )mm | [7 empty] | EA | EA | A02AB022 | A02AB022-00001
A02AB023-00001 | AR | A02 | Pile Work | AB | Pile Head Treatment | 023 | Cast-In-Place Pile Work | [17 empty] | DIA=( )mm | [7 empty] | EA | EA | A02AB023 | A02AB023-00001
A02AC024-00001 | AR | A02 | Pile Work | AC | Pile Test | 024 | Static Axial Compressive Load Test | [25 empty] | EA | EA | A02AC024 | A02AC024-00001
A02AC025-00001 | AR | A02 | Pile Work | AC | Pile Test | 025 | Static Axial Tensile Load Test | [25 empty] | EA | EA | A02AC025 | A02AC025-00001
A02AC026-00001 | AR | A02 | Pile Work | AC | Pile Test | 026 | Lateral Load Test | [25 empty] | EA | EA | A02AC026 | A02AC026-00001
A02AC027-00001 | AR | A02 | Pile Work | AC | Pile Test | 027 | Dynamic Load Test | [25 empty] | EA | EA | A02AC027 | A02AC027-00001
A02AC028-00001 | AR | A02 | Pile Work | AC | Pile Test | 028 | Integrity Test | [25 empty] | EA | EA | A02AC028 | A02AC028-00001
A03AD029-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 37 | M12 | [9 empty] | EA | EA | A03AD029 | A03AD029-00001
A03AD029-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 38 | M16 | [9 empty] | EA | EA | A03AD029 | A03AD029-00002
A03AD029-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 39 | M20 | [9 empty] | EA | EA | A03AD029 | A03AD029-00003
A03AD029-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 40 | M22 | [9 empty] | EA | EA | A03AD029 | A03AD029-00004
A03AD029-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 41 | M24 | [9 empty] | EA | EA | A03AD029 | A03AD029-00005
A03AD029-00006 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 42 | M30 | [9 empty] | EA | EA | A03AD029 | A03AD029-00006
A03AD029-00007 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 43 | M33 | [9 empty] | EA | EA | A03AD029 | A03AD029-00007
A03AD029-00008 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 44 | M36 | [9 empty] | EA | EA | A03AD029 | A03AD029-00008
A03AD029-00009 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 45 | M42 | [9 empty] | EA | EA | A03AD029 | A03AD029-00009
A03AD029-00010 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 46 | M48 | [9 empty] | EA | EA | A03AD029 | A03AD029-00010
A03AD029-00011 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 47 | M52 | [9 empty] | EA | EA | A03AD029 | A03AD029-00011
A03AD029-00012 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 48 | M56 | [9 empty] | EA | EA | A03AD029 | A03AD029-00012
A03AD029-00013 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 49 | M64 | [9 empty] | EA | EA | A03AD029 | A03AD029-00013
A03AD029-00014 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 50 | M72 | [9 empty] | EA | EA | A03AD029 | A03AD029-00014
A03AD029-00015 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 51 | M76 | [9 empty] | EA | EA | A03AD029 | A03AD029-00015
A03AD029-00016 | AR | A03 | Concrete Work | AD | Substructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 52 | Over M76 | [9 empty] | EA | EA | A03AD029 | A03AD029-00016
A03AD030-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 36 | M10 | [9 empty] | EA | EA | A03AD030 | A03AD030-00001
A03AD030-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 37 | M12 | [9 empty] | EA | EA | A03AD030 | A03AD030-00002
A03AD030-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 38 | M16 | [9 empty] | EA | EA | A03AD030 | A03AD030-00003
A03AD030-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 39 | M20 | [9 empty] | EA | EA | A03AD030 | A03AD030-00004
A03AD030-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 40 | M22 | [9 empty] | EA | EA | A03AD030 | A03AD030-00005
A03AD030-00006 | AR | A03 | Concrete Work | AD | Substructure Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 41 | M24 | [9 empty] | EA | EA | A03AD030 | A03AD030-00006
A03AD031-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 031 | Expansion Anchor Bolt | [14 empty] | 36 | M10 | [9 empty] | EA | EA | A03AD031 | A03AD031-00001
A03AD031-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 031 | Expansion Anchor Bolt | [14 empty] | 37 | M12 | [9 empty] | EA | EA | A03AD031 | A03AD031-00002
A03AD031-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 031 | Expansion Anchor Bolt | [14 empty] | 38 | M16 | [9 empty] | EA | EA | A03AD031 | A03AD031-00003
A03AD031-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 031 | Expansion Anchor Bolt | [14 empty] | 39 | M20 | [9 empty] | EA | EA | A03AD031 | A03AD031-00004
A03AD031-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 031 | Expansion Anchor Bolt | [14 empty] | 40 | M22 | [9 empty] | EA | EA | A03AD031 | A03AD031-00005
A03AD031-00006 | AR | A03 | Concrete Work | AD | Substructure Work | 031 | Expansion Anchor Bolt | [14 empty] | 41 | M24 | [9 empty] | EA | EA | A03AD031 | A03AD031-00006
A03AD032-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 01 | F'c (Cylinder Strength) > 35MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00001
A03AD032-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 01 | F'c (Cylinder Strength) > 35MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00002
A03AD032-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 01 | F'c (Cylinder Strength) > 35MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00003
A03AD032-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00004
A03AD032-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00005
A03AD032-00006 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00006
A03AD032-00007 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00007
A03AD032-00008 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00008
A03AD032-00009 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00009
A03AD032-00010 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00010
A03AD032-00011 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00011
A03AD032-00012 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00012
A03AD032-00013 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 05 | F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00013
A03AD032-00014 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 05 | F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00014
A03AD032-00015 | AR | A03 | Concrete Work | AD | Substructure Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 05 | F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AD032 | A03AD032-00015
A03AD033-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 01 | Cement Type-1 | 01 | F'c (Cylinder Strength) > 35MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00001
A03AD033-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 02 | Cement Type-2 | 01 | F'c (Cylinder Strength) > 35MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00002
A03AD033-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 03 | Cement Type-5 | 01 | F'c (Cylinder Strength) > 35MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00003
A03AD033-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 01 | Cement Type-1 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00004
A03AD033-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 02 | Cement Type-2 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00005
A03AD033-00006 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 03 | Cement Type-5 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00006
A03AD033-00007 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 01 | Cement Type-1 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00007
A03AD033-00008 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 02 | Cement Type-2 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00008
A03AD033-00009 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 03 | Cement Type-5 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00009
A03AD033-00010 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 01 | Cement Type-1 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00010
A03AD033-00011 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 02 | Cement Type-2 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00011
A03AD033-00012 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 03 | Cement Type-5 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00012
A03AD033-00013 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 01 | Cement Type-1 | 05 | F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00013
A03AD033-00014 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 02 | Cement Type-2 | 05 | F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00014
A03AD033-00015 | AR | A03 | Concrete Work | AD | Substructure Work | 033 | Colored Concrete |  |  | 03 | Cement Type-5 | 05 | F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AD033 | A03AD033-00015
A03AD034-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  |  | 01 | Cement Type-1 | 06 | F'c (Cylinder Strength) > 20MPa | [19 empty] | M3 | M3 | A03AD034 | A03AD034-00001
A03AD034-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  |  | 02 | Cement Type-2 | 06 | F'c (Cylinder Strength) > 20MPa | [19 empty] | M3 | M3 | A03AD034 | A03AD034-00002
A03AD034-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  |  | 03 | Cement Type-5 | 06 | F'c (Cylinder Strength) > 20MPa | [19 empty] | M3 | M3 | A03AD034 | A03AD034-00003
A03AD034-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  |  | 01 | Cement Type-1 | 07 | 10MPa < F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AD034 | A03AD034-00004
A03AD034-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  |  | 02 | Cement Type-2 | 07 | 10MPa < F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AD034 | A03AD034-00005
A03AD034-00006 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  |  | 03 | Cement Type-5 | 07 | 10MPa < F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AD034 | A03AD034-00006
A03AD034-00007 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  |  | 01 | Cement Type-1 | 08 | F'c (Cylinder Strength) ≤ 10MPa | [19 empty] | M3 | M3 | A03AD034 | A03AD034-00007
A03AD034-00008 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  |  | 02 | Cement Type-2 | 08 | F'c (Cylinder Strength) ≤ 10MPa | [19 empty] | M3 | M3 | A03AD034 | A03AD034-00008
A03AD034-00009 | AR | A03 | Concrete Work | AD | Substructure Work | 034 | Lean Concrete (including Form work) |  |  | 03 | Cement Type-5 | 08 | F'c (Cylinder Strength) ≤ 10MPa | [19 empty] | M3 | M3 | A03AD034 | A03AD034-00009
A03AD035-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 035 | Form Work (3 times in use) | 25 | Flat Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AD035 | A03AD035-00001
A03AD035-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 035 | Form Work (3 times in use) | 26 | Circular Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AD035 | A03AD035-00002
A03AD036-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 036 | Form Work (1 time in use) | 25 | Flat Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AD036 | A03AD036-00001
A03AD036-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 036 | Form Work (1 time in use) | 26 | Circular Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AD036 | A03AD036-00002
A03AD037-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 09 | Fy>470MPa | [19 empty] | TON | TON | A03AD037 | A03AD037-00001
A03AD037-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 10 | 400MPa<Fy≤470MPa | [19 empty] | TON | TON | A03AD037 | A03AD037-00002
A03AD037-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 11 | 300MPa<Fy≤400MPa | [19 empty] | TON | TON | A03AD037 | A03AD037-00003
A03AD037-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 12 | Fy≤300MPa | [19 empty] | TON | TON | A03AD037 | A03AD037-00004
A03AD037-00005 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 09 | Fy>470MPa | [19 empty] | TON | TON | A03AD037 | A03AD037-00005
A03AD037-00006 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 10 | 400MPa<Fy≤470MPa | [19 empty] | TON | TON | A03AD037 | A03AD037-00006
A03AD037-00007 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 11 | 300MPa<Fy≤400MPa | [19 empty] | TON | TON | A03AD037 | A03AD037-00007
A03AD037-00008 | AR | A03 | Concrete Work | AD | Substructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 12 | Fy≤300MPa | [19 empty] | TON | TON | A03AD037 | A03AD037-00008
A03AD038-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 038 | Welded Wire Fabric | [14 empty] | 53 | DIA≤6mm |  | Mesh Size=DIA( )mm x ( )mm x ( )mm | [7 empty] | M2 | M2 | A03AD038 | A03AD038-00001
A03AD038-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 038 | Welded Wire Fabric | [14 empty] | 54 | DIA>6mm |  | Mesh Size=DIA( )mm x ( )mm x ( )mm | [7 empty] | M2 | M2 | A03AD038 | A03AD038-00002
A03AD039-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 039 | Expansion Joint (Exposed Type) | [10 empty] | 06 | w/ Flexible Joint Filler, Sealant, Dowel Bar w/ PVC Sleeve | [5 empty] | THK=( )mm | [7 empty] | M | M | A03AD039 | A03AD039-00001
A03AD040-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 040 | Expansion Joint (w/ Aluminum Cover) | [10 empty] | 07 | w/ Flexible Joint Filler, Sealant, Aluminum Flashing Cover w/ Fixing Accessories | [5 empty] | THK=( )mm | [7 empty] | M | M | A03AD040 | A03AD040-00001
A03AD041-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 041 | Expansion Joint (w/ Galvanized Steel Cover) | [10 empty] | 08 | w/ Flexible Joint Filler, Sealant, Galv. Steel Cover w/ Galv. Steel Angle, Fixing Accessories | [5 empty] | THK=( )mm | [7 empty] | M | M | A03AD041 | A03AD041-00001
A03AD042-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 042 | Expansion Joint (w/ Stainless Steel Cover) | [10 empty] | 09 | w/ Flexible Joint Filler, Sealant, SST Flashing Cover w/ Fixing Accessories | [5 empty] | THK=( )mm | [7 empty] | M | M | A03AD042 | A03AD042-00001
A03AD043-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 043 | Expansion Joint (w/ Ready-Made Cover) | [10 empty] | 10 | w/ Flexible Joint Filler, Sealant, Ready-Made Cover Profile w/ Fixing Accessories | [5 empty] | THK=( )mm | [7 empty] | M | M | A03AD043 | A03AD043-00001
A03AD044-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 044 | Isolation Joint (Separation Joint) | [10 empty] | 11 | w/ Flexible Joint Filler, Sealant | [5 empty] | THK=( )mm | [7 empty] | M | M | A03AD044 | A03AD044-00001
A03AD045-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 045 | Control Joint | [10 empty] | 12 | w/ Joint Sealant, Backstop | [5 empty] | Saw Cut: W( )mm x D( )mm | [7 empty] | M | M | A03AD045 | A03AD045-00001
A03AD045-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 045 | Control Joint | [10 empty] | 13 | w/ Joint Sealant, Backstop, Bottom Crack Inducer | [5 empty] | Saw Cut: W( )mm x D( )mm | [7 empty] | M | M | A03AD045 | A03AD045-00002
A03AD046-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 046 | Water Stop | 29 | PVC Type | [15 empty] | W=( )mm | [7 empty] | M | M | A03AD046 | A03AD046-00001
A03AD046-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 046 | Water Stop | 30 | Stainless Steel Type | [15 empty] | W=( )mm | [7 empty] | M | M | A03AD046 | A03AD046-00002
A03AD046-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 046 | Water Stop | 31 | Expandable Rubber Type | [15 empty] | W=( )mm | [7 empty] | M | M | A03AD046 | A03AD046-00003
A03AD047-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 047 | Insulation under Ground Floor | 32 | Extruded Polystyrene Insulation Board | [12 empty] | 31 | THK<50mm |  | THK=( )mm | [7 empty] | M2 | M2 | A03AD047 | A03AD047-00001
A03AD047-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 047 | Insulation under Ground Floor | 32 | Extruded Polystyrene Insulation Board | [12 empty] | 09 | 50mm≤THK<75mm |  | THK=( )mm | [7 empty] | M2 | M2 | A03AD047 | A03AD047-00002
A03AD047-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 047 | Insulation under Ground Floor | 32 | Extruded Polystyrene Insulation Board | [12 empty] | 10 | 75mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A03AD047 | A03AD047-00003
A03AD047-00004 | AR | A03 | Concrete Work | AD | Substructure Work | 047 | Insulation under Ground Floor | 32 | Extruded Polystyrene Insulation Board | [12 empty] | 11 | 100mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A03AD047 | A03AD047-00004
A03AD048-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 048 | Ladder Rung | 33 | Hot-Dip Galvanized Steel | [8 empty] | 14 | Galv.: ASTM A123 |  |  | 55 | DIA=20mm |  | L=( )mm | [7 empty] | EA | EA | A03AD048 | A03AD048-00001
A03AD048-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 048 | Ladder Rung | 34 | SUS | [12 empty] | 55 | DIA=20mm |  | L=( )mm | [7 empty] | EA | EA | A03AD048 | A03AD048-00002
A03AD048-00003 | AR | A03 | Concrete Work | AD | Substructure Work | 048 | Ladder Rung | 35 | FRP | [12 empty] | 55 | DIA=20mm |  | L=( )mm | [7 empty] | EA | EA | A03AD048 | A03AD048-00003
A03AD049-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 33 | Hot-Dip Galvanized Steel | [8 empty] | 14 | Galv.: ASTM A123 | [13 empty] | TON | TON | A03AD049 | A03AD049-00001
A03AD049-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS | [23 empty] | TON | TON | A03AD049 | A03AD049-00002
A03AD050-00001 | AR | A03 | Concrete Work | AD | Substructure Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 33 | Hot-Dip Galvanized Steel | [8 empty] | 14 | Galv.: ASTM A123 | [13 empty] | TON | TON | A03AD050 | A03AD050-00001
A03AD050-00002 | AR | A03 | Concrete Work | AD | Substructure Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS | [23 empty] | TON | TON | A03AD050 | A03AD050-00002
A03AE029-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 37 | M12 | [9 empty] | EA | EA | A03AE029 | A03AE029-00001
A03AE029-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 38 | M16 | [9 empty] | EA | EA | A03AE029 | A03AE029-00002
A03AE029-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 39 | M20 | [9 empty] | EA | EA | A03AE029 | A03AE029-00003
A03AE029-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 40 | M22 | [9 empty] | EA | EA | A03AE029 | A03AE029-00004
A03AE029-00005 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 41 | M24 | [9 empty] | EA | EA | A03AE029 | A03AE029-00005
A03AE029-00006 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 42 | M30 | [9 empty] | EA | EA | A03AE029 | A03AE029-00006
A03AE029-00007 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 43 | M33 | [9 empty] | EA | EA | A03AE029 | A03AE029-00007
A03AE029-00008 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 44 | M36 | [9 empty] | EA | EA | A03AE029 | A03AE029-00008
A03AE029-00009 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 45 | M42 | [9 empty] | EA | EA | A03AE029 | A03AE029-00009
A03AE029-00010 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 46 | M48 | [9 empty] | EA | EA | A03AE029 | A03AE029-00010
A03AE029-00011 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 47 | M52 | [9 empty] | EA | EA | A03AE029 | A03AE029-00011
A03AE029-00012 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 48 | M56 | [9 empty] | EA | EA | A03AE029 | A03AE029-00012
A03AE029-00013 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 49 | M64 | [9 empty] | EA | EA | A03AE029 | A03AE029-00013
A03AE029-00014 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 50 | M72 | [9 empty] | EA | EA | A03AE029 | A03AE029-00014
A03AE029-00015 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 51 | M76 | [9 empty] | EA | EA | A03AE029 | A03AE029-00015
A03AE029-00016 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 52 | Over M76 | [9 empty] | EA | EA | A03AE029 | A03AE029-00016
A03AE030-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 36 | M10 | [9 empty] | EA | EA | A03AE030 | A03AE030-00001
A03AE030-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 37 | M12 | [9 empty] | EA | EA | A03AE030 | A03AE030-00002
A03AE030-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 38 | M16 | [9 empty] | EA | EA | A03AE030 | A03AE030-00003
A03AE030-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 39 | M20 | [9 empty] | EA | EA | A03AE030 | A03AE030-00004
A03AE030-00005 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 40 | M22 | [9 empty] | EA | EA | A03AE030 | A03AE030-00005
A03AE030-00006 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 41 | M24 | [9 empty] | EA | EA | A03AE030 | A03AE030-00006
A03AE031-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 031 | Expansion Anchor Bolt | [14 empty] | 36 | M10 | [9 empty] | EA | EA | A03AE031 | A03AE031-00001
A03AE031-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 031 | Expansion Anchor Bolt | [14 empty] | 37 | M12 | [9 empty] | EA | EA | A03AE031 | A03AE031-00002
A03AE031-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 031 | Expansion Anchor Bolt | [14 empty] | 38 | M16 | [9 empty] | EA | EA | A03AE031 | A03AE031-00003
A03AE031-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 031 | Expansion Anchor Bolt | [14 empty] | 39 | M20 | [9 empty] | EA | EA | A03AE031 | A03AE031-00004
A03AE031-00005 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 031 | Expansion Anchor Bolt | [14 empty] | 40 | M22 | [9 empty] | EA | EA | A03AE031 | A03AE031-00005
A03AE031-00006 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 031 | Expansion Anchor Bolt | [14 empty] | 41 | M24 | [9 empty] | EA | EA | A03AE031 | A03AE031-00006
A03AE032-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 01 | F'c (Cylinder Strength) > 35MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00001
A03AE032-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 01 | F'c (Cylinder Strength) > 35MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00002
A03AE032-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 01 | F'c (Cylinder Strength) > 35MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00003
A03AE032-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00004
A03AE032-00005 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00005
A03AE032-00006 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00006
A03AE032-00007 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00007
A03AE032-00008 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00008
A03AE032-00009 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00009
A03AE032-00010 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00010
A03AE032-00011 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00011
A03AE032-00012 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00012
A03AE032-00013 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 05 | F'c (Cylinder Strength) ≤ 20MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00013
A03AE032-00014 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 05 | F'c (Cylinder Strength) ≤ 20MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00014
A03AE032-00015 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 05 | F'c (Cylinder Strength) ≤ 20MPa |  |  |  |  | 15 | Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | [13 empty] | M3 | M3 | A03AE032 | A03AE032-00015
A03AE034-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  |  | 01 | Cement Type-1 | 06 | F'c (Cylinder Strength) > 20MPa | [19 empty] | M3 | M3 | A03AE034 | A03AE034-00001
A03AE034-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  |  | 02 | Cement Type-2 | 06 | F'c (Cylinder Strength) > 20MPa | [19 empty] | M3 | M3 | A03AE034 | A03AE034-00002
A03AE034-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  |  | 03 | Cement Type-5 | 06 | F'c (Cylinder Strength) > 20MPa | [19 empty] | M3 | M3 | A03AE034 | A03AE034-00003
A03AE034-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  |  | 01 | Cement Type-1 | 07 | 10MPa < F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AE034 | A03AE034-00004
A03AE034-00005 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  |  | 02 | Cement Type-2 | 07 | 10MPa < F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AE034 | A03AE034-00005
A03AE034-00006 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  |  | 03 | Cement Type-5 | 07 | 10MPa < F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AE034 | A03AE034-00006
A03AE034-00007 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  |  | 01 | Cement Type-1 | 08 | F'c (Cylinder Strength) ≤ 10MPa | [19 empty] | M3 | M3 | A03AE034 | A03AE034-00007
A03AE034-00008 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  |  | 02 | Cement Type-2 | 08 | F'c (Cylinder Strength) ≤ 10MPa | [19 empty] | M3 | M3 | A03AE034 | A03AE034-00008
A03AE034-00009 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 034 | Lean Concrete (including Form work) |  |  | 03 | Cement Type-5 | 08 | F'c (Cylinder Strength) ≤ 10MPa | [19 empty] | M3 | M3 | A03AE034 | A03AE034-00009
A03AE035-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 035 | Form Work (3 times in use) | 25 | Flat Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AE035 | A03AE035-00001
A03AE035-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 035 | Form Work (3 times in use) | 26 | Circular Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AE035 | A03AE035-00002
A03AE036-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 036 | Form Work (1 time in use) | 25 | Flat Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AE036 | A03AE036-00001
A03AE036-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 036 | Form Work (1 time in use) | 26 | Circular Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AE036 | A03AE036-00002
A03AE037-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 09 | Fy>470MPa | [19 empty] | TON | TON | A03AE037 | A03AE037-00001
A03AE037-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 10 | 400MPa<Fy≤470MPa | [19 empty] | TON | TON | A03AE037 | A03AE037-00002
A03AE037-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 11 | 300MPa<Fy≤400MPa | [19 empty] | TON | TON | A03AE037 | A03AE037-00003
A03AE037-00004 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 12 | Fy≤300MPa | [19 empty] | TON | TON | A03AE037 | A03AE037-00004
A03AE037-00005 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 09 | Fy>470MPa | [19 empty] | TON | TON | A03AE037 | A03AE037-00005
A03AE037-00006 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 10 | 400MPa<Fy≤470MPa | [19 empty] | TON | TON | A03AE037 | A03AE037-00006
A03AE037-00007 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 11 | 300MPa<Fy≤400MPa | [19 empty] | TON | TON | A03AE037 | A03AE037-00007
A03AE037-00008 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 12 | Fy≤300MPa | [19 empty] | TON | TON | A03AE037 | A03AE037-00008
A03AE046-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 046 | Water Stop | 29 | PVC Type | [15 empty] | W=( )mm | [7 empty] | M | M | A03AE046 | A03AE046-00001
A03AE046-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 046 | Water Stop | 30 | Stainless Steel Type | [15 empty] | W=( )mm | [7 empty] | M | M | A03AE046 | A03AE046-00002
A03AE046-00003 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 046 | Water Stop | 31 | Expandable Rubber Type | [15 empty] | W=( )mm | [7 empty] | M | M | A03AE046 | A03AE046-00003
A03AE049-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 33 | Hot-Dip Galvanized Steel | [8 empty] | 14 | Galv.: ASTM A123 | [13 empty] | TON | TON | A03AE049 | A03AE049-00001
A03AE049-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS | [23 empty] | TON | TON | A03AE049 | A03AE049-00002
A03AE050-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 33 | Hot-Dip Galvanized Steel | [8 empty] | 14 | Galv.: ASTM A123 | [13 empty] | TON | TON | A03AE050 | A03AE050-00001
A03AE050-00002 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS | [23 empty] | TON | TON | A03AE050 | A03AE050-00002
A03AE052-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 052 | Concrete Temperature Monitoring | [10 empty] | 16 | Including Themo Coupler, Monitoring & Record Acc. To Approved MS | [13 empty] | M3 | M3 | A03AE052 | A03AE052-00001
A03AE053-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 053 | Steel Casing for CEP | [10 empty] | 17 | Including Anchoring, Tar Epoxy Coating, Frame & Accessories, Weldings | [5 empty] | Steel Pipe: D( )mm x THK( )t x L( )m, Steel Plate: W( )mm x L( )mm x THK( )t | [7 empty] | M3 | M3 | A03AE053 | A03AE053-00001
A03AE054-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 054 | System Form | 36 | Heavy Duty Forms, Metal Framed Playwood forms | [8 empty] | 18 | Including Form Tie, All Accessories, Sealing of Form Tie Hole, Separator & Anchor Box out, Chamfer for Exposed Edge, Opening & Sleeve, Shoring, Scaffording, Safety Measures and Shop Drawing | [13 empty] | M3 | M3 | A03AE054 | A03AE054-00001
A03AE055-00001 | AR | A03 | Concrete Work | AE | Mass Concrete Work | 055 | System Support | [25 empty] | M3 | M3 | A03AE055 | A03AE055-00001
A03AF029-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 37 | M12 | [9 empty] | EA | EA | A03AF029 | A03AF029-00001
A03AF029-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 38 | M16 | [9 empty] | EA | EA | A03AF029 | A03AF029-00002
A03AF029-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 39 | M20 | [9 empty] | EA | EA | A03AF029 | A03AF029-00003
A03AF029-00004 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 40 | M22 | [9 empty] | EA | EA | A03AF029 | A03AF029-00004
A03AF029-00005 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 41 | M24 | [9 empty] | EA | EA | A03AF029 | A03AF029-00005
A03AF029-00006 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 42 | M30 | [9 empty] | EA | EA | A03AF029 | A03AF029-00006
A03AF029-00007 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 43 | M33 | [9 empty] | EA | EA | A03AF029 | A03AF029-00007
A03AF029-00008 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 44 | M36 | [9 empty] | EA | EA | A03AF029 | A03AF029-00008
A03AF029-00009 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 45 | M42 | [9 empty] | EA | EA | A03AF029 | A03AF029-00009
A03AF029-00010 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 46 | M48 | [9 empty] | EA | EA | A03AF029 | A03AF029-00010
A03AF029-00011 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 47 | M52 | [9 empty] | EA | EA | A03AF029 | A03AF029-00011
A03AF029-00012 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 48 | M56 | [9 empty] | EA | EA | A03AF029 | A03AF029-00012
A03AF029-00013 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 49 | M64 | [9 empty] | EA | EA | A03AF029 | A03AF029-00013
A03AF029-00014 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 50 | M72 | [9 empty] | EA | EA | A03AF029 | A03AF029-00014
A03AF029-00015 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 51 | M76 | [9 empty] | EA | EA | A03AF029 | A03AF029-00015
A03AF029-00016 | AR | A03 | Concrete Work | AF | Superstructure Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 52 | Over M76 | [9 empty] | EA | EA | A03AF029 | A03AF029-00016
A03AF030-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 36 | M10 | [9 empty] | EA | EA | A03AF030 | A03AF030-00001
A03AF030-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 37 | M12 | [9 empty] | EA | EA | A03AF030 | A03AF030-00002
A03AF030-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 38 | M16 | [9 empty] | EA | EA | A03AF030 | A03AF030-00003
A03AF030-00004 | AR | A03 | Concrete Work | AF | Superstructure Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 39 | M20 | [9 empty] | EA | EA | A03AF030 | A03AF030-00004
A03AF030-00005 | AR | A03 | Concrete Work | AF | Superstructure Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 40 | M22 | [9 empty] | EA | EA | A03AF030 | A03AF030-00005
A03AF030-00006 | AR | A03 | Concrete Work | AF | Superstructure Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 41 | M24 | [9 empty] | EA | EA | A03AF030 | A03AF030-00006
A03AF031-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 031 | Expansion Anchor Bolt | [14 empty] | 36 | M10 | [9 empty] | EA | EA | A03AF031 | A03AF031-00001
A03AF031-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 031 | Expansion Anchor Bolt | [14 empty] | 37 | M12 | [9 empty] | EA | EA | A03AF031 | A03AF031-00002
A03AF031-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 031 | Expansion Anchor Bolt | [14 empty] | 38 | M16 | [9 empty] | EA | EA | A03AF031 | A03AF031-00003
A03AF031-00004 | AR | A03 | Concrete Work | AF | Superstructure Work | 031 | Expansion Anchor Bolt | [14 empty] | 39 | M20 | [9 empty] | EA | EA | A03AF031 | A03AF031-00004
A03AF031-00005 | AR | A03 | Concrete Work | AF | Superstructure Work | 031 | Expansion Anchor Bolt | [14 empty] | 40 | M22 | [9 empty] | EA | EA | A03AF031 | A03AF031-00005
A03AF031-00006 | AR | A03 | Concrete Work | AF | Superstructure Work | 031 | Expansion Anchor Bolt | [14 empty] | 41 | M24 | [9 empty] | EA | EA | A03AF031 | A03AF031-00006
A03AF032-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 01 | F'c (Cylinder Strength) > 35MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00001
A03AF032-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 01 | F'c (Cylinder Strength) > 35MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00002
A03AF032-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 01 | F'c (Cylinder Strength) > 35MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00003
A03AF032-00004 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00004
A03AF032-00005 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00005
A03AF032-00006 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00006
A03AF032-00007 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00007
A03AF032-00008 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00008
A03AF032-00009 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00009
A03AF032-00010 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00010
A03AF032-00011 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00011
A03AF032-00012 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00012
A03AF032-00013 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 05 | F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00013
A03AF032-00014 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 05 | F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00014
A03AF032-00015 | AR | A03 | Concrete Work | AF | Superstructure Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 05 | F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AF032 | A03AF032-00015
A03AF035-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 035 | Form Work (3 times in use) | 25 | Flat Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AF035 | A03AF035-00001
A03AF035-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 035 | Form Work (3 times in use) | 26 | Circular Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AF035 | A03AF035-00002
A03AF036-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 036 | Form Work (1 time in use) | 25 | Flat Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AF036 | A03AF036-00001
A03AF036-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 036 | Form Work (1 time in use) | 26 | Circular Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AF036 | A03AF036-00002
A03AF037-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 09 | Fy>470MPa | [19 empty] | TON | TON | A03AF037 | A03AF037-00001
A03AF037-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 10 | 400MPa<Fy≤470MPa | [19 empty] | TON | TON | A03AF037 | A03AF037-00002
A03AF037-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 11 | 300MPa<Fy≤400MPa | [19 empty] | TON | TON | A03AF037 | A03AF037-00003
A03AF037-00004 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 12 | Fy≤300MPa | [19 empty] | TON | TON | A03AF037 | A03AF037-00004
A03AF037-00005 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 09 | Fy>470MPa | [19 empty] | TON | TON | A03AF037 | A03AF037-00005
A03AF037-00006 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 10 | 400MPa<Fy≤470MPa | [19 empty] | TON | TON | A03AF037 | A03AF037-00006
A03AF037-00007 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 11 | 300MPa<Fy≤400MPa | [19 empty] | TON | TON | A03AF037 | A03AF037-00007
A03AF037-00008 | AR | A03 | Concrete Work | AF | Superstructure Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 12 | Fy≤300MPa | [19 empty] | TON | TON | A03AF037 | A03AF037-00008
A03AF038-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 038 | Welded Wire Fabric | [14 empty] | 53 | DIA≤6mm |  | Mesh Size=DIA( )mm x ( )mm x ( )mm | [7 empty] | M2 | M2 | A03AF038 | A03AF038-00001
A03AF038-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 038 | Welded Wire Fabric | [14 empty] | 54 | DIA>6mm |  | Mesh Size=DIA( )mm x ( )mm x ( )mm | [7 empty] | M2 | M2 | A03AF038 | A03AF038-00002
A03AF039-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 039 | Expansion Joint (Exposed Type) | [10 empty] | 06 | w/ Flexible Joint Filler, Sealant, Dowel Bar w/ PVC Sleeve | [5 empty] | THK=( )mm | [7 empty] | M | M | A03AF039 | A03AF039-00001
A03AF040-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 040 | Expansion Joint (w/ Aluminum Cover) | [10 empty] | 07 | w/ Flexible Joint Filler, Sealant, Aluminum Flashing Cover w/ Fixing Accessories | [5 empty] | THK=( )mm | [7 empty] | M | M | A03AF040 | A03AF040-00001
A03AF041-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 041 | Expansion Joint (w/ Galvanized Steel Cover) | [10 empty] | 08 | w/ Flexible Joint Filler, Sealant, Galv. Steel Cover w/ Galv. Steel Angle, Fixing Accessories | [5 empty] | THK=( )mm | [7 empty] | M | M | A03AF041 | A03AF041-00001
A03AF042-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 042 | Expansion Joint (w/ Stainless Steel Cover) | [10 empty] | 09 | w/ Flexible Joint Filler, Sealant, SST Flashing Cover w/ Fixing Accessories | [5 empty] | THK=( )mm | [7 empty] | M | M | A03AF042 | A03AF042-00001
A03AF043-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 043 | Expansion Joint (w/ Ready-Made Cover) | [10 empty] | 10 | w/ Flexible Joint Filler, Sealant, Ready-Made Cover Profile w/ Fixing Accessories | [5 empty] | THK=( )mm | [7 empty] | M | M | A03AF043 | A03AF043-00001
A03AF044-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 044 | Isolation Joint (Separation Joint) | [10 empty] | 11 | w/ Flexible Joint Filler, Sealant | [5 empty] | THK=( )mm | [7 empty] | M | M | A03AF044 | A03AF044-00001
A03AF045-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 045 | Control Joint | [10 empty] | 12 | w/ Joint Sealant, Backstop | [5 empty] | Saw Cut: W( )mm x D( )mm | [7 empty] | M | M | A03AF045 | A03AF045-00001
A03AF045-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 045 | Control Joint | [10 empty] | 13 | w/ Joint Sealant, Backstop, Bottom Crack Inducer | [5 empty] | Saw Cut: W( )mm x D( )mm | [7 empty] | M | M | A03AF045 | A03AF045-00002
A03AF046-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 046 | Water Stop | 29 | PVC Type | [15 empty] | W=( )mm | [7 empty] | M | M | A03AF046 | A03AF046-00001
A03AF046-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 046 | Water Stop | 30 | Stainless Steel Type | [15 empty] | W=( )mm | [7 empty] | M | M | A03AF046 | A03AF046-00002
A03AF046-00003 | AR | A03 | Concrete Work | AF | Superstructure Work | 046 | Water Stop | 31 | Expandable Rubber Type | [15 empty] | W=( )mm | [7 empty] | M | M | A03AF046 | A03AF046-00003
A03AF049-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 33 | Hot-Dip Galvanized Steel | [8 empty] | 14 | Galv.: ASTM A123 | [13 empty] | TON | TON | A03AF049 | A03AF049-00001
A03AF049-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS | [23 empty] | TON | TON | A03AF049 | A03AF049-00002
A03AF050-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 33 | Hot-Dip Galvanized Steel | [8 empty] | 14 | Galv.: ASTM A123 | [13 empty] | TON | TON | A03AF050 | A03AF050-00001
A03AF050-00002 | AR | A03 | Concrete Work | AF | Superstructure Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS | [23 empty] | TON | TON | A03AF050 | A03AF050-00002
A03AF051-00001 | AR | A03 | Concrete Work | AF | Superstructure Work | 051 | Groove Joint | [17 empty] | Size=( )mm x ( )mm | [7 empty] | M | M | A03AF051 | A03AF051-00001
A03AG029-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 37 | M12 | [9 empty] | EA | EA | A03AG029 | A03AG029-00001
A03AG029-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 38 | M16 | [9 empty] | EA | EA | A03AG029 | A03AG029-00002
A03AG029-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 39 | M20 | [9 empty] | EA | EA | A03AG029 | A03AG029-00003
A03AG029-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 40 | M22 | [9 empty] | EA | EA | A03AG029 | A03AG029-00004
A03AG029-00005 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 41 | M24 | [9 empty] | EA | EA | A03AG029 | A03AG029-00005
A03AG029-00006 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 42 | M30 | [9 empty] | EA | EA | A03AG029 | A03AG029-00006
A03AG029-00007 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 43 | M33 | [9 empty] | EA | EA | A03AG029 | A03AG029-00007
A03AG029-00008 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 44 | M36 | [9 empty] | EA | EA | A03AG029 | A03AG029-00008
A03AG029-00009 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 45 | M42 | [9 empty] | EA | EA | A03AG029 | A03AG029-00009
A03AG029-00010 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 46 | M48 | [9 empty] | EA | EA | A03AG029 | A03AG029-00010
A03AG029-00011 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 47 | M52 | [9 empty] | EA | EA | A03AG029 | A03AG029-00011
A03AG029-00012 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 48 | M56 | [9 empty] | EA | EA | A03AG029 | A03AG029-00012
A03AG029-00013 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 49 | M64 | [9 empty] | EA | EA | A03AG029 | A03AG029-00013
A03AG029-00014 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 50 | M72 | [9 empty] | EA | EA | A03AG029 | A03AG029-00014
A03AG029-00015 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 51 | M76 | [9 empty] | EA | EA | A03AG029 | A03AG029-00015
A03AG029-00016 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 029 | Anchor Bolt (Installation only) | [14 empty] | 52 | Over M76 | [9 empty] | EA | EA | A03AG029 | A03AG029-00016
A03AG030-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 36 | M10 | [9 empty] | EA | EA | A03AG030 | A03AG030-00001
A03AG030-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 37 | M12 | [9 empty] | EA | EA | A03AG030 | A03AG030-00002
A03AG030-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 38 | M16 | [9 empty] | EA | EA | A03AG030 | A03AG030-00003
A03AG030-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 39 | M20 | [9 empty] | EA | EA | A03AG030 | A03AG030-00004
A03AG030-00005 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 40 | M22 | [9 empty] | EA | EA | A03AG030 | A03AG030-00005
A03AG030-00006 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 030 | Chemical Anchor Bolt | [10 empty] | 04 | Including injected Chemical material |  |  | 41 | M24 | [9 empty] | EA | EA | A03AG030 | A03AG030-00006
A03AG031-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 031 | Expansion Anchor Bolt | [14 empty] | 36 | M10 | [9 empty] | EA | EA | A03AG031 | A03AG031-00001
A03AG031-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 031 | Expansion Anchor Bolt | [14 empty] | 37 | M12 | [9 empty] | EA | EA | A03AG031 | A03AG031-00002
A03AG031-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 031 | Expansion Anchor Bolt | [14 empty] | 38 | M16 | [9 empty] | EA | EA | A03AG031 | A03AG031-00003
A03AG031-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 031 | Expansion Anchor Bolt | [14 empty] | 39 | M20 | [9 empty] | EA | EA | A03AG031 | A03AG031-00004
A03AG031-00005 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 031 | Expansion Anchor Bolt | [14 empty] | 40 | M22 | [9 empty] | EA | EA | A03AG031 | A03AG031-00005
A03AG031-00006 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 031 | Expansion Anchor Bolt | [14 empty] | 41 | M24 | [9 empty] | EA | EA | A03AG031 | A03AG031-00006
A03AG032-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 01 | F'c (Cylinder Strength) > 35MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00001
A03AG032-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 01 | F'c (Cylinder Strength) > 35MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00002
A03AG032-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 01 | F'c (Cylinder Strength) > 35MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00003
A03AG032-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00004
A03AG032-00005 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00005
A03AG032-00006 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 02 | 30MPa < F'c (Cylinder Strength) ≤ 35MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00006
A03AG032-00007 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00007
A03AG032-00008 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00008
A03AG032-00009 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00009
A03AG032-00010 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00010
A03AG032-00011 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00011
A03AG032-00012 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00012
A03AG032-00013 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 01 | Cement Type-1 | 05 | F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00013
A03AG032-00014 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 02 | Cement Type-2 | 05 | F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00014
A03AG032-00015 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 032 | Structural Concrete |  |  | 03 | Cement Type-5 | 05 | F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AG032 | A03AG032-00015
A03AG034-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  |  | 01 | Cement Type-1 | 06 | F'c (Cylinder Strength) > 20MPa | [19 empty] | M3 | M3 | A03AG034 | A03AG034-00001
A03AG034-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  |  | 02 | Cement Type-2 | 06 | F'c (Cylinder Strength) > 20MPa | [19 empty] | M3 | M3 | A03AG034 | A03AG034-00002
A03AG034-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  |  | 03 | Cement Type-5 | 06 | F'c (Cylinder Strength) > 20MPa | [19 empty] | M3 | M3 | A03AG034 | A03AG034-00003
A03AG034-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  |  | 01 | Cement Type-1 | 07 | 10MPa < F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AG034 | A03AG034-00004
A03AG034-00005 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  |  | 02 | Cement Type-2 | 07 | 10MPa < F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AG034 | A03AG034-00005
A03AG034-00006 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  |  | 03 | Cement Type-5 | 07 | 10MPa < F'c (Cylinder Strength) ≤ 20MPa | [19 empty] | M3 | M3 | A03AG034 | A03AG034-00006
A03AG034-00007 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  |  | 01 | Cement Type-1 | 08 | F'c (Cylinder Strength) ≤ 10MPa | [19 empty] | M3 | M3 | A03AG034 | A03AG034-00007
A03AG034-00008 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  |  | 02 | Cement Type-2 | 08 | F'c (Cylinder Strength) ≤ 10MPa | [19 empty] | M3 | M3 | A03AG034 | A03AG034-00008
A03AG034-00009 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 034 | Lean Concrete (including Form work) |  |  | 03 | Cement Type-5 | 08 | F'c (Cylinder Strength) ≤ 10MPa | [19 empty] | M3 | M3 | A03AG034 | A03AG034-00009
A03AG035-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 035 | Form Work (3 times in use) | 25 | Flat Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AG035 | A03AG035-00001
A03AG035-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 035 | Form Work (3 times in use) | 26 | Circular Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AG035 | A03AG035-00002
A03AG036-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 036 | Form Work (1 time in use) | 25 | Flat Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AG036 | A03AG036-00001
A03AG036-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 036 | Form Work (1 time in use) | 26 | Circular Form | [8 empty] | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [13 empty] | M2 | M2 | A03AG036 | A03AG036-00002
A03AG037-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 09 | Fy>470MPa | [19 empty] | TON | TON | A03AG037 | A03AG037-00001
A03AG037-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 10 | 400MPa<Fy≤470MPa | [19 empty] | TON | TON | A03AG037 | A03AG037-00002
A03AG037-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 11 | 300MPa<Fy≤400MPa | [19 empty] | TON | TON | A03AG037 | A03AG037-00003
A03AG037-00004 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) |  |  | 12 | Fy≤300MPa | [19 empty] | TON | TON | A03AG037 | A03AG037-00004
A03AG037-00005 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 09 | Fy>470MPa | [19 empty] | TON | TON | A03AG037 | A03AG037-00005
A03AG037-00006 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 10 | 400MPa<Fy≤470MPa | [19 empty] | TON | TON | A03AG037 | A03AG037-00006
A03AG037-00007 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 11 | 300MPa<Fy≤400MPa | [19 empty] | TON | TON | A03AG037 | A03AG037-00007
A03AG037-00008 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 037 | Rebar Work | 28 | Deformed Bar (Epoxy Coat.) |  |  | 12 | Fy≤300MPa | [19 empty] | TON | TON | A03AG037 | A03AG037-00008
A03AG046-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 046 | Water Stop | 29 | PVC Type | [15 empty] | W=( )mm | [7 empty] | M | M | A03AG046 | A03AG046-00001
A03AG046-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 046 | Water Stop | 30 | Stainless Steel Type | [15 empty] | W=( )mm | [7 empty] | M | M | A03AG046 | A03AG046-00002
A03AG046-00003 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 046 | Water Stop | 31 | Expandable Rubber Type | [15 empty] | W=( )mm | [7 empty] | M | M | A03AG046 | A03AG046-00003
A03AG049-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 33 | Hot-Dip Galvanized Steel | [8 empty] | 14 | Galv.: ASTM A123 | [13 empty] | TON | TON | A03AG049 | A03AG049-00001
A03AG049-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 34 | SUS | [23 empty] | TON | TON | A03AG049 | A03AG049-00002
A03AG050-00001 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 33 | Hot-Dip Galvanized Steel | [8 empty] | 14 | Galv.: ASTM A123 | [13 empty] | TON | TON | A03AG050 | A03AG050-00001
A03AG050-00002 | AR | A03 | Concrete Work | AG | Equipment Foundation Work | 050 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Installation Only) | 34 | SUS | [23 empty] | TON | TON | A03AG050 | A03AG050-00002
A03AH056-00001 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 056 | Bitumen/Bituminous/Asphalt Coating | [25 empty] | M2 | M2 | A03AH056 | A03AH056-00001
A03AH057-00001 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 057 | Coal Tar Epoxy | [25 empty] | M2 | M2 | A03AH057 | A03AH057-00001
A03AH058-00001 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 058 | Epoxy Coating (Epoxy Resin Based Coating) | [25 empty] | M2 | M2 | A03AH058 | A03AH058-00001
A03AH059-00001 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 059 | Sheet Membrane | 37 | Adhesive Rubber Sheet or Bitumen Polyethylene Laminated Waterproofing Membrane | [15 empty] | THK=( )mm | [7 empty] | M2 | M2 | A03AH059 | A03AH059-00001
A03AH060-00001 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 060 | Memebrane Protection Board | 38 | Bitumen Impregnated Fiberboard | [15 empty] | THK=( )mm | [7 empty] | M2 | M2 | A03AH060 | A03AH060-00001
A03AH060-00002 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 060 | Memebrane Protection Board | 39 | Bitumen Impregnated Softboard | [15 empty] | THK=( )mm | [7 empty] | M2 | M2 | A03AH060 | A03AH060-00002
A03AH061-00001 | AR | A03 | Concrete Work | AH | Concrete Protective Coating (U/G) | 061 | Protective Screed | [17 empty] | THK=( )mm | [7 empty] | M2 | M2 | A03AH061 | A03AH061-00001
A03AJ058-00001 | AR | A03 | Concrete Work | AJ | Concrete Protective Coating (A/G) | 058 | Epoxy Coating (Epoxy Resin Based Coating) | [25 empty] | M2 | M2 | A03AJ058 | A03AJ058-00001
A03AJ062-00001 | AR | A03 | Concrete Work | AJ | Concrete Protective Coating (A/G) | 062 | Acrylic Polymer Coating | [25 empty] | M2 | M2 | A03AJ062 | A03AJ062-00001
A03AJ063-00001 | AR | A03 | Concrete Work | AJ | Concrete Protective Coating (A/G) | 063 | Bituminous Damp Proofing | [8 empty] | 01 | for External Conc. Wall behind Panel (Granite, Marble, Aluminum Panel, ETC.) | [15 empty] | M2 | M2 | A03AJ063 | A03AJ063-00001
A03AK064-00001 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Roof Panel | 40 | Hollow Core Slab | [8 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 12 | 100mm<THK≤120mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK064 | A03AK064-00001
A03AK064-00002 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Roof Panel | 40 | Hollow Core Slab | [8 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 13 | 120mm<THK≤150mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK064 | A03AK064-00002
A03AK064-00003 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Roof Panel | 40 | Hollow Core Slab | [8 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 02 | 150mm<THK≤200mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK064 | A03AK064-00003
A03AK064-00004 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Roof Panel | 40 | Hollow Core Slab | [8 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 14 | 200mm<THK |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK064 | A03AK064-00004
A03AK064-00005 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Roof Panel | 41 | Single Tee Slab | [8 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 12 | 100mm<THK≤120mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK064 | A03AK064-00005
A03AK064-00006 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Roof Panel | 41 | Single Tee Slab | [8 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 13 | 120mm<THK≤150mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK064 | A03AK064-00006
A03AK064-00007 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Roof Panel | 41 | Single Tee Slab | [8 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 02 | 150mm<THK≤200mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK064 | A03AK064-00007
A03AK064-00008 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Roof Panel | 41 | Single Tee Slab | [8 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 14 | 200mm<THK |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK064 | A03AK064-00008
A03AK064-00009 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Roof Panel | 42 | Doube Tee Slab | [8 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 12 | 100mm<THK≤120mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK064 | A03AK064-00009
A03AK064-00010 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Roof Panel | 42 | Doube Tee Slab | [8 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 13 | 120mm<THK≤150mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK064 | A03AK064-00010
A03AK064-00011 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Roof Panel | 42 | Doube Tee Slab | [8 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 02 | 150mm<THK≤200mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK064 | A03AK064-00011
A03AK064-00012 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 064 | PC Roof Panel | 42 | Doube Tee Slab | [8 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 14 | 200mm<THK |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK064 | A03AK064-00012
A03AK065-00001 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 065 | PC Wall Panel | [10 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 02 | 150mm<THK≤200mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK065 | A03AK065-00001
A03AK065-00002 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 065 | PC Wall Panel | [10 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 03 | 200mm<THK≤250mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK065 | A03AK065-00002
A03AK065-00003 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 065 | PC Wall Panel | [10 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 04 | 250mm<THK≤300mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK065 | A03AK065-00003
A03AK065-00004 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 065 | PC Wall Panel | [10 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 05 | 300mm<THK≤350mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK065 | A03AK065-00004
A03AK065-00005 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 065 | PC Wall Panel | [10 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 15 | 350mm<THK≤400mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK065 | A03AK065-00005
A03AK065-00006 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 065 | PC Wall Panel | [10 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work |  |  | 16 | 400mm<THK≤450mm |  | THK=( )mm | [7 empty] | M3 | M3 | A03AK065 | A03AK065-00006
A03AK066-00001 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 066 | PC Column | [10 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work | [5 empty] | W( )mm x L( )mm | [7 empty] | M3 | M3 | A03AK066 | A03AK066-00001
A03AK067-00001 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 067 | PC Girder & Beam | [10 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work | [5 empty] | W( )mm x H( )mm | [7 empty] | M3 | M3 | A03AK067 | A03AK067-00001
A03AK068-00001 | AR | A03 | Concrete Work | AK | Precast Concrete Work | 068 | PC Cover | [10 empty] | 20 | Including Supply and Install Work w/ All Items to Complete the Work | [5 empty] | W( )mm x L( )mm x THK( )mm | [7 empty] | M3 | M3 | A03AK068 | A03AK068-00001
A04AL012-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 012 | PE Sheet (Vapor Barrier) | [17 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AL012 | A04AL012-00001
A04AL069-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 069 | Reinforced Concrete Block | [10 empty] | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 17 | 50mm<THK≤100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL069 | A04AL069-00001
A04AL069-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 069 | Reinforced Concrete Block | [10 empty] | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 18 | 100mm<THK≤200mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL069 | A04AL069-00002
A04AL069-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 069 | Reinforced Concrete Block | [10 empty] | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 14 | 200mm<THK |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL069 | A04AL069-00003
A04AL070-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 070 | AAC (Autoclaved Aerated Concrete) Block | [10 empty] | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 17 | 50mm<THK≤100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL070 | A04AL070-00001
A04AL070-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 070 | AAC (Autoclaved Aerated Concrete) Block | [10 empty] | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 18 | 100mm<THK≤200mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL070 | A04AL070-00002
A04AL070-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 070 | AAC (Autoclaved Aerated Concrete) Block | [10 empty] | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 14 | 200mm<THK |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL070 | A04AL070-00003
A04AL071-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 071 | Glass Block | [10 empty] | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 19 | 50mm<THK≤80mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL071 | A04AL071-00001
A04AL071-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 071 | Glass Block | [10 empty] | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 20 | 80mm<THK≤90mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL071 | A04AL071-00002
A04AL071-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 071 | Glass Block | [10 empty] | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 21 | 90mm<THK |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL071 | A04AL071-00003
A04AL072-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 072 | Clay Block | [10 empty] | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 17 | 50mm<THK≤100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL072 | A04AL072-00001
A04AL072-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 072 | Clay Block | [10 empty] | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 18 | 100mm<THK≤200mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL072 | A04AL072-00002
A04AL072-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 072 | Clay Block | [10 empty] | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 14 | 200mm<THK |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL072 | A04AL072-00003
A04AL073-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 073 | Concrete Brick | [10 empty] | 22 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 22 | THK≤90mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL073 | A04AL073-00001
A04AL073-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 073 | Concrete Brick | [10 empty] | 23 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 23 | 90mm<THK≤190mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL073 | A04AL073-00002
A04AL073-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 073 | Concrete Brick | [10 empty] | 24 | [1.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 24 | 190mm<THK≤290mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL073 | A04AL073-00003
A04AL073-00004 | AR | A04 | Finishing Work | AL | Masonry Work | 073 | Concrete Brick | [10 empty] | 25 | [2.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 25 | 290mm<THK |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL073 | A04AL073-00004
A04AL074-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 074 | Burnt Clay Brick | [10 empty] | 22 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 22 | THK≤90mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL074 | A04AL074-00001
A04AL074-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 074 | Burnt Clay Brick | [10 empty] | 23 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 23 | 90mm<THK≤190mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL074 | A04AL074-00002
A04AL074-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 074 | Burnt Clay Brick | [10 empty] | 24 | [1.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 24 | 190mm<THK≤290mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL074 | A04AL074-00003
A04AL074-00004 | AR | A04 | Finishing Work | AL | Masonry Work | 074 | Burnt Clay Brick | [10 empty] | 25 | [2.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. |  |  | 25 | 290mm<THK |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL074 | A04AL074-00004
A04AL075-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 075 | Insulated Brick | [10 empty] | 21 | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AL075 | A04AL075-00001
A04AL076-00001 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 43 | Mineral Wool (Rock Wool) | [8 empty] | 26 | Minimum Density of 50 kg/m3 |  |  | 31 | THK<50mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL076 | A04AL076-00001
A04AL076-00002 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 43 | Mineral Wool (Rock Wool) | [8 empty] | 26 | Minimum Density of 50 kg/m3 |  |  | 09 | 50mm≤THK<75mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL076 | A04AL076-00002
A04AL076-00003 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 43 | Mineral Wool (Rock Wool) | [8 empty] | 26 | Minimum Density of 50 kg/m3 |  |  | 10 | 75mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL076 | A04AL076-00003
A04AL076-00004 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 43 | Mineral Wool (Rock Wool) | [8 empty] | 26 | Minimum Density of 50 kg/m3 |  |  | 11 | 100mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL076 | A04AL076-00004
A04AL076-00005 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 44 | Glass Wool (Fiberglass) | [8 empty] | 26 | Minimum Density of 50 kg/m3 |  |  | 31 | THK<50mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL076 | A04AL076-00005
A04AL076-00006 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 44 | Glass Wool (Fiberglass) | [8 empty] | 26 | Minimum Density of 50 kg/m3 |  |  | 09 | 50mm≤THK<75mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL076 | A04AL076-00006
A04AL076-00007 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 44 | Glass Wool (Fiberglass) | [8 empty] | 26 | Minimum Density of 50 kg/m3 |  |  | 10 | 75mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL076 | A04AL076-00007
A04AL076-00008 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 44 | Glass Wool (Fiberglass) | [8 empty] | 26 | Minimum Density of 50 kg/m3 |  |  | 11 | 100mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL076 | A04AL076-00008
A04AL076-00009 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 64 | Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) | [8 empty] | 57 | Minimum Density of 25 kg/m3 |  |  | 31 | THK<50mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL076 | A04AL076-00009
A04AL076-00010 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 64 | Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) | [8 empty] | 57 | Minimum Density of 25 kg/m3 |  |  | 09 | 50mm≤THK<75mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL076 | A04AL076-00010
A04AL076-00011 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 64 | Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) | [8 empty] | 57 | Minimum Density of 25 kg/m3 |  |  | 10 | 75mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL076 | A04AL076-00011
A04AL076-00012 | AR | A04 | Finishing Work | AL | Masonry Work | 076 | Insulation | 64 | Polystyrene (Extruded Polystyrene(XPS) or Expanded Polystyrene(EPS)) | [8 empty] | 57 | Minimum Density of 25 kg/m3 |  |  | 11 | 100mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A04AL076 | A04AL076-00012
A04AM077-00001 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 45 | Acrylic Emulsion Paint | [23 empty] | M2 | M2 | A04AM077 | A04AM077-00001
A04AM077-00002 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 46 | Acrylic Emulsion Paint (Textured Type) | [23 empty] | M2 | M2 | A04AM077 | A04AM077-00002
A04AM077-00003 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 47 | Water Emulsion Paint | [23 empty] | M2 | M2 | A04AM077 | A04AM077-00003
A04AM077-00004 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 48 | Latex Paint | [23 empty] | M2 | M2 | A04AM077 | A04AM077-00004
A04AM077-00005 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 49 | Latex Paint (Textured Type) | [23 empty] | M2 | M2 | A04AM077 | A04AM077-00005
A04AM077-00006 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 50 | Epoxy Paint | [23 empty] | M2 | M2 | A04AM077 | A04AM077-00006
A04AM077-00007 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 51 | Stucco Finish | [23 empty] | M2 | M2 | A04AM077 | A04AM077-00007
A04AM077-00008 | AR | A04 | Finishing Work | AM | Painting Work | 077 | External Wall Painting | 74 | Chemical Resistant Paint | [23 empty] | M2 | M2 | A04AM077 | A04AM077-00008
A04AM078-00001 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 45 | Acrylic Emulsion Paint | [23 empty] | M2 | M2 | A04AM078 | A04AM078-00001
A04AM078-00002 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 47 | Water Emulsion Paint | [23 empty] | M2 | M2 | A04AM078 | A04AM078-00002
A04AM078-00003 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 48 | Latex Paint | [23 empty] | M2 | M2 | A04AM078 | A04AM078-00003
A04AM078-00004 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 52 | Acid/Alkaline Resistant Paint | [23 empty] | M2 | M2 | A04AM078 | A04AM078-00004
A04AM078-00005 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 50 | Epoxy Paint | [23 empty] | M2 | M2 | A04AM078 | A04AM078-00005
A04AM078-00006 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 51 | Stucco Finish | [23 empty] | M2 | M2 | A04AM078 | A04AM078-00006
A04AM078-00007 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 53 | Anti-Dust Paint | [23 empty] | M2 | M2 | A04AM078 | A04AM078-00007
A04AM078-00008 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 54 | Epoxy Based Sealer | [23 empty] | M2 | M2 | A04AM078 | A04AM078-00008
A04AM078-00009 | AR | A04 | Finishing Work | AM | Painting Work | 078 | Internal Wall Painting | 74 | Chemical Resistant Paint | [23 empty] | M2 | M2 | A04AM078 | A04AM078-00009
A04AM079-00001 | AR | A04 | Finishing Work | AM | Painting Work | 079 | Ceiling Painting | 45 | Acrylic Emulsion Paint | [23 empty] | M2 | M2 | A04AM079 | A04AM079-00001
A04AM079-00002 | AR | A04 | Finishing Work | AM | Painting Work | 079 | Ceiling Painting | 47 | Water Emulsion Paint | [23 empty] | M2 | M2 | A04AM079 | A04AM079-00002
A04AM079-00003 | AR | A04 | Finishing Work | AM | Painting Work | 079 | Ceiling Painting | 48 | Latex Paint | [23 empty] | M2 | M2 | A04AM079 | A04AM079-00003
A04AM079-00004 | AR | A04 | Finishing Work | AM | Painting Work | 079 | Ceiling Painting | 52 | Acid/Alkaline Resistant Paint | [23 empty] | M2 | M2 | A04AM079 | A04AM079-00004
A04AM079-00005 | AR | A04 | Finishing Work | AM | Painting Work | 079 | Ceiling Painting | 53 | Anti-Dust Paint | [23 empty] | M2 | M2 | A04AM079 | A04AM079-00005
A04AM079-00006 | AR | A04 | Finishing Work | AM | Painting Work | 079 | Ceiling Painting | 50 | Epoxy Paint | [23 empty] | M2 | M2 | A04AM079 | A04AM079-00006
A04AM080-00001 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 45 | Acrylic Emulsion Paint | [23 empty] | M2 | M2 | A04AM080 | A04AM080-00001
A04AM080-00002 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 47 | Water Emulsion Paint | [23 empty] | M2 | M2 | A04AM080 | A04AM080-00002
A04AM080-00003 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 52 | Acid/Alkaline Resistant Paint | [23 empty] | M2 | M2 | A04AM080 | A04AM080-00003
A04AM080-00004 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 55 | Oil Based Paint | [23 empty] | M2 | M2 | A04AM080 | A04AM080-00004
A04AM080-00005 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 53 | Anti-Dust Paint | [23 empty] | M2 | M2 | A04AM080 | A04AM080-00005
A04AM080-00006 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 50 | Epoxy Paint | [23 empty] | M2 | M2 | A04AM080 | A04AM080-00006
A04AM080-00007 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 54 | Epoxy Based Sealer | [23 empty] | M2 | M2 | A04AM080 | A04AM080-00007
A04AM080-00008 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 56 | Epoxy Lining | [23 empty] | M2 | M2 | A04AM080 | A04AM080-00008
A04AM080-00009 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 57 | Road Marker Paint | [23 empty] | M2 | M2 | A04AM080 | A04AM080-00009
A04AM080-00010 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 58 | White Strips for Parking Place | [15 empty] | W=( )mm | [7 empty] | M2 | M | A04AM080 | A04AM080-00010
A04AM080-00011 | AR | A04 | Finishing Work | AM | Painting Work | 080 | Floor Painting | 74 | Chemical Resistant Paint | [23 empty] | M2 | M2 | A04AM080 | A04AM080-00011
A04AM081-00001 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 45 | Acrylic Emulsion Paint | [12 empty] | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AM081 | A04AM081-00001
A04AM081-00002 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 45 | Acrylic Emulsion Paint | [12 empty] | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AM081 | A04AM081-00002
A04AM081-00003 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 45 | Acrylic Emulsion Paint | [12 empty] | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AM081 | A04AM081-00003
A04AM081-00004 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 52 | Acid/Alkaline Resistant Paint | [12 empty] | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AM081 | A04AM081-00004
A04AM081-00005 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 52 | Acid/Alkaline Resistant Paint | [12 empty] | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AM081 | A04AM081-00005
A04AM081-00006 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 52 | Acid/Alkaline Resistant Paint | [12 empty] | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AM081 | A04AM081-00006
A04AM081-00007 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 50 | Epoxy Paint | [12 empty] | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AM081 | A04AM081-00007
A04AM081-00008 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 50 | Epoxy Paint | [12 empty] | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AM081 | A04AM081-00008
A04AM081-00009 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 50 | Epoxy Paint | [12 empty] | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AM081 | A04AM081-00009
A04AM081-00010 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 74 | Chemical Resistant Paint | [12 empty] | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AM081 | A04AM081-00010
A04AM081-00011 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 74 | Chemical Resistant Paint | [12 empty] | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AM081 | A04AM081-00011
A04AM081-00012 | AR | A04 | Finishing Work | AM | Painting Work | 081 | Skirt Painting | 74 | Chemical Resistant Paint | [12 empty] | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AM081 | A04AM081-00012
A04AN082-00001 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 59 | Unglazed Ceramic Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN082 | A04AN082-00001
A04AN082-00002 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 60 | Glazed Ceramic Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN082 | A04AN082-00002
A04AN082-00003 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 61 | Acid/Alkaline Resistant Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN082 | A04AN082-00003
A04AN082-00004 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 62 | Granite Tile | [8 empty] | 28 | w/ Wet Method (Mortar Bond Coat or Adhesive) or Dry Method (Steel or SST Frame, Angle, Bolt, etc.) | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN082 | A04AN082-00004
A04AN082-00005 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 63 | Marble Tile | [8 empty] | 28 | w/ Wet Method (Mortar Bond Coat or Adhesive) or Dry Method (Steel or SST Frame, Angle, Bolt, etc.) | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN082 | A04AN082-00005
A04AN082-00006 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 72 | Stone Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN082 | A04AN082-00006
A04AN082-00007 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 65 | Mosaic Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN082 | A04AN082-00007
A04AN082-00008 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 66 | Acoustic Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN082 | A04AN082-00008
A04AN082-00009 | AR | A04 | Finishing Work | AN | Tile Work | 082 | Wall Tile | 67 | Porcelain Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN082 | A04AN082-00009
A04AN083-00001 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 68 | Ceramic Tile | [8 empty] | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN083 | A04AN083-00001
A04AN083-00002 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 61 | Acid/Alkaline Resistant Tile | [8 empty] | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN083 | A04AN083-00002
A04AN083-00003 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 69 | Terrazzo Tile | [8 empty] | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN083 | A04AN083-00003
A04AN083-00004 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 70 | Vinyl Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN083 | A04AN083-00004
A04AN083-00005 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 71 | Anti-Static Vinyl Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN083 | A04AN083-00005
A04AN083-00006 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 62 | Granite Tile | [8 empty] | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN083 | A04AN083-00006
A04AN083-00007 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 63 | Marble Tile | [8 empty] | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN083 | A04AN083-00007
A04AN083-00008 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 72 | Stone Tile | [8 empty] | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN083 | A04AN083-00008
A04AN083-00009 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 73 | Concrete Tile | [8 empty] | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN083 | A04AN083-00009
A04AN083-00010 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 65 | Mosaic Tile | [8 empty] | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN083 | A04AN083-00010
A04AN083-00011 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | 67 | Porcelain Tile | [8 empty] | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN083 | A04AN083-00011
A04AN083-00012 | AR | A04 | Finishing Work | AN | Tile Work | 083 | Floor Tile | FD | Rubber Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [5 empty] | Tile Size=W( )mm x L( )mm x THK( )mm | [7 empty] | M2 | M2 | A04AN083 | A04AN083-00012
A04AN084-00001 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 59 | Unglazed Ceramic Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00001
A04AN084-00002 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 59 | Unglazed Ceramic Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00002
A04AN084-00003 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 59 | Unglazed Ceramic Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00003
A04AN084-00004 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 60 | Glazed Ceramic Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00004
A04AN084-00005 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 60 | Glazed Ceramic Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00005
A04AN084-00006 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 60 | Glazed Ceramic Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00006
A04AN084-00007 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 61 | Acid/Alkaline Resistant Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00007
A04AN084-00008 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 61 | Acid/Alkaline Resistant Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00008
A04AN084-00009 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 61 | Acid/Alkaline Resistant Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00009
A04AN084-00010 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 69 | Terrazzo Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00010
A04AN084-00011 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 69 | Terrazzo Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00011
A04AN084-00012 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 69 | Terrazzo Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00012
A04AN084-00013 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 70 | Vinyl Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00013
A04AN084-00014 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 70 | Vinyl Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00014
A04AN084-00015 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 70 | Vinyl Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00015
A04AN084-00016 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 71 | Anti-Static Vinyl Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00016
A04AN084-00017 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 71 | Anti-Static Vinyl Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00017
A04AN084-00018 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 71 | Anti-Static Vinyl Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00018
A04AN084-00019 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 62 | Granite Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00019
A04AN084-00020 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 62 | Granite Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00020
A04AN084-00021 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 62 | Granite Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00021
A04AN084-00022 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 63 | Marble Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00022
A04AN084-00023 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 63 | Marble Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00023
A04AN084-00024 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 63 | Marble Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00024
A04AN084-00025 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 72 | Stone Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00025
A04AN084-00026 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 72 | Stone Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00026
A04AN084-00027 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 72 | Stone Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00027
A04AN084-00028 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 73 | Concrete Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00028
A04AN084-00029 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 73 | Concrete Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00029
A04AN084-00030 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 73 | Concrete Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00030
A04AN084-00031 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 67 | Porcelain Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00031
A04AN084-00032 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 67 | Porcelain Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00032
A04AN084-00033 | AR | A04 | Finishing Work | AN | Tile Work | 084 | Skirt Tile | 67 | Porcelain Tile | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AN084 | A04AN084-00033
A04AP085-00001 | AR | A04 | Finishing Work | AP | Waterproofing Work | 085 | Liquid Waterproofing | [8 empty] | 02 | for Internal Floor Area | 30 | Min. 2 Coats | [13 empty] | M2 | M2 | A04AP085 | A04AP085-00001
A04AP085-00002 | AR | A04 | Finishing Work | AP | Waterproofing Work | 085 | Liquid Waterproofing | [8 empty] | 03 | for Internal Wall Area | 30 | Min. 2 Coats | [13 empty] | M2 | M2 | A04AP085 | A04AP085-00002
A04AP310-00001 | AR | A04 | Finishing Work | AP | Waterproofing Work | 310 | Waterproofing Membrane | [8 empty] | 04 | for Internal Area | [7 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AP310 | A04AP310-00001
A04AQ012-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 012 | PE Sheet (Vapor Barrier) | [17 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AQ012 | A04AQ012-00001
A04AQ038-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 038 | Welded Wire Fabric | [14 empty] | 53 | DIA≤6mm |  | Mesh Size=DIA( )mm x ( )mm x ( )mm | [7 empty] | M2 | M2 | A04AQ038 | A04AQ038-00001
A04AQ038-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 038 | Welded Wire Fabric | [14 empty] | 54 | DIA>6mm |  | Mesh Size=DIA( )mm x ( )mm x ( )mm | [7 empty] | M2 | M2 | A04AQ038 | A04AQ038-00002
A04AQ086-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 086 | Roof Screed | 75 | Light-Weight Concrete Screed | [8 empty] | 31 | w/o Welded Wire Fabric |  |  | 83 | 30mm≤Min. THK<50mm |  | Min. THK=( )mm, Slope=( ) | [7 empty] | M3 | M3 | A04AQ086 | A04AQ086-00001
A04AQ086-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 086 | Roof Screed | 75 | Light-Weight Concrete Screed | [8 empty] | 31 | w/o Welded Wire Fabric |  |  | 84 | 50mm≤Min. THK<75mm |  | Min. THK=( )mm, Slope=( ) | [7 empty] | M3 | M3 | A04AQ086 | A04AQ086-00002
A04AQ086-00003 | AR | A04 | Finishing Work | AQ | Roof Work | 086 | Roof Screed | 75 | Light-Weight Concrete Screed | [8 empty] | 31 | w/o Welded Wire Fabric |  |  | 85 | 75mm≤Min. THK |  | Min. THK=( )mm, Slope=( ) | [7 empty] | M3 | M3 | A04AQ086 | A04AQ086-00003
A04AQ086-00004 | AR | A04 | Finishing Work | AQ | Roof Work | 086 | Roof Screed | 76 | Bed Mortar Screed | [8 empty] | 31 | w/o Welded Wire Fabric |  |  | 83 | 30mm≤Min. THK<50mm |  | Min. THK=( )mm, Slope=( ) | [7 empty] | M3 | M3 | A04AQ086 | A04AQ086-00004
A04AQ086-00005 | AR | A04 | Finishing Work | AQ | Roof Work | 086 | Roof Screed | 76 | Bed Mortar Screed | [8 empty] | 31 | w/o Welded Wire Fabric |  |  | 84 | 50mm≤Min. THK<75mm |  | Min. THK=( )mm, Slope=( ) | [7 empty] | M3 | M3 | A04AQ086 | A04AQ086-00005
A04AQ086-00006 | AR | A04 | Finishing Work | AQ | Roof Work | 086 | Roof Screed | 76 | Bed Mortar Screed | [8 empty] | 31 | w/o Welded Wire Fabric |  |  | 85 | 75mm≤Min. THK |  | Min. THK=( )mm, Slope=( ) | [7 empty] | M3 | M3 | A04AQ086 | A04AQ086-00006
A04AQ087-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 087 | Waterproofing Coating | 79 | Hot Bitumen | [6 empty] | 05 | only for Roof Area | [15 empty] | M2 | M2 | A04AQ087 | A04AQ087-00001
A04AQ087-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 087 | Waterproofing Coating | 80 | Acrylic Polymer Protective Coating | [6 empty] | 05 | only for Roof Area | [15 empty] | M2 | M2 | A04AQ087 | A04AQ087-00002
A04AQ088-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 088 | Roof Insulation | 81 | Rigid Extruded Polystyrene Foam Insulation | [12 empty] | 31 | THK<50mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AQ088 | A04AQ088-00001
A04AQ088-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 088 | Roof Insulation | 81 | Rigid Extruded Polystyrene Foam Insulation | [12 empty] | 09 | 50mm≤THK<75mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AQ088 | A04AQ088-00002
A04AQ088-00003 | AR | A04 | Finishing Work | AQ | Roof Work | 088 | Roof Insulation | 81 | Rigid Extruded Polystyrene Foam Insulation | [12 empty] | 10 | 75mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AQ088 | A04AQ088-00003
A04AQ088-00004 | AR | A04 | Finishing Work | AQ | Roof Work | 088 | Roof Insulation | 81 | Rigid Extruded Polystyrene Foam Insulation | [12 empty] | 11 | 100mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A04AQ088 | A04AQ088-00004
A04AQ089-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 089 | Protective Concrete w/ Steel Trowel Finish | [25 empty] | M3 | M3 | A04AQ089 | A04AQ089-00001
A04AQ090-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 090 | Concrete Tile | [10 empty] | 33 | w/ Plastic Spacer |  |  | 28 | THK≤50mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AQ090 | A04AQ090-00001
A04AQ090-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 090 | Concrete Tile | [10 empty] | 33 | w/ Plastic Spacer |  |  | 29 | 50mm<THK≤75mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AQ090 | A04AQ090-00002
A04AQ090-00003 | AR | A04 | Finishing Work | AQ | Roof Work | 090 | Concrete Tile | [10 empty] | 33 | w/ Plastic Spacer |  |  | 30 | 75mm<THK≤100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AQ090 | A04AQ090-00003
A04AQ091-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 091 | Gravel for Roof | [17 empty] | THK=( )mmDIA=( )mm~( )mm or Max DIA=( )mm | [7 empty] | M2 | M2 | A04AQ091 | A04AQ091-00001
A04AQ092-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 092 | Crushed Stone for Roof | [17 empty] | THK=( )mmDIA=( )mm~( )mm or Max DIA=( )mm | [7 empty] | M2 | M2 | A04AQ092 | A04AQ092-00001
A04AQ093-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 093 | Clean Sand | [17 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AQ093 | A04AQ093-00001
A04AQ094-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 094 | Substrate Board | 82 | Water-Resistant Gypsum Substrate | [8 empty] | 34 | w/ Fixing Accessories | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AQ094 | A04AQ094-00001
A04AQ095-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 095 | Geotextile | [10 empty] | 34 | w/ Fixing Accessories | [13 empty] | M2 | M2 | A04AQ095 | A04AQ095-00001
A04AQ096-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 096 | Metal Coping for Parapet | 83 | Galvanized Steel Coping | [8 empty] | 35 | w/ Fixing Accessories, Sealant | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AQ096 | A04AQ096-00001
A04AQ096-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 096 | Metal Coping for Parapet | 84 | Aluminum Coping | [8 empty] | 35 | w/ Fixing Accessories, Sealant | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AQ096 | A04AQ096-00002
A04AQ096-00003 | AR | A04 | Finishing Work | AQ | Roof Work | 096 | Metal Coping for Parapet | 85 | Stainless Steel Coping | [8 empty] | 35 | w/ Fixing Accessories, Sealant | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AQ096 | A04AQ096-00003
A04AQ097-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 097 | Flashing along Roof Corner | 86 | Galvanized Steel Flashing | [8 empty] | 35 | w/ Fixing Accessories, Sealant | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AQ097 | A04AQ097-00001
A04AQ097-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 097 | Flashing along Roof Corner | 87 | Aluminum Flashing | [8 empty] | 35 | w/ Fixing Accessories, Sealant | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AQ097 | A04AQ097-00002
A04AQ097-00003 | AR | A04 | Finishing Work | AQ | Roof Work | 097 | Flashing along Roof Corner | 88 | Stainless Steel Flashing | [8 empty] | 35 | w/ Fixing Accessories, Sealant | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AQ097 | A04AQ097-00003
A04AQ310-00001 | AR | A04 | Finishing Work | AQ | Roof Work | 310 | Waterproofing Membrane | 77 | EPDM(or Equivalent) | [8 empty] | 32 | w/ Accessories | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AQ310 | A04AQ310-00001
A04AQ310-00002 | AR | A04 | Finishing Work | AQ | Roof Work | 310 | Waterproofing Membrane | 78 | EPDM(or Equivalent) with Solar Shield | [8 empty] | 32 | w/ Accessories | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AQ310 | A04AQ310-00002
A04AR098-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 098 | Steel Door w/ Steel Frame (UoM: M2) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR098 | A04AR098-00001
A04AR098-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 098 | Steel Door w/ Steel Frame (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR098 | A04AR098-00002
A04AR098-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 098 | Steel Door w/ Steel Frame (UoM: M2) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR098 | A04AR098-00003
A04AR098-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 098 | Steel Door w/ Steel Frame (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR098 | A04AR098-00004
A04AR098-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 098 | Steel Door w/ Steel Frame (UoM: M2) | AF | Fire Protective Rating: 2-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR098 | A04AR098-00005
A04AR099-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR099 | A04AR099-00001
A04AR099-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR099 | A04AR099-00002
A04AR099-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR099 | A04AR099-00003
A04AR099-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR099 | A04AR099-00004
A04AR099-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR099 | A04AR099-00005
A04AR099-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR099 | A04AR099-00006
A04AR099-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR099 | A04AR099-00007
A04AR099-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR099 | A04AR099-00008
A04AR099-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR099 | A04AR099-00009
A04AR099-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 099 | Steel Door w/ Steel Frame (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR099 | A04AR099-00010
A04AR100-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 100 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR100 | A04AR100-00001
A04AR100-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 100 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR100 | A04AR100-00002
A04AR100-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 100 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR100 | A04AR100-00003
A04AR100-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 100 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR100 | A04AR100-00004
A04AR100-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 100 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: M2) | AF | Fire Protective Rating: 2-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR100 | A04AR100-00005
A04AR101-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR101 | A04AR101-00001
A04AR101-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR101 | A04AR101-00002
A04AR101-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR101 | A04AR101-00003
A04AR101-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR101 | A04AR101-00004
A04AR101-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR101 | A04AR101-00005
A04AR101-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR101 | A04AR101-00006
A04AR101-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR101 | A04AR101-00007
A04AR101-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR101 | A04AR101-00008
A04AR101-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR101 | A04AR101-00009
A04AR101-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 101 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR101 | A04AR101-00010
A04AR102-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 102 | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR102 | A04AR102-00001
A04AR102-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 102 | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR102 | A04AR102-00002
A04AR102-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 102 | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR102 | A04AR102-00003
A04AR102-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 102 | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR102 | A04AR102-00004
A04AR102-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 102 | Steel Door w/ Steel Frame & Panic Bar (UoM: M2) | AF | Fire Protective Rating: 2-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR102 | A04AR102-00005
A04AR103-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR103 | A04AR103-00001
A04AR103-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR103 | A04AR103-00002
A04AR103-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR103 | A04AR103-00003
A04AR103-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR103 | A04AR103-00004
A04AR103-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR103 | A04AR103-00005
A04AR103-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR103 | A04AR103-00006
A04AR103-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR103 | A04AR103-00007
A04AR103-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR103 | A04AR103-00008
A04AR103-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR103 | A04AR103-00009
A04AR103-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 103 | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR103 | A04AR103-00010
A04AR104-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 104 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR104 | A04AR104-00001
A04AR104-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 104 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR104 | A04AR104-00002
A04AR104-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 104 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR104 | A04AR104-00003
A04AR104-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 104 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR104 | A04AR104-00004
A04AR104-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 104 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: M2) | AF | Fire Protective Rating: 2-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR104 | A04AR104-00005
A04AR105-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR105 | A04AR105-00001
A04AR105-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR105 | A04AR105-00002
A04AR105-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR105 | A04AR105-00003
A04AR105-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR105 | A04AR105-00004
A04AR105-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR105 | A04AR105-00005
A04AR105-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR105 | A04AR105-00006
A04AR105-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR105 | A04AR105-00007
A04AR105-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR105 | A04AR105-00008
A04AR105-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR105 | A04AR105-00009
A04AR105-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 105 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR105 | A04AR105-00010
A04AR106-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 106 | Blast Resistant Door w/ Steel Frame (UoM: M2) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR106 | A04AR106-00001
A04AR106-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 106 | Blast Resistant Door w/ Steel Frame (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR106 | A04AR106-00002
A04AR106-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 106 | Blast Resistant Door w/ Steel Frame (UoM: M2) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR106 | A04AR106-00003
A04AR106-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 106 | Blast Resistant Door w/ Steel Frame (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR106 | A04AR106-00004
A04AR106-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 106 | Blast Resistant Door w/ Steel Frame (UoM: M2) | AF | Fire Protective Rating: 2-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR106 | A04AR106-00005
A04AR107-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR107 | A04AR107-00001
A04AR107-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR107 | A04AR107-00002
A04AR107-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR107 | A04AR107-00003
A04AR107-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR107 | A04AR107-00004
A04AR107-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR107 | A04AR107-00005
A04AR107-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR107 | A04AR107-00006
A04AR107-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR107 | A04AR107-00007
A04AR107-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR107 | A04AR107-00008
A04AR107-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR107 | A04AR107-00009
A04AR107-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 107 | Blast Resistant Door w/ Steel Frame (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR107 | A04AR107-00010
A04AR108-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 108 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR108 | A04AR108-00001
A04AR108-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 108 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR108 | A04AR108-00002
A04AR108-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 108 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR108 | A04AR108-00003
A04AR108-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 108 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR108 | A04AR108-00004
A04AR108-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 108 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: M2) | AF | Fire Protective Rating: 2-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR108 | A04AR108-00005
A04AR109-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR109 | A04AR109-00001
A04AR109-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR109 | A04AR109-00002
A04AR109-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR109 | A04AR109-00003
A04AR109-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR109 | A04AR109-00004
A04AR109-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR109 | A04AR109-00005
A04AR109-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR109 | A04AR109-00006
A04AR109-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR109 | A04AR109-00007
A04AR109-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR109 | A04AR109-00008
A04AR109-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AG | Fire Protective Rating: 2-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR109 | A04AR109-00009
A04AR109-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 109 | Blast Resistant Door w/ Steel Frame, Panic Bar (UoM: EA) | AH | Fire Protective Rating: 2-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR109 | A04AR109-00010
A04AR110-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 110 | Aluminum Door w/ Aluminum Frame (UoM: M2) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR110 | A04AR110-00001
A04AR110-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 110 | Aluminum Door w/ Aluminum Frame (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR110 | A04AR110-00002
A04AR110-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 110 | Aluminum Door w/ Aluminum Frame (UoM: M2) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR110 | A04AR110-00003
A04AR110-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 110 | Aluminum Door w/ Aluminum Frame (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR110 | A04AR110-00004
A04AR111-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR111 | A04AR111-00001
A04AR111-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR111 | A04AR111-00002
A04AR111-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR111 | A04AR111-00003
A04AR111-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR111 | A04AR111-00004
A04AR111-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR111 | A04AR111-00005
A04AR111-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR111 | A04AR111-00006
A04AR111-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR111 | A04AR111-00007
A04AR111-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 111 | Aluminum Door w/ Aluminum Frame (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR111 | A04AR111-00008
A04AR112-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 112 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR112 | A04AR112-00001
A04AR112-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 112 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR112 | A04AR112-00002
A04AR112-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 112 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR112 | A04AR112-00003
A04AR112-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 112 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR112 | A04AR112-00004
A04AR113-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR113 | A04AR113-00001
A04AR113-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR113 | A04AR113-00002
A04AR113-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR113 | A04AR113-00003
A04AR113-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR113 | A04AR113-00004
A04AR113-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR113 | A04AR113-00005
A04AR113-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR113 | A04AR113-00006
A04AR113-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR113 | A04AR113-00007
A04AR113-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 113 | Aluminum Door w/ Aluminum Frame & Vision Panel for Each Leaf (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR113 | A04AR113-00008
A04AR114-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 114 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR114 | A04AR114-00001
A04AR114-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 114 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR114 | A04AR114-00002
A04AR114-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 114 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR114 | A04AR114-00003
A04AR114-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 114 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR114 | A04AR114-00004
A04AR115-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR115 | A04AR115-00001
A04AR115-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR115 | A04AR115-00002
A04AR115-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR115 | A04AR115-00003
A04AR115-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR115 | A04AR115-00004
A04AR115-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR115 | A04AR115-00005
A04AR115-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR115 | A04AR115-00006
A04AR115-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR115 | A04AR115-00007
A04AR115-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 115 | Aluminum Door w/ Aluminum Frame & Panic Bar (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR115 | A04AR115-00008
A04AR116-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 116 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR116 | A04AR116-00001
A04AR116-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 116 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR116 | A04AR116-00002
A04AR116-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 116 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR116 | A04AR116-00003
A04AR116-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 116 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leafr (UoM: M2) | AC | Fire Protective Rating: 1.5-hrs | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR116 | A04AR116-00004
A04AR117-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 90 | Fire Protective Rating: N/A, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR117 | A04AR117-00001
A04AR117-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 91 | Fire Protective Rating: N/A, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR117 | A04AR117-00002
A04AR117-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 93 | Fire Protective Rating: 0.5-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR117 | A04AR117-00003
A04AR117-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | 94 | Fire Protective Rating: 0.5-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR117 | A04AR117-00004
A04AR117-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AA | Fire Protective Rating: 1-hr, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR117 | A04AR117-00005
A04AR117-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AB | Fire Protective Rating: 1-hr, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR117 | A04AR117-00006
A04AR117-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AD | Fire Protective Rating: 1.5-hrs, Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR117 | A04AR117-00007
A04AR117-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 117 | Aluminum Door w/ Aluminum Frame, Panic Bar & Vision Panel for Each Leaf (UoM: EA) | AE | Fire Protective Rating: 1.5-hrs, Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR117 | A04AR117-00008
A04AR118-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 118 | Glass Door w/ SST Frame (UoM: M2) | [10 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR118 | A04AR118-00001
A04AR119-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 119 | Glass Door w/ SST Frame (UoM: EA) | AJ | Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR119 | A04AR119-00001
A04AR119-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 119 | Glass Door w/ SST Frame (UoM: EA) | AK | Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR119 | A04AR119-00002
A04AR120-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 120 | Stainless Steel Door w/ SST Frame (UoM: M2) | [10 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR120 | A04AR120-00001
A04AR121-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 121 | Stainless Steel Door w/ SST Frame (UoM: EA) | AJ | Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR121 | A04AR121-00001
A04AR121-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 121 | Stainless Steel Door w/ SST Frame (UoM: EA) | AK | Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR121 | A04AR121-00002
A04AR122-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 122 | Wood Door w/ Wood Frame (UoM: M2) | [10 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR122 | A04AR122-00001
A04AR123-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 123 | Wood Door w/ Wood Frame (UoM: EA) | AJ | Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR123 | A04AR123-00001
A04AR123-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 123 | Wood Door w/ Wood Frame (UoM: EA) | AK | Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR123 | A04AR123-00002
A04AR124-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 124 | Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: M2) | [10 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR124 | A04AR124-00001
A04AR125-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 125 | Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) | AJ | Single Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR125 | A04AR125-00001
A04AR125-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 125 | Wood Door w/ Wood Frame & Vision Panel for Each Leaf (UoM: EA) | AK | Double Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR125 | A04AR125-00002
A04AR126-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AL | Fire Protective Rating: N/A, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR126 | A04AR126-00001
A04AR126-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AM | Fire Protective Rating: N/A, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR126 | A04AR126-00002
A04AR126-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AN | Fire Protective Rating: 0.5-hr, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR126 | A04AR126-00003
A04AR126-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AP | Fire Protective Rating: 0.5-hr, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR126 | A04AR126-00004
A04AR126-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AQ | Fire Protective Rating: 1-hr, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR126 | A04AR126-00005
A04AR126-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AR | Fire Protective Rating: 1-hr, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR126 | A04AR126-00006
A04AR126-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AS | Fire Protective Rating: 1.5-hrs, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR126 | A04AR126-00007
A04AR126-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AT | Fire Protective Rating: 1.5-hrs, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR126 | A04AR126-00008
A04AR126-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AU | Fire Protective Rating: 2-hrs, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR126 | A04AR126-00009
A04AR126-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 126 | Steel Roll Up Door w/ Steel Frame (UoM: M2) | AV | Fire Protective Rating: 2-hrs, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR126 | A04AR126-00010
A04AR127-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AL | Fire Protective Rating: N/A, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR127 | A04AR127-00001
A04AR127-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AM | Fire Protective Rating: N/A, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR127 | A04AR127-00002
A04AR127-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AN | Fire Protective Rating: 0.5-hr, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR127 | A04AR127-00003
A04AR127-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AP | Fire Protective Rating: 0.5-hr, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR127 | A04AR127-00004
A04AR127-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AQ | Fire Protective Rating: 1-hr, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR127 | A04AR127-00005
A04AR127-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AR | Fire Protective Rating: 1-hr, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR127 | A04AR127-00006
A04AR127-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AS | Fire Protective Rating: 1.5-hrs, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR127 | A04AR127-00007
A04AR127-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AT | Fire Protective Rating: 1.5-hrs, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR127 | A04AR127-00008
A04AR127-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AU | Fire Protective Rating: 2-hrs, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR127 | A04AR127-00009
A04AR127-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 127 | Steel Roll Up Door w/ Steel Frame (UoM: EA) | AV | Fire Protective Rating: 2-hrs, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR127 | A04AR127-00010
A04AR128-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 128 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | AL | Fire Protective Rating: N/A, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR128 | A04AR128-00001
A04AR128-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 128 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | AM | Fire Protective Rating: N/A, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR128 | A04AR128-00002
A04AR128-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 128 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | AQ | Fire Protective Rating: 1-hr, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR128 | A04AR128-00003
A04AR128-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 128 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | AR | Fire Protective Rating: 1-hr, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR128 | A04AR128-00004
A04AR128-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 128 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | AU | Fire Protective Rating: 2-hrs, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR128 | A04AR128-00005
A04AR128-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 128 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: M2) | AV | Fire Protective Rating: 2-hrs, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR128 | A04AR128-00006
A04AR129-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 129 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | AL | Fire Protective Rating: N/A, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR129 | A04AR129-00001
A04AR129-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 129 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | AM | Fire Protective Rating: N/A, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR129 | A04AR129-00002
A04AR129-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 129 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | AQ | Fire Protective Rating: 1-hr, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR129 | A04AR129-00003
A04AR129-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 129 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | AR | Fire Protective Rating: 1-hr, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR129 | A04AR129-00004
A04AR129-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 129 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | AU | Fire Protective Rating: 2-hrs, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR129 | A04AR129-00005
A04AR129-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 129 | Blast Resistant Roll Up Door w/ Steel Frame (UoM: EA) | AV | Fire Protective Rating: 2-hrs, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR129 | A04AR129-00006
A04AR130-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 130 | Aluminum Roll Up Door w/ Aluminum Frame (UoM: M2) | AL | Fire Protective Rating: N/A, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR130 | A04AR130-00001
A04AR130-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 130 | Aluminum Roll Up Door w/ Aluminum Frame (UoM: M2) | AM | Fire Protective Rating: N/A, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR130 | A04AR130-00002
A04AR131-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 131 | Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) | AL | Fire Protective Rating: N/A, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR131 | A04AR131-00001
A04AR131-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 131 | Aluminum Roll Up Door w/ Aluminum Frame (UoM: EA) | AM | Fire Protective Rating: N/A, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR131 | A04AR131-00002
A04AR132-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AL | Fire Protective Rating: N/A, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR132 | A04AR132-00001
A04AR132-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AM | Fire Protective Rating: N/A, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR132 | A04AR132-00002
A04AR132-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AN | Fire Protective Rating: 0.5-hr, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR132 | A04AR132-00003
A04AR132-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AP | Fire Protective Rating: 0.5-hr, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR132 | A04AR132-00004
A04AR132-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AQ | Fire Protective Rating: 1-hr, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR132 | A04AR132-00005
A04AR132-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AR | Fire Protective Rating: 1-hr, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR132 | A04AR132-00006
A04AR132-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AS | Fire Protective Rating: 1.5-hrs, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR132 | A04AR132-00007
A04AR132-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AT | Fire Protective Rating: 1.5-hrs, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR132 | A04AR132-00008
A04AR132-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AU | Fire Protective Rating: 2-hrs, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR132 | A04AR132-00009
A04AR132-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 132 | Steel Sliding Door w/ Steel Frame (UoM: M2) | AV | Fire Protective Rating: 2-hrs, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR132 | A04AR132-00010
A04AR133-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AL | Fire Protective Rating: N/A, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR133 | A04AR133-00001
A04AR133-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AM | Fire Protective Rating: N/A, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR133 | A04AR133-00002
A04AR133-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AN | Fire Protective Rating: 0.5-hr, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR133 | A04AR133-00003
A04AR133-00004 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AP | Fire Protective Rating: 0.5-hr, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR133 | A04AR133-00004
A04AR133-00005 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AQ | Fire Protective Rating: 1-hr, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR133 | A04AR133-00005
A04AR133-00006 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AR | Fire Protective Rating: 1-hr, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR133 | A04AR133-00006
A04AR133-00007 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AS | Fire Protective Rating: 1.5-hrs, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR133 | A04AR133-00007
A04AR133-00008 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AT | Fire Protective Rating: 1.5-hrs, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR133 | A04AR133-00008
A04AR133-00009 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AU | Fire Protective Rating: 2-hrs, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR133 | A04AR133-00009
A04AR133-00010 | AR | A04 | Finishing Work | AR | Door & Window Work | 133 | Steel Sliding Door w/ Steel Frame (UoM: EA) | AV | Fire Protective Rating: 2-hrs, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR133 | A04AR133-00010
A04AR134-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 134 | Aluminum Sliding Door w/ Aluminum Frame (UoM: M2) | AL | Fire Protective Rating: N/A, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR134 | A04AR134-00001
A04AR134-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 134 | Aluminum Sliding Door w/ Aluminum Frame (UoM: M2) | AM | Fire Protective Rating: N/A, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR134 | A04AR134-00002
A04AR135-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 135 | Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) | AL | Fire Protective Rating: N/A, Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR135 | A04AR135-00001
A04AR135-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 135 | Aluminum Sliding Door w/ Aluminum Frame (UoM: EA) | AM | Fire Protective Rating: N/A, Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR135 | A04AR135-00002
A04AR136-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 136 | Steel Hanger Door w/ Steel Frame (UoM: M2) | [10 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR136 | A04AR136-00001
A04AR137-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 137 | Steel Hanger Door w/ Steel Frame (UoM: EA) | [10 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR137 | A04AR137-00001
A04AR138-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 138 | Steel Swing Door w/ Steel Frame (UoM: M2) | [10 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR138 | A04AR138-00001
A04AR139-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 139 | Steel Swing Door w/ Steel Frame (UoM: EA) | [10 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR139 | A04AR139-00001
A04AR140-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 140 | Aluminum Swing Door w/ Aluminum Frame (UoM: M2) | [10 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR140 | A04AR140-00001
A04AR141-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 141 | Aluminum Swing Door w/ Aluminum Frame (UoM: EA) | [10 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR141 | A04AR141-00001
A04AR142-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 142 | Revolving Door (UoM: EA) | AW | Manual Revolving Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | DIA=( )mm | [7 empty] | EA | EA | A04AR142 | A04AR142-00001
A04AR142-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 142 | Revolving Door (UoM: EA) | BA | Auto Revolving Door | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | DIA=( )mm | [7 empty] | EA | EA | A04AR142 | A04AR142-00002
A04AR143-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 143 | Steel Folding(Accordion) Door w/ Steel Frame (UoM: M2) | BB | Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR143 | A04AR143-00001
A04AR143-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 143 | Steel Folding(Accordion) Door w/ Steel Frame (UoM: M2) | BC | Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR143 | A04AR143-00002
A04AR144-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 144 | Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) | BB | Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR144 | A04AR144-00001
A04AR144-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 144 | Steel Folding(Accordion) Door w/ Steel Frame (UoM: EA) | BC | Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR144 | A04AR144-00002
A04AR145-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 145 | Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: M2) | BB | Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR145 | A04AR145-00001
A04AR145-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 145 | Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: M2) | BC | Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR145 | A04AR145-00002
A04AR146-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 146 | Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) | BB | Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR146 | A04AR146-00001
A04AR146-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 146 | Aluminum Folding(Accordion) Door w/ Aluminum Frame (UoM: EA) | BC | Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR146 | A04AR146-00002
A04AR147-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 147 | PVC Folding(Accordion) Door w/ PVC Frame (UoM: M2) | BC | Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR147 | A04AR147-00001
A04AR148-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 148 | PVC Folding(Accordion) Door w/ PVC Frame (UoM: EA) | BC | Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR148 | A04AR148-00001
A04AR149-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 149 | uPVC Door w/ uPVC Frame (UoM: M2) | [10 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR149 | A04AR149-00001
A04AR150-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 150 | uPVC Door w/ uPVC Frame (UoM: EA) | [10 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR150 | A04AR150-00001
A04AR151-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 151 | Master Key System | BD | Three Levels Master Key | [8 empty] | 37 | w/ Accessories (Key Box, Key Tag and ETC) | [13 empty] | SET | SET | A04AR151 | A04AR151-00001
A04AR152-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 152 | Steel Window (UoM: M2) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR152 | A04AR152-00001
A04AR152-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 152 | Steel Window (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR152 | A04AR152-00002
A04AR152-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 152 | Steel Window (UoM: M2) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR152 | A04AR152-00003
A04AR153-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 153 | Steel Window (UoM: EA) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR153 | A04AR153-00001
A04AR153-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 153 | Steel Window (UoM: EA) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR153 | A04AR153-00002
A04AR153-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 153 | Steel Window (UoM: EA) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR153 | A04AR153-00003
A04AR154-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 154 | Blast Resistant Steel Window (UoM: M2) | [10 empty] | 36 | w/ Hardware & Accessories | [10 empty] | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | M2 | A04AR154 | A04AR154-00001
A04AR155-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 155 | Blast Resistant Steel Window (UoM: EA) | [10 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm |  |  |  |  | Blast Load: Overpressure ( )psi, Duration ( )ms |  |  | EA | EA | A04AR155 | A04AR155-00001
A04AR156-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 156 | Bullet-Proof Steel Window (UoM: M2) | [10 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR156 | A04AR156-00001
A04AR157-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 157 | Bullet-Proof Steel Window (UoM: EA) | [10 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR157 | A04AR157-00001
A04AR158-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 158 | Aluminum Window (UoM: M2) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR158 | A04AR158-00001
A04AR158-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 158 | Aluminum Window (UoM: M2) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR158 | A04AR158-00002
A04AR158-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 158 | Aluminum Window (UoM: M2) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR158 | A04AR158-00003
A04AR159-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 159 | Aluminum Window (UoM: EA) | 89 | Fire Protective Rating: N/A | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR159 | A04AR159-00001
A04AR159-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 159 | Aluminum Window (UoM: EA) | 92 | Fire Protective Rating: 0.5-hr | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR159 | A04AR159-00002
A04AR159-00003 | AR | A04 | Finishing Work | AR | Door & Window Work | 159 | Aluminum Window (UoM: EA) | 95 | Fire Protective Rating: 1-hr | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR159 | A04AR159-00003
A04AR160-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 160 | uPVC Window (UoM: M2) | [10 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR160 | A04AR160-00001
A04AR161-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 161 | uPVC Window (UoM: EA) | [10 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR161 | A04AR161-00001
A04AR162-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 162 | Skylight (UoM: M2) | BG | FRP(Fiberglass Reinforced Plastics) Skylight | [23 empty] | M2 | M2 | A04AR162 | A04AR162-00001
A04AR162-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 162 | Skylight (UoM: M2) | BH | Acrylic Skylight w/ Ventilation | [23 empty] | M2 | M2 | A04AR162 | A04AR162-00002
A04AR163-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 163 | Louver (UoM: M2) | BJ | Aluminum | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR163 | A04AR163-00001
A04AR163-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 163 | Louver (UoM: M2) | BK | Steel | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR163 | A04AR163-00002
A04AR164-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 164 | Louver (UoM: EA) | BJ | Aluminum | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR164 | A04AR164-00001
A04AR164-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 164 | Louver (UoM: EA) | BK | Steel | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR164 | A04AR164-00002
A04AR165-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 165 | Shade (UoM: M2) | BC | Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR165 | A04AR165-00001
A04AR165-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 165 | Shade (UoM: M2) | BB | Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR165 | A04AR165-00002
A04AR166-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 166 | Shade (UoM: EA) | BC | Manual Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR166 | A04AR166-00001
A04AR166-00002 | AR | A04 | Finishing Work | AR | Door & Window Work | 166 | Shade (UoM: EA) | BB | Motorized Type | [8 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR166 | A04AR166-00002
A04AR315-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 315 | Curtain Wall System (UoM: M2) | [10 empty] | 36 | w/ Hardware & Accessories | [13 empty] | EA | M2 | A04AR315 | A04AR315-00001
A04AR316-00001 | AR | A04 | Finishing Work | AR | Door & Window Work | 316 | Curtain Wall System (UoM: EA) | [10 empty] | 36 | w/ Hardware & Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AR316 | A04AR316-00001
A04AS038-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 038 | Welded Wire Fabric | [14 empty] | 53 | DIA≤6mm |  | Mesh Size=DIA( )mm x ( )mm x ( )mm | [7 empty] | M2 | M2 | A04AS038 | A04AS038-00001
A04AS038-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 038 | Welded Wire Fabric | [14 empty] | 54 | DIA>6mm |  | Mesh Size=DIA( )mm x ( )mm x ( )mm | [7 empty] | M2 | M2 | A04AS038 | A04AS038-00002
A04AS167-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 167 | Marble Window Sill | [10 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [5 empty] | THK=( )mm / W=( )mm | [7 empty] | M | M | A04AS167 | A04AS167-00001
A04AS168-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 168 | Screed | [10 empty] | 31 | w/o Welded Wire Fabric |  |  | 31 | THK<50mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AS168 | A04AS168-00001
A04AS168-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 168 | Screed | [10 empty] | 31 | w/o Welded Wire Fabric |  |  | 09 | 50mm≤THK<75mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AS168 | A04AS168-00002
A04AS168-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 168 | Screed | [10 empty] | 31 | w/o Welded Wire Fabric |  |  | 27 | 75mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A04AS168 | A04AS168-00003
A04AS169-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 169 | Carpet | [25 empty] | M2 | M2 | A04AS169 | A04AS169-00001
A04AS170-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 170 | Carpet Tile | [17 empty] | Tile Size=W( )mm x L( )mm | [7 empty] | M2 | M2 | A04AS170 | A04AS170-00001
A04AS171-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 171 | Recess Floor Mat | [25 empty] | M2 | M2 | A04AS171 | A04AS171-00001
A04AS172-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 172 | Entrance Floor Mats and Frame | [25 empty] | M2 | M2 | A04AS172 | A04AS172-00001
A04AS172-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 172 | Entrance Floor Mats and Frame | BL | Embedded Type | [23 empty] | M2 | M2 | A04AS172 | A04AS172-00002
A04AS173-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 173 | Steel Trowel Finish | [25 empty] | M2 | M2 | A04AS173 | A04AS173-00001
A04AS173-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 173 | Steel Trowel Finish | BM | Brushed(Broom) Finish | [23 empty] | M2 | M2 | A04AS173 | A04AS173-00002
A04AS173-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 173 | Steel Trowel Finish | BN | Hardener Finish(Powder Type) | [23 empty] | M2 | M2 | A04AS173 | A04AS173-00003
A04AS173-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 173 | Steel Trowel Finish | BP | Hardener Finish(Liquid Type) | [23 empty] | M2 | M2 | A04AS173 | A04AS173-00004
A04AS174-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BQ | Top Finish: Anti-Static Vinyl Tile | [12 empty] | 73 | 600mm x 600mm / H≤600mm |  | H=( )mm | [7 empty] | M2 | M2 | A04AS174 | A04AS174-00001
A04AS174-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BQ | Top Finish: Anti-Static Vinyl Tile | [12 empty] | 74 | 600mm x 600mm / 600mm<H≤1000mm |  | H=( )mm | [7 empty] | M2 | M2 | A04AS174 | A04AS174-00002
A04AS174-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BQ | Top Finish: Anti-Static Vinyl Tile | [12 empty] | 75 | 600mm x 600mm / 1000mm<H≤1500mm |  | H=( )mm | [7 empty] | M2 | M2 | A04AS174 | A04AS174-00003
A04AS174-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BR | Top Finish: Carpet Tile | [12 empty] | 73 | 600mm x 600mm / H≤600mm |  | H=( )mm | [7 empty] | M2 | M2 | A04AS174 | A04AS174-00004
A04AS174-00005 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BR | Top Finish: Carpet Tile | [12 empty] | 74 | 600mm x 600mm / 600mm<H≤1000mm |  | H=( )mm | [7 empty] | M2 | M2 | A04AS174 | A04AS174-00005
A04AS174-00006 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BR | Top Finish: Carpet Tile | [12 empty] | 75 | 600mm x 600mm / 1000mm<H≤1500mm |  | H=( )mm | [7 empty] | M2 | M2 | A04AS174 | A04AS174-00006
A04AS174-00007 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BS | Top Finish: Marble | [12 empty] | 73 | 600mm x 600mm / H≤600mm |  | H=( )mm | [7 empty] | M2 | M2 | A04AS174 | A04AS174-00007
A04AS174-00008 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BS | Top Finish: Marble | [12 empty] | 74 | 600mm x 600mm / 600mm<H≤1000mm |  | H=( )mm | [7 empty] | M2 | M2 | A04AS174 | A04AS174-00008
A04AS174-00009 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 174 | Raised Floor | BS | Top Finish: Marble | [12 empty] | 75 | 600mm x 600mm / 1000mm<H≤1500mm |  | H=( )mm | [7 empty] | M2 | M2 | A04AS174 | A04AS174-00009
A04AS175-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 175 | Material Dividing Strip | BT | Stainless Steel | [23 empty] | M | M | A04AS175 | A04AS175-00001
A04AS176-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System | [6 empty] | 03 | Mineral Wool (Rock Wool) | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS176 | A04AS176-00001
A04AS176-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System | [6 empty] | 03 | Mineral Wool (Rock Wool) | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS176 | A04AS176-00002
A04AS176-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System | [6 empty] | 03 | Mineral Wool (Rock Wool) | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS176 | A04AS176-00003
A04AS176-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System | [6 empty] | 04 | Glass Wool (Fiberglass) | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS176 | A04AS176-00004
A04AS176-00005 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System | [6 empty] | 04 | Glass Wool (Fiberglass) | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS176 | A04AS176-00005
A04AS176-00006 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System | [6 empty] | 04 | Glass Wool (Fiberglass) | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS176 | A04AS176-00006
A04AS176-00007 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System | [6 empty] | 05 | Rigid Insulation | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS176 | A04AS176-00007
A04AS176-00008 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System | [6 empty] | 05 | Rigid Insulation | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS176 | A04AS176-00008
A04AS176-00009 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 176 | Plasterboard Dry Liner System | [6 empty] | 05 | Rigid Insulation | 06 | for Wall To External Side | 38 | w/ 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS176 | A04AS176-00009
A04AS177-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BU | Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm | [9 empty] | M2 | M2 | A04AS177 | A04AS177-00001
A04AS177-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BU | Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm | [9 empty] | M2 | M2 | A04AS177 | A04AS177-00002
A04AS177-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BU | Fire Protective Rating: N/A, 1-Layer Gypsum Board to One Side |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm | [9 empty] | M2 | M2 | A04AS177 | A04AS177-00003
A04AS177-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BV | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm | [9 empty] | M2 | M2 | A04AS177 | A04AS177-00004
A04AS177-00005 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BV | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm | [9 empty] | M2 | M2 | A04AS177 | A04AS177-00005
A04AS177-00006 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BV | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to One Side |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm | [9 empty] | M2 | M2 | A04AS177 | A04AS177-00006
A04AS177-00007 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00007
A04AS177-00008 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00008
A04AS177-00009 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00009
A04AS177-00010 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00010
A04AS177-00011 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00011
A04AS177-00012 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00012
A04AS177-00013 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm | [9 empty] | M2 | M2 | A04AS177 | A04AS177-00013
A04AS177-00014 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm | [9 empty] | M2 | M2 | A04AS177 | A04AS177-00014
A04AS177-00015 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm | [9 empty] | M2 | M2 | A04AS177 | A04AS177-00015
A04AS177-00016 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00016
A04AS177-00017 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00017
A04AS177-00018 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00018
A04AS177-00019 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00019
A04AS177-00020 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00020
A04AS177-00021 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00021
A04AS177-00022 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm | [9 empty] | M2 | M2 | A04AS177 | A04AS177-00022
A04AS177-00023 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm | [9 empty] | M2 | M2 | A04AS177 | A04AS177-00023
A04AS177-00024 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CA | Fire Protective Rating: N/A, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm | [9 empty] | M2 | M2 | A04AS177 | A04AS177-00024
A04AS177-00025 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CB | Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00025
A04AS177-00026 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CB | Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00026
A04AS177-00027 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CB | Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00027
A04AS177-00028 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CB | Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00028
A04AS177-00029 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CB | Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00029
A04AS177-00030 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CB | Fire Protective Rating: 1-hr, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00030
A04AS177-00031 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CC | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00031
A04AS177-00032 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CC | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00032
A04AS177-00033 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CC | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00033
A04AS177-00034 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CC | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00034
A04AS177-00035 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CC | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00035
A04AS177-00036 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 177 | Gypsumboard Partition Wall (Fixed Type) | CC | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS177 | A04AS177-00036
A04AS178-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS178 | A04AS178-00001
A04AS178-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS178 | A04AS178-00002
A04AS178-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 03 | Mineral Wool (Rock Wool) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS178 | A04AS178-00003
A04AS178-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS178 | A04AS178-00004
A04AS178-00005 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS178 | A04AS178-00005
A04AS178-00006 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 04 | Glass Wool (Fiberglass) |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm |  | Insulation THK=( )mm | [7 empty] | M2 | M2 | A04AS178 | A04AS178-00006
A04AS178-00007 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 76 | 1-Layer Gypsumboard THK=9.5mm | [9 empty] | M2 | M2 | A04AS178 | A04AS178-00007
A04AS178-00008 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm | [9 empty] | M2 | M2 | A04AS178 | A04AS178-00008
A04AS178-00009 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 178 | Gypsumboard Partition Wall (Removable Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides |  |  |  |  | 02 | w/o Insulation |  |  | 39 | Including Supporting Frame(Stud) & Accessories |  |  | 78 | 1-Layer Gypsumboard THK=16mm | [9 empty] | M2 | M2 | A04AS178 | A04AS178-00009
A04AS179-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 179 | Cubicle Partition | [8 empty] | 07 | for Toilet | 32 | w/ Accessories | [5 empty] | H=( )mm | [7 empty] | M | M | A04AS179 | A04AS179-00001
A04AS180-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 180 | Shower Booth Partition | [10 empty] | 32 | w/ Accessories | [5 empty] | H=( )mm | [7 empty] | M | M | A04AS180 | A04AS180-00001
A04AS181-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 181 | Acoustic Panel | [8 empty] | 08 | for Wall | 40 | w/ Accessories (Supporting Frame, Acoustic Insulation, Etc.) | [13 empty] | M2 | M2 | A04AS181 | A04AS181-00001
A04AS182-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 182 | Face Brick | [10 empty] | 41 | w/ Bedding | [13 empty] | M2 | M2 | A04AS182 | A04AS182-00001
A04AS183-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 183 | Hard Wood Trim | [8 empty] | 08 | for Wall |  |  |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AS183 | A04AS183-00001
A04AS183-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 183 | Hard Wood Trim | [8 empty] | 08 | for Wall |  |  |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AS183 | A04AS183-00002
A04AS183-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 183 | Hard Wood Trim | [8 empty] | 08 | for Wall |  |  |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AS183 | A04AS183-00003
A04AS184-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 184 | Aluminum Baseboard | [8 empty] | 09 | for Skirt | 42 | w/ Adhesive |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AS184 | A04AS184-00001
A04AS184-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 184 | Aluminum Baseboard | [8 empty] | 09 | for Skirt | 42 | w/ Adhesive |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AS184 | A04AS184-00002
A04AS184-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 184 | Aluminum Baseboard | [8 empty] | 09 | for Skirt | 42 | w/ Adhesive |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AS184 | A04AS184-00003
A04AS185-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 185 | Coved Rubber Skirting | [8 empty] | 09 | for Skirt | 42 | w/ Adhesive |  |  | 86 | H<150mm |  | H=( )mm | [7 empty] | M | M | A04AS185 | A04AS185-00001
A04AS185-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 185 | Coved Rubber Skirting | [8 empty] | 09 | for Skirt | 42 | w/ Adhesive |  |  | 67 | 150mm≤H<200mm |  | H=( )mm | [7 empty] | M | M | A04AS185 | A04AS185-00002
A04AS185-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 185 | Coved Rubber Skirting | [8 empty] | 09 | for Skirt | 42 | w/ Adhesive |  |  | 68 | 200mm≤H |  | H=( )mm | [7 empty] | M | M | A04AS185 | A04AS185-00003
A04AS186-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 186 | Fiber Board Ceiling System | CD | M-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | [5 empty] | Tile Size=( )mm x ( )mm | [7 empty] | M2 | M2 | A04AS186 | A04AS186-00001
A04AS186-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 186 | Fiber Board Ceiling System | CE | T-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | [5 empty] | Tile Size=( )mm x ( )mm | [7 empty] | M2 | M2 | A04AS186 | A04AS186-00002
A04AS187-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 187 | Gypsum Plaster Board Ceiling System | CD | M-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm | [9 empty] | M2 | M2 | A04AS187 | A04AS187-00001
A04AS187-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 187 | Gypsum Plaster Board Ceiling System | CD | M-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  |  | 78 | 1-Layer Gypsumboard THK=16mm | [9 empty] | M2 | M2 | A04AS187 | A04AS187-00002
A04AS188-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 188 | Moisture Resistant Gypsum Plaster Board Ceiling System | CD | M-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  |  | 77 | 1-Layer Gypsumboard THK=12.5mm | [9 empty] | M2 | M2 | A04AS188 | A04AS188-00001
A04AS188-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 188 | Moisture Resistant Gypsum Plaster Board Ceiling System | CD | M-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) |  |  | 78 | 1-Layer Gypsumboard THK=16mm | [9 empty] | M2 | M2 | A04AS188 | A04AS188-00002
A04AS189-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 189 | Cement Board Ceiling System | CD | M-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | [5 empty] | Tile Size=( )mm x ( )mm | [7 empty] | M2 | M2 | A04AS189 | A04AS189-00001
A04AS189-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 189 | Cement Board Ceiling System | CE | T-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | [5 empty] | Tile Size=( )mm x ( )mm | [7 empty] | M2 | M2 | A04AS189 | A04AS189-00002
A04AS190-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 190 | Acoustic Tiled Ceiling System | CD | M-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | [5 empty] | Tile Size=( )mm x ( )mm | [7 empty] | M2 | M2 | A04AS190 | A04AS190-00001
A04AS190-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 190 | Acoustic Tiled Ceiling System | CE | T-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | [5 empty] | Tile Size=( )mm x ( )mm | [7 empty] | M2 | M2 | A04AS190 | A04AS190-00002
A04AS191-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 191 | Moisture Resistant Tiled Ceiling System | CD | M-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | [5 empty] | Tile Size=( )mm x ( )mm | [7 empty] | M2 | M2 | A04AS191 | A04AS191-00001
A04AS191-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 191 | Moisture Resistant Tiled Ceiling System | CE | T-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | [5 empty] | Tile Size=( )mm x ( )mm | [7 empty] | M2 | M2 | A04AS191 | A04AS191-00002
A04AS192-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 192 | Aluminum Spandrel Ceiling System | CD | M-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | [13 empty] | M2 | M2 | A04AS192 | A04AS192-00001
A04AS193-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 193 | Metal Open Cell Ceiling | CD | M-Bar System | [8 empty] | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | [13 empty] | M2 | M2 | A04AS193 | A04AS193-00001
A04AS194-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 194 | Rigid Insulation | [8 empty] | 10 | for Exposed Ceiling Structure of Cable Room | 32 | w/ Accessories |  |  | 31 | THK<50mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AS194 | A04AS194-00001
A04AS194-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 194 | Rigid Insulation | [8 empty] | 10 | for Exposed Ceiling Structure of Cable Room | 32 | w/ Accessories |  |  | 09 | 50mm≤THK<75mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AS194 | A04AS194-00002
A04AS194-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 194 | Rigid Insulation | [8 empty] | 10 | for Exposed Ceiling Structure of Cable Room | 32 | w/ Accessories |  |  | 27 | 75mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A04AS194 | A04AS194-00003
A04AS194-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 194 | Rigid Insulation | [8 empty] | 11 | for Exposed Wall Structure of Cable Room | 32 | w/ Accessories |  |  | 31 | THK<50mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AS194 | A04AS194-00004
A04AS194-00005 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 194 | Rigid Insulation | [8 empty] | 11 | for Exposed Wall Structure of Cable Room | 32 | w/ Accessories |  |  | 09 | 50mm≤THK<75mm |  | THK=( )mm | [7 empty] | M2 | M2 | A04AS194 | A04AS194-00005
A04AS194-00006 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 194 | Rigid Insulation | [8 empty] | 11 | for Exposed Wall Structure of Cable Room | 32 | w/ Accessories |  |  | 27 | 75mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A04AS194 | A04AS194-00006
A04AS195-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CF | Steel Canopy | [8 empty] | 44 | w/ Supporting Frame, Accessories | [5 empty] | W x L x Min. D=( )mm x ( )mm x ( )mm | [7 empty] | EA | EA | A04AS195 | A04AS195-00001
A04AS195-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CG | Stainless Steel Canopy | [8 empty] | 44 | w/ Supporting Frame, Accessories | [5 empty] | W x L x Min. D=( )mm x ( )mm x ( )mm | [7 empty] | EA | EA | A04AS195 | A04AS195-00002
A04AS195-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CH | Aluminum Canopy | [8 empty] | 44 | w/ Supporting Frame, Accessories | [5 empty] | W x L x Min. D=( )mm x ( )mm x ( )mm | [7 empty] | EA | EA | A04AS195 | A04AS195-00003
A04AS195-00004 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CJ | Polycarbonate Canopy | [8 empty] | 44 | w/ Supporting Frame, Accessories | [5 empty] | W x L x Min. D=( )mm x ( )mm x ( )mm | [7 empty] | EA | EA | A04AS195 | A04AS195-00004
A04AS195-00005 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CK | GRP Canopy | [8 empty] | 44 | w/ Supporting Frame, Accessories | [5 empty] | W x L x Min. D=( )mm x ( )mm x ( )mm | [7 empty] | EA | EA | A04AS195 | A04AS195-00005
A04AS195-00006 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CL | Steel Canopy (Continuous Type) | [8 empty] | 45 | along Walkway, w/ Supporting Frame, Accessories | [5 empty] | W x Min. D=( )mm x ( )mm | [7 empty] | EA | M | A04AS195 | A04AS195-00006
A04AS195-00007 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CM | Polycarbonate Canopy (Continuous Type) | [8 empty] | 45 | along Walkway, w/ Supporting Frame, Accessories | [5 empty] | W x Min. D=( )mm x ( )mm | [7 empty] | EA | M | A04AS195 | A04AS195-00007
A04AS195-00008 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CN | Steel Canopy (Rounded Type) | [8 empty] | 44 | w/ Supporting Frame, Accessories | [5 empty] | W x H x Min. D=( )mm x ( )mm x ( )mm | [7 empty] | EA | EA | A04AS195 | A04AS195-00008
A04AS195-00009 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CP | Stainless Steel Canopy (Rounded Type) | [8 empty] | 44 | w/ Supporting Frame, Accessories | [5 empty] | W x H x Min. D=( )mm x ( )mm x ( )mm | [7 empty] | EA | EA | A04AS195 | A04AS195-00009
A04AS195-00010 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CQ | Aluminum Canopy (Rounded Type) | [8 empty] | 44 | w/ Supporting Frame, Accessories | [5 empty] | W x H x Min. D=( )mm x ( )mm x ( )mm | [7 empty] | EA | EA | A04AS195 | A04AS195-00010
A04AS195-00011 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CR | Polycarbonate Canopy (Rounded Type) | [8 empty] | 44 | w/ Supporting Frame, Accessories | [5 empty] | W x H x Min. D=( )mm x ( )mm x ( )mm | [7 empty] | EA | EA | A04AS195 | A04AS195-00011
A04AS195-00012 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 195 | Pre-Fabricated Canopy | CS | GRP Canopy (Rounded Type) | [8 empty] | 44 | w/ Supporting Frame, Accessories | [5 empty] | W x H x Min. D=( )mm x ( )mm x ( )mm | [7 empty] | EA | EA | A04AS195 | A04AS195-00012
A04AS196-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 196 | Custom-Made Canopy for Main Entrance | CF | Steel Canopy | [8 empty] | 46 | w/ Supporting Frame, Accessories, Lighting Fixtures | [5 empty] | W x H x Min. D=( )mm x ( )mm x ( )mm | [7 empty] | SET | SET | A04AS196 | A04AS196-00001
A04AS196-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 196 | Custom-Made Canopy for Main Entrance | CG | Stainless Steel Canopy | [8 empty] | 46 | w/ Supporting Frame, Accessories, Lighting Fixtures | [5 empty] | W x H x Min. D=( )mm x ( )mm x ( )mm | [7 empty] | SET | SET | A04AS196 | A04AS196-00002
A04AS196-00003 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 196 | Custom-Made Canopy for Main Entrance | CH | Aluminum Canopy | [8 empty] | 46 | w/ Supporting Frame, Accessories, Lighting Fixtures | [5 empty] | W x H x Min. D=( )mm x ( )mm x ( )mm | [7 empty] | SET | SET | A04AS196 | A04AS196-00003
A04AS197-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 197 | Roof Tile | CT | Metallic Tile w/ Insulation | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [13 empty] | M2 | M2 | A04AS197 | A04AS197-00001
A04AS197-00002 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 197 | Roof Tile | CU | Metallic Tile w/o Insulation | [8 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [13 empty] | M2 | M2 | A04AS197 | A04AS197-00002
A04AS314-00001 | AR | A04 | Finishing Work | AS | Exterior/Interior Finish Work | 314 | Plywood w/ Fire Retardant Paint | [25 empty] | M2 | M2 | A04AS314 | A04AS314-00001
A04AT198-00001 | AR | A04 | Finishing Work | AT | Plastering Work | 198 | Plastering | [8 empty] | 12 | for External Masonry Wall | [7 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AT198 | A04AT198-00001
A04AT198-00002 | AR | A04 | Finishing Work | AT | Plastering Work | 198 | Plastering | [8 empty] | 13 | for Internal Masonry Wall | [7 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AT198 | A04AT198-00002
A04AT198-00003 | AR | A04 | Finishing Work | AT | Plastering Work | 198 | Plastering | [8 empty] | 14 | for Exposed Conc. Surface | [7 empty] | THK=( )mm | [7 empty] | M2 | M2 | A04AT198 | A04AT198-00003
A04AV205-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | DQ | Cast Iron Type | [12 empty] | 56 | DIA=100mm | [9 empty] | EA | EA | A04AV205 | A04AV205-00001
A04AV205-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | DQ | Cast Iron Type | [12 empty] | 57 | DIA=150mm | [9 empty] | EA | EA | A04AV205 | A04AV205-00002
A04AV205-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | DQ | Cast Iron Type | [12 empty] | 58 | DIA=200mm | [9 empty] | EA | EA | A04AV205 | A04AV205-00003
A04AV205-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | DQ | Cast Iron Type | [12 empty] | 59 | DIA=250mm | [9 empty] | EA | EA | A04AV205 | A04AV205-00004
A04AV205-00005 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 29 | PVC Type | [12 empty] | 56 | DIA=100mm | [9 empty] | EA | EA | A04AV205 | A04AV205-00005
A04AV205-00006 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 29 | PVC Type | [12 empty] | 57 | DIA=150mm | [9 empty] | EA | EA | A04AV205 | A04AV205-00006
A04AV205-00007 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 29 | PVC Type | [12 empty] | 58 | DIA=200mm | [9 empty] | EA | EA | A04AV205 | A04AV205-00007
A04AV205-00008 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 29 | PVC Type | [12 empty] | 59 | DIA=250mm | [9 empty] | EA | EA | A04AV205 | A04AV205-00008
A04AV205-00009 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 30 | Stainless Steel Type | [12 empty] | 56 | DIA=100mm | [9 empty] | EA | EA | A04AV205 | A04AV205-00009
A04AV205-00010 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 30 | Stainless Steel Type | [12 empty] | 57 | DIA=150mm | [9 empty] | EA | EA | A04AV205 | A04AV205-00010
A04AV205-00011 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 30 | Stainless Steel Type | [12 empty] | 58 | DIA=200mm | [9 empty] | EA | EA | A04AV205 | A04AV205-00011
A04AV205-00012 | AR | A04 | Finishing Work | AV | Misc. Work | 205 | Roof Drain (for Building) | 30 | Stainless Steel Type | [12 empty] | 59 | DIA=250mm | [9 empty] | EA | EA | A04AV205 | A04AV205-00012
A04AV206-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | DQ | Cast Iron Type | [12 empty] | 56 | DIA=100mm | [9 empty] | EA | EA | A04AV206 | A04AV206-00001
A04AV206-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | DQ | Cast Iron Type | [12 empty] | 57 | DIA=150mm | [9 empty] | EA | EA | A04AV206 | A04AV206-00002
A04AV206-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | DQ | Cast Iron Type | [12 empty] | 58 | DIA=200mm | [9 empty] | EA | EA | A04AV206 | A04AV206-00003
A04AV206-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | DQ | Cast Iron Type | [12 empty] | 59 | DIA=250mm | [9 empty] | EA | EA | A04AV206 | A04AV206-00004
A04AV206-00005 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 29 | PVC Type | [12 empty] | 56 | DIA=100mm | [9 empty] | EA | EA | A04AV206 | A04AV206-00005
A04AV206-00006 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 29 | PVC Type | [12 empty] | 57 | DIA=150mm | [9 empty] | EA | EA | A04AV206 | A04AV206-00006
A04AV206-00007 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 29 | PVC Type | [12 empty] | 58 | DIA=200mm | [9 empty] | EA | EA | A04AV206 | A04AV206-00007
A04AV206-00008 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 29 | PVC Type | [12 empty] | 59 | DIA=250mm | [9 empty] | EA | EA | A04AV206 | A04AV206-00008
A04AV206-00009 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 30 | Stainless Steel Type | [12 empty] | 56 | DIA=100mm | [9 empty] | EA | EA | A04AV206 | A04AV206-00009
A04AV206-00010 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 30 | Stainless Steel Type | [12 empty] | 57 | DIA=150mm | [9 empty] | EA | EA | A04AV206 | A04AV206-00010
A04AV206-00011 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 30 | Stainless Steel Type | [12 empty] | 58 | DIA=200mm | [9 empty] | EA | EA | A04AV206 | A04AV206-00011
A04AV206-00012 | AR | A04 | Finishing Work | AV | Misc. Work | 206 | Roof Drain (for Shelter) | 30 | Stainless Steel Type | [12 empty] | 59 | DIA=250mm | [9 empty] | EA | EA | A04AV206 | A04AV206-00012
A04AV207-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | DR | Galvanized Steel Type | [8 empty] | 34 | w/ Fixing Accessories |  |  | 56 | DIA=100mm | [9 empty] | M | M | A04AV207 | A04AV207-00001
A04AV207-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | DR | Galvanized Steel Type | [8 empty] | 34 | w/ Fixing Accessories |  |  | 57 | DIA=150mm | [9 empty] | M | M | A04AV207 | A04AV207-00002
A04AV207-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | DR | Galvanized Steel Type | [8 empty] | 34 | w/ Fixing Accessories |  |  | 58 | DIA=200mm | [9 empty] | M | M | A04AV207 | A04AV207-00003
A04AV207-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | DR | Galvanized Steel Type | [8 empty] | 34 | w/ Fixing Accessories |  |  | 59 | DIA=250mm | [9 empty] | M | M | A04AV207 | A04AV207-00004
A04AV207-00005 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 29 | PVC Type | [8 empty] | 34 | w/ Fixing Accessories |  |  | 56 | DIA=100mm | [9 empty] | M | M | A04AV207 | A04AV207-00005
A04AV207-00006 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 29 | PVC Type | [8 empty] | 34 | w/ Fixing Accessories |  |  | 57 | DIA=150mm | [9 empty] | M | M | A04AV207 | A04AV207-00006
A04AV207-00007 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 29 | PVC Type | [8 empty] | 34 | w/ Fixing Accessories |  |  | 58 | DIA=200mm | [9 empty] | M | M | A04AV207 | A04AV207-00007
A04AV207-00008 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 29 | PVC Type | [8 empty] | 34 | w/ Fixing Accessories |  |  | 59 | DIA=250mm | [9 empty] | M | M | A04AV207 | A04AV207-00008
A04AV207-00009 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 30 | Stainless Steel Type | [8 empty] | 34 | w/ Fixing Accessories |  |  | 56 | DIA=100mm | [9 empty] | M | M | A04AV207 | A04AV207-00009
A04AV207-00010 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 30 | Stainless Steel Type | [8 empty] | 34 | w/ Fixing Accessories |  |  | 57 | DIA=150mm | [9 empty] | M | M | A04AV207 | A04AV207-00010
A04AV207-00011 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 30 | Stainless Steel Type | [8 empty] | 34 | w/ Fixing Accessories |  |  | 58 | DIA=200mm | [9 empty] | M | M | A04AV207 | A04AV207-00011
A04AV207-00012 | AR | A04 | Finishing Work | AV | Misc. Work | 207 | Downspout | 30 | Stainless Steel Type | [8 empty] | 34 | w/ Fixing Accessories |  |  | 59 | DIA=250mm | [9 empty] | M | M | A04AV207 | A04AV207-00012
A04AV208-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 208 | Water Collection Box | DR | Galvanized Steel Type | [8 empty] | 34 | w/ Fixing Accessories | [13 empty] | EA | EA | A04AV208 | A04AV208-00001
A04AV208-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 208 | Water Collection Box | 29 | PVC Type | [8 empty] | 34 | w/ Fixing Accessories | [13 empty] | EA | EA | A04AV208 | A04AV208-00002
A04AV208-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 208 | Water Collection Box | 30 | Stainless Steel Type | [8 empty] | 34 | w/ Fixing Accessories | [13 empty] | EA | EA | A04AV208 | A04AV208-00003
A04AV209-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 209 | Splash Block | DS | Precast Concrete Block Type | [23 empty] | EA | EA | A04AV209 | A04AV209-00001
A04AV210-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 210 | Natural Ventilator | [10 empty] | 34 | w/ Fixing Accessories |  |  | 61 | 400mm≤DIA<600mm |  | DIA=( )mm | [7 empty] | EA | EA | A04AV210 | A04AV210-00001
A04AV210-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 210 | Natural Ventilator | [10 empty] | 34 | w/ Fixing Accessories |  |  | 62 | 600mm≤DIA<800mm |  | DIA=( )mm | [7 empty] | EA | EA | A04AV210 | A04AV210-00002
A04AV210-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 210 | Natural Ventilator | [10 empty] | 34 | w/ Fixing Accessories |  |  | 63 | 800mm≤DIA<1000mm |  | DIA=( )mm | [7 empty] | EA | EA | A04AV210 | A04AV210-00003
A04AV210-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 210 | Natural Ventilator | [10 empty] | 34 | w/ Fixing Accessories |  |  | 64 | 1000mm≤DIA |  | DIA=( )mm | [7 empty] | EA | EA | A04AV210 | A04AV210-00004
A04AV211-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 211 | Manhole Cover | DT | Round Cast Iron Cover w/Frame | [8 empty] | 49 | Heavy Duty Type |  |  | 60 | DIA=600mm | [9 empty] | EA | EA | A04AV211 | A04AV211-00001
A04AV212-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DU | Self-Standing Type w/ Steel Frame | [8 empty] | 34 | w/ Fixing Accessories |  |  | 69 | 1500mm≤H<2000mm |  | H=( )mm | [7 empty] | M | M | A04AV212 | A04AV212-00001
A04AV212-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DU | Self-Standing Type w/ Steel Frame | [8 empty] | 34 | w/ Fixing Accessories |  |  | 70 | 2000mm≤H<2500mm |  | H=( )mm | [7 empty] | M | M | A04AV212 | A04AV212-00002
A04AV212-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DU | Self-Standing Type w/ Steel Frame | [8 empty] | 34 | w/ Fixing Accessories |  |  | 71 | 2500mm≤H<3000mm |  | H=( )mm | [7 empty] | M | M | A04AV212 | A04AV212-00003
A04AV212-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DU | Self-Standing Type w/ Steel Frame | [8 empty] | 34 | w/ Fixing Accessories |  |  | 72 | 3000mm≤H<3500mm |  | H=( )mm | [7 empty] | M | M | A04AV212 | A04AV212-00004
A04AV212-00005 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DV | Self-Standing Type w/ Stainless Steel Frame | [8 empty] | 34 | w/ Fixing Accessories |  |  | 69 | 1500mm≤H<2000mm |  | H=( )mm | [7 empty] | M | M | A04AV212 | A04AV212-00005
A04AV212-00006 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DV | Self-Standing Type w/ Stainless Steel Frame | [8 empty] | 34 | w/ Fixing Accessories |  |  | 70 | 2000mm≤H<2500mm |  | H=( )mm | [7 empty] | M | M | A04AV212 | A04AV212-00006
A04AV212-00007 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DV | Self-Standing Type w/ Stainless Steel Frame | [8 empty] | 34 | w/ Fixing Accessories |  |  | 71 | 2500mm≤H<3000mm |  | H=( )mm | [7 empty] | M | M | A04AV212 | A04AV212-00007
A04AV212-00008 | AR | A04 | Finishing Work | AV | Misc. Work | 212 | Chain Link Fence (Fixed Type) | DV | Self-Standing Type w/ Stainless Steel Frame | [8 empty] | 34 | w/ Fixing Accessories |  |  | 72 | 3000mm≤H<3500mm |  | H=( )mm | [7 empty] | M | M | A04AV212 | A04AV212-00008
A04AV213-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DU | Self-Standing Type w/ Steel Frame | [8 empty] | 34 | w/ Fixing Accessories |  |  | 69 | 1500mm≤H<2000mm |  | H=( )mm | [7 empty] | M | M | A04AV213 | A04AV213-00001
A04AV213-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DU | Self-Standing Type w/ Steel Frame | [8 empty] | 34 | w/ Fixing Accessories |  |  | 70 | 2000mm≤H<2500mm |  | H=( )mm | [7 empty] | M | M | A04AV213 | A04AV213-00002
A04AV213-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DU | Self-Standing Type w/ Steel Frame | [8 empty] | 34 | w/ Fixing Accessories |  |  | 71 | 2500mm≤H<3000mm |  | H=( )mm | [7 empty] | M | M | A04AV213 | A04AV213-00003
A04AV213-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DU | Self-Standing Type w/ Steel Frame | [8 empty] | 34 | w/ Fixing Accessories |  |  | 72 | 3000mm≤H<3500mm |  | H=( )mm | [7 empty] | M | M | A04AV213 | A04AV213-00004
A04AV213-00005 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DW | Frame Type w/ Steel Frame | [6 empty] | 17 | for Cable Room | 34 | w/ Fixing Accessories |  |  | 69 | 1500mm≤H<2000mm |  | H=( )mm | [7 empty] | M | M | A04AV213 | A04AV213-00005
A04AV213-00006 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DW | Frame Type w/ Steel Frame | [6 empty] | 17 | for Cable Room | 34 | w/ Fixing Accessories |  |  | 70 | 2000mm≤H<2500mm |  | H=( )mm | [7 empty] | M | M | A04AV213 | A04AV213-00006
A04AV213-00007 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DW | Frame Type w/ Steel Frame | [6 empty] | 17 | for Cable Room | 34 | w/ Fixing Accessories |  |  | 71 | 2500mm≤H<3000mm |  | H=( )mm | [7 empty] | M | M | A04AV213 | A04AV213-00007
A04AV213-00008 | AR | A04 | Finishing Work | AV | Misc. Work | 213 | Chain Link Fence (Removable Type) | DW | Frame Type w/ Steel Frame | [6 empty] | 17 | for Cable Room | 34 | w/ Fixing Accessories |  |  | 72 | 3000mm≤H<3500mm |  | H=( )mm | [7 empty] | M | M | A04AV213 | A04AV213-00008
A04AV214-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 214 | Chain Link Fence Single Gate | EA | Self-Standing Type, Single | [8 empty] | 50 | w/ Frame, Fixing Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AV214 | A04AV214-00001
A04AV214-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 214 | Chain Link Fence Single Gate | EC | Frame Type, Single | [8 empty] | 50 | w/ Frame, Fixing Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AV214 | A04AV214-00002
A04AV215-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 215 | Chain Link Fence Double Gate | EB | Self-Standing Type, Double | [8 empty] | 50 | w/ Frame, Fixing Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AV215 | A04AV215-00001
A04AV215-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 215 | Chain Link Fence Double Gate | ED | Frame Type, Double | [8 empty] | 50 | w/ Frame, Fixing Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AV215 | A04AV215-00002
A04AV216-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 216 | Metal Louvered Fence | DU | Self-Standing Type w/ Steel Frame | [8 empty] | 34 | w/ Fixing Accessories | [5 empty] | H=( )mm | [7 empty] | M | M | A04AV216 | A04AV216-00001
A04AV216-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 216 | Metal Louvered Fence | EE | Self-Standing Type w/ Galv. Steel Frame | [8 empty] | 34 | w/ Fixing Accessories | [5 empty] | H=( )mm | [7 empty] | M | M | A04AV216 | A04AV216-00002
A04AV216-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 216 | Metal Louvered Fence | EF | Self-Standing Type w/ Aluminum Frame | [8 empty] | 34 | w/ Fixing Accessories | [5 empty] | H=( )mm | [7 empty] | M | M | A04AV216 | A04AV216-00003
A04AV217-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 217 | Metal Louvered Fence Single Gate | DU | Self-Standing Type w/ Steel Frame | [8 empty] | 50 | w/ Frame, Fixing Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AV217 | A04AV217-00001
A04AV217-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 217 | Metal Louvered Fence Single Gate | EE | Self-Standing Type w/ Galv. Steel Frame | [8 empty] | 50 | w/ Frame, Fixing Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AV217 | A04AV217-00002
A04AV217-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 217 | Metal Louvered Fence Single Gate | EF | Self-Standing Type w/ Aluminum Frame | [8 empty] | 50 | w/ Frame, Fixing Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AV217 | A04AV217-00003
A04AV218-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 218 | Metal Louvered Fence Double Gate | DU | Self-Standing Type w/ Steel Frame | [8 empty] | 50 | w/ Frame, Fixing Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AV218 | A04AV218-00001
A04AV218-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 218 | Metal Louvered Fence Double Gate | EE | Self-Standing Type w/ Galv. Steel Frame | [8 empty] | 50 | w/ Frame, Fixing Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AV218 | A04AV218-00002
A04AV218-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 218 | Metal Louvered Fence Double Gate | EF | Self-Standing Type w/ Aluminum Frame | [8 empty] | 50 | w/ Frame, Fixing Accessories | [5 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AV218 | A04AV218-00003
A04AV219-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 219 | Steel Bollard | EG | Fixed Type | [8 empty] | 51 | w/ Paint, Concrete Fill | [5 empty] | DIA=( )mm / H=( )mm | [7 empty] | EA | EA | A04AV219 | A04AV219-00001
A04AV219-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 219 | Steel Bollard | EH | Removable Type | [8 empty] | 51 | w/ Paint, Concrete Fill | [5 empty] | DIA=( )mm / H=( )mm | [7 empty] | EA | EA | A04AV219 | A04AV219-00002
A04AV220-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 220 | Building Signage | [25 empty] | SET | SET | A04AV220 | A04AV220-00001
A04AV221-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 221 | Room Signage | [25 empty] | SET | SET | A04AV221 | A04AV221-00001
A04AV222-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 222 | Turnstile | [10 empty] | 50 | w/ Frame, Fixing Accessories | [13 empty] | SET | SET | A04AV222 | A04AV222-00001
A04AV223-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 223 | Wheel Stop | EJ | Concrete Type | [8 empty] | 52 | w/ Painting, Fixing Accessories | [13 empty] | EA | EA | A04AV223 | A04AV223-00001
A04AV223-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 223 | Wheel Stop | EK | Rubber Type | [8 empty] | 34 | w/ Fixing Accessories | [13 empty] | EA | EA | A04AV223 | A04AV223-00002
A04AV224-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 224 | Mirror | EL | Stainless Steel, Surface Mounted Type | [15 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AV224 | A04AV224-00001
A04AV225-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 225 | Mirror w/ Shelf | EL | Stainless Steel, Surface Mounted Type | [15 empty] | W x H=( )mm x ( )mm | [7 empty] | EA | EA | A04AV225 | A04AV225-00001
A04AV226-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 226 | Liquid Soap Dispensers | EL | Stainless Steel, Surface Mounted Type | [23 empty] | EA | EA | A04AV226 | A04AV226-00001
A04AV227-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 227 | Soap Dish | EL | Stainless Steel, Surface Mounted Type | [23 empty] | EA | EA | A04AV227 | A04AV227-00001
A04AV228-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 228 | Towel Bar | EL | Stainless Steel, Surface Mounted Type | [23 empty] | EA | EA | A04AV228 | A04AV228-00001
A04AV229-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 229 | Coat & Hat Hooks | EL | Stainless Steel, Surface Mounted Type | [23 empty] | EA | EA | A04AV229 | A04AV229-00001
A04AV230-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 230 | Electric Hand Dryer | EM | Surface Mounted Type | [23 empty] | EA | EA | A04AV230 | A04AV230-00001
A04AV231-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 231 | Paper Tower Dispenser | EL | Stainless Steel, Surface Mounted Type | [23 empty] | EA | EA | A04AV231 | A04AV231-00001
A04AV232-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 232 | Paper Towel Dispenser and Waste Receptacle | EN | Stainless Steel, Recessed Type | [23 empty] | EA | EA | A04AV232 | A04AV232-00001
A04AV233-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 233 | Toilet Tissue Dispenser | EL | Stainless Steel, Surface Mounted Type | [23 empty] | EA | EA | A04AV233 | A04AV233-00001
A04AV234-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 234 | Grease Traps | EP | Stainless Steel, Embedded Type | [23 empty] | EA | EA | A04AV234 | A04AV234-00001
A04AV235-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 235 | Shelves | EL | Stainless Steel, Surface Mounted Type | [23 empty] | EA | EA | A04AV235 | A04AV235-00001
A04AV236-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 236 | Shower Curtain and Curtain Rod | [25 empty] | EA | EA | A04AV236 | A04AV236-00001
A04AV237-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 237 | Waste Bin | BT | Stainless Steel | [21 empty] | Capa.=( )L |  | EA | EA | A04AV237 | A04AV237-00001
A04AV238-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 238 | Toilet Seat-Cover Dispenser | EL | Stainless Steel, Surface Mounted Type | [23 empty] | EA | EA | A04AV238 | A04AV238-00001
A04AV239-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 239 | Ash Tray | EL | Stainless Steel, Surface Mounted Type | [23 empty] | EA | EA | A04AV239 | A04AV239-00001
A04AV240-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 240 | Urinal Partition | [25 empty] | EA | EA | A04AV240 | A04AV240-00001
A04AV241-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 241 | Septic Tank | EQ | FRP Type | [8 empty] | 53 | Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work |  |  | 79 | 10 People≤Capa.<50 People | [7 empty] | Capa.=( )People |  | EA | EA | A04AV241 | A04AV241-00001
A04AV241-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 241 | Septic Tank | EQ | FRP Type | [8 empty] | 53 | Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work |  |  | 80 | 50 People≤Capa.<100 People | [7 empty] | Capa.=( )People |  | EA | EA | A04AV241 | A04AV241-00002
A04AV241-00003 | AR | A04 | Finishing Work | AV | Misc. Work | 241 | Septic Tank | EQ | FRP Type | [8 empty] | 53 | Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work |  |  | 81 | 100 People≤Capa.<150 People | [7 empty] | Capa.=( )People |  | EA | EA | A04AV241 | A04AV241-00003
A04AV241-00004 | AR | A04 | Finishing Work | AV | Misc. Work | 241 | Septic Tank | EQ | FRP Type | [8 empty] | 53 | Including Excatvation, Installation, Backfilling and Any Other Works to Complete the Work |  |  | 82 | 150 People≤Capa. | [7 empty] | Capa.=( )People |  | EA | EA | A04AV241 | A04AV241-00004
A04AV242-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 242 | Feature Water Wall | ER | w/ Water Circulation System, Accessories | [23 empty] | M2 | M2 | A04AV242 | A04AV242-00001
A04AV243-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 243 | Urinal Sill | [10 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [5 empty] | THK=( )mm / W=( )mm | [7 empty] | M | M | A04AV243 | A04AV243-00001
A04AV244-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 244 | Marble Washstand | [10 empty] | 27 | w/ Mortar Bond Coat or Adhesive | [5 empty] | THK=( )mm / W=( )mm | [7 empty] | M | M | A04AV244 | A04AV244-00001
A04AV245-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 245 | Column Guard | [25 empty] | EA | EA | A04AV245 | A04AV245-00001
A04AV246-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 246 | Non Slip Nosing | ES | Adhesive Vinyl/Rubber Type | [23 empty] | M | M | A04AV246 | A04AV246-00001
A04AV246-00002 | AR | A04 | Finishing Work | AV | Misc. Work | 246 | Non Slip Nosing | ET | Adhesive PVC Type | [23 empty] | M | M | A04AV246 | A04AV246-00002
A04AV247-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 247 | Flashing Cover for Opening | [10 empty] | 34 | w/ Fixing Accessories | [13 empty] | M2 | M2 | A04AV247 | A04AV247-00001
A04AV248-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 248 | Interlocking Block | [10 empty] | 54 | w/ Sand Bedding | [13 empty] | M2 | M2 | A04AV248 | A04AV248-00001
A04AV249-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 249 | Plant Box | [17 empty] | Size=( )mm x ( )mm | [7 empty] | EA | EA | A04AV249 | A04AV249-00001
A04AV311-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 311 | PVC Pipe | [17 empty] | DIA=( )mm | [7 empty] | M | M | A04AV311 | A04AV311-00001
A04AV312-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 312 | Catch Basin (Ready-made) | [17 empty] | W x L x H=( )mm x ( )mm x ( )mm | [7 empty] | EA | EA | A04AV312 | A04AV312-00001
A04AV313-00001 | AR | A04 | Finishing Work | AV | Misc. Work | 313 | Safety Rope System | [8 empty] | 15 | for Roof | 58 | w/ Rope, Supporting Frame, Accessories | [13 empty] | M | M | A04AV313 | A04AV313-00001
A04AW250-00001 | AR | A04 | Finishing Work | AW | Landscaping | 250 | Detail Design | EU | Comply with local condition | [23 empty] | Lot | Lot | A04AW250 | A04AW250-00001
A04AW251-00001 | AR | A04 | Finishing Work | AW | Landscaping | 251 | Soft Landscaping | EV | w/ Irrigation System | [8 empty] | 55 | Supply and Install Work w/ All Items to Complete the Work | [13 empty] | M2 | M2 | A04AW251 | A04AW251-00001
A04AW251-00002 | AR | A04 | Finishing Work | AW | Landscaping | 251 | Soft Landscaping | EW | w/o Irrigation System | [8 empty] | 55 | Supply and Install Work w/ All Items to Complete the Work | [13 empty] | M2 | M2 | A04AW251 | A04AW251-00002
A04AW252-00001 | AR | A04 | Finishing Work | AW | Landscaping | 252 | Hard Landscaping | FA | Interlocking Paving Block w/ Sand Bedding | [23 empty] | M2 | M2 | A04AW252 | A04AW252-00001
A04AW252-00002 | AR | A04 | Finishing Work | AW | Landscaping | 252 | Hard Landscaping | FB | Kerbstone | [23 empty] | M2 | M | A04AW252 | A04AW252-00002
A04AW252-00003 | AR | A04 | Finishing Work | AW | Landscaping | 252 | Hard Landscaping | FC | Bench | [23 empty] | M2 | EA | A04AW252 | A04AW252-00003
A04BA253-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 253 | Automatic Counter Top Tea/Coffee Machine | [25 empty] | EA | EA | A04BA253 | A04BA253-00001
A04BA254-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 254 | Benches | [25 empty] | EA | EA | A04BA254 | A04BA254-00001
A04BA255-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 255 | Bicycle/ Tricycle Cart Stand | [25 empty] | EA | EA | A04BA255 | A04BA255-00001
A04BA256-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 256 | Printer | [25 empty] | EA | EA | A04BA256 | A04BA256-00001
A04BA257-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 257 | Bed | [25 empty] | EA | EA | A04BA257 | A04BA257-00001
A04BA258-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 258 | Chairs | [25 empty] | EA | EA | A04BA258 | A04BA258-00001
A04BA259-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 259 | Cloak-Stand | [25 empty] | EA | EA | A04BA259 | A04BA259-00001
A04BA260-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 260 | Desk | [25 empty] | EA | EA | A04BA260 | A04BA260-00001
A04BA261-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 261 | Desk Lamp | [25 empty] | EA | EA | A04BA261 | A04BA261-00001
A04BA262-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 262 | Desk Top Computer & Monitor | [25 empty] | EA | EA | A04BA262 | A04BA262-00001
A04BA263-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 263 | Dining Chair | [25 empty] | EA | EA | A04BA263 | A04BA263-00001
A04BA264-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 264 | Dining Table | [25 empty] | EA | EA | A04BA264 | A04BA264-00001
A04BA265-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 265 | Hanger | [25 empty] | EA | EA | A04BA265 | A04BA265-00001
A04BA266-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 266 | Executive Chair | [25 empty] | EA | EA | A04BA266 | A04BA266-00001
A04BA267-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 267 | Filing Drawers | [25 empty] | EA | EA | A04BA267 | A04BA267-00001
A04BA268-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 268 | Full Height Locker | [25 empty] | EA | EA | A04BA268 | A04BA268-00001
A04BA269-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 269 | Half Height Locker | [25 empty] | EA | EA | A04BA269 | A04BA269-00001
A04BA270-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 270 | Hot Plate | [25 empty] | EA | EA | A04BA270 | A04BA270-00001
A04BA271-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 271 | Information Board | [25 empty] | EA | EA | A04BA271 | A04BA271-00001
A04BA272-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 272 | Key Cabinet | [25 empty] | EA | EA | A04BA272 | A04BA272-00001
A04BA273-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 273 | Kitchen Sink | [25 empty] | EA | EA | A04BA273 | A04BA273-00001
A04BA274-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 274 | Kitchen Unit | [25 empty] | LOT | LOT | A04BA274 | A04BA274-00001
A04BA275-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 275 | Metal Cabinet | [25 empty] | EA | EA | A04BA275 | A04BA275-00001
A04BA276-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 276 | Microwave Oven | [25 empty] | EA | EA | A04BA276 | A04BA276-00001
A04BA277-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 277 | Office Partition | [25 empty] | LOT | LOT | A04BA277 | A04BA277-00001
A04BA278-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 278 | Printer Table | [25 empty] | EA | EA | A04BA278 | A04BA278-00001
A04BA279-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 279 | Quartz Clock | [25 empty] | EA | EA | A04BA279 | A04BA279-00001
A04BA280-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 280 | Reception Counter | [25 empty] | EA | EA | A04BA280 | A04BA280-00001
A04BA281-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 281 | Refrigerator | [25 empty] | EA | EA | A04BA281 | A04BA281-00001
A04BA282-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 282 | Side Chair | [25 empty] | EA | EA | A04BA282 | A04BA282-00001
A04BA283-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 283 | Sofa | [25 empty] | EA | EA | A04BA283 | A04BA283-00001
A04BA284-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 284 | Storage Cabinets(Bookcase) | [25 empty] | EA | EA | A04BA284 | A04BA284-00001
A04BA285-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 285 | Strip Curtain | [25 empty] | EA | EA | A04BA285 | A04BA285-00001
A04BA286-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 286 | Table | [25 empty] | EA | EA | A04BA286 | A04BA286-00001
A04BA287-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 287 | Tall Storage Cupboard | [25 empty] | EA | EA | A04BA287 | A04BA287-00001
A04BA288-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 288 | Umbrella's Holder | [25 empty] | EA | EA | A04BA288 | A04BA288-00001
A04BA289-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 289 | Visitors Chairs | [25 empty] | EA | EA | A04BA289 | A04BA289-00001
A04BA290-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 290 | Wall Cupboard | [25 empty] | EA | EA | A04BA290 | A04BA290-00001
A04BA291-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 291 | Washing Unit | [25 empty] | LOT | LOT | A04BA291 | A04BA291-00001
A04BA292-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 292 | Water Cooler | [25 empty] | EA | EA | A04BA292 | A04BA292-00001
A04BA293-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 293 | White Board | [25 empty] | EA | EA | A04BA293 | A04BA293-00001
A04BA294-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 294 | Rack | [25 empty] | EA | EA | A04BA294 | A04BA294-00001
A04BA295-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 295 | Medicine Cabinet | [25 empty] | EA | EA | A04BA295 | A04BA295-00001
A04BA296-00001 | AR | A04 | Finishing Work | BA | Furniture Installation | 296 | Others | [25 empty] | EA | EA | A04BA296 | A04BA296-00001
A04BD308-00001 | AR | A04 | Finishing Work | BD | Work for Ergonomic/Sustainable Design | 308 | Ergonomic Designed Area | [8 empty] | 29 | for Floor | [15 empty] | M2 | M2 | A04BD308 | A04BD308-00001
A04BD308-00002 | AR | A04 | Finishing Work | BD | Work for Ergonomic/Sustainable Design | 308 | Ergonomic Designed Area | [8 empty] | 08 | for Wall | [15 empty] | M2 | M2 | A04BD308 | A04BD308-00002
A04BD308-00003 | AR | A04 | Finishing Work | BD | Work for Ergonomic/Sustainable Design | 308 | Ergonomic Designed Area | [8 empty] | 30 | for Ceiling | [15 empty] | M2 | M2 | A04BD308 | A04BD308-00003
A04BD309-00001 | AR | A04 | Finishing Work | BD | Work for Ergonomic/Sustainable Design | 309 | Sustainable Designed Area | [25 empty] | M2 | M2 | A04BD309 | A04BD309-00001
A05ZZ199-00001 | AR | A05 | Cladding Work | ZZ | - | 199 | Single Metal Sheet | CV | Stainless Steel Sheet | [6 empty] | 08 | for Wall | 47 | w/ Accessories, Flashing | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ199 | A05ZZ199-00001
A05ZZ199-00002 | AR | A05 | Cladding Work | ZZ | - | 199 | Single Metal Sheet | CV | Stainless Steel Sheet | [6 empty] | 15 | for Roof | 47 | w/ Accessories, Flashing | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ199 | A05ZZ199-00002
A05ZZ199-00003 | AR | A05 | Cladding Work | ZZ | - | 199 | Single Metal Sheet | CW | Corrugated Aluminum Sheet | [6 empty] | 08 | for Wall | 47 | w/ Accessories, Flashing | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ199 | A05ZZ199-00003
A05ZZ199-00004 | AR | A05 | Cladding Work | ZZ | - | 199 | Single Metal Sheet | CW | Corrugated Aluminum Sheet | [6 empty] | 15 | for Roof | 47 | w/ Accessories, Flashing | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ199 | A05ZZ199-00004
A05ZZ199-00005 | AR | A05 | Cladding Work | ZZ | - | 199 | Single Metal Sheet | DA | Corrugated Galvanized Steel Sheet | [6 empty] | 08 | for Wall | 47 | w/ Accessories, Flashing | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ199 | A05ZZ199-00005
A05ZZ199-00006 | AR | A05 | Cladding Work | ZZ | - | 199 | Single Metal Sheet | DA | Corrugated Galvanized Steel Sheet | [6 empty] | 15 | for Roof | 47 | w/ Accessories, Flashing | [5 empty] | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ199 | A05ZZ199-00006
A05ZZ200-00001 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00001
A05ZZ200-00002 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00002
A05ZZ200-00003 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00003
A05ZZ200-00004 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00004
A05ZZ200-00005 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00005
A05ZZ200-00006 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00006
A05ZZ200-00007 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00007
A05ZZ200-00008 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00008
A05ZZ200-00009 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00009
A05ZZ200-00010 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00010
A05ZZ200-00011 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00011
A05ZZ200-00012 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00012
A05ZZ200-00013 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00013
A05ZZ200-00014 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00014
A05ZZ200-00015 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00015
A05ZZ200-00016 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00016
A05ZZ200-00017 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00017
A05ZZ200-00018 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00018
A05ZZ200-00019 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00019
A05ZZ200-00020 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00020
A05ZZ200-00021 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00021
A05ZZ200-00022 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00022
A05ZZ200-00023 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00023
A05ZZ200-00024 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00024
A05ZZ200-00025 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00025
A05ZZ200-00026 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00026
A05ZZ200-00027 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00027
A05ZZ200-00028 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00028
A05ZZ200-00029 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00029
A05ZZ200-00030 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00030
A05ZZ200-00031 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00031
A05ZZ200-00032 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00032
A05ZZ200-00033 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00033
A05ZZ200-00034 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00034
A05ZZ200-00035 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00035
A05ZZ200-00036 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00036
A05ZZ200-00037 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00037
A05ZZ200-00038 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00038
A05ZZ200-00039 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00039
A05ZZ200-00040 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DC | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00040
A05ZZ200-00041 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00041
A05ZZ200-00042 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00042
A05ZZ200-00043 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00043
A05ZZ200-00044 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00044
A05ZZ200-00045 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00045
A05ZZ200-00046 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00046
A05ZZ200-00047 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00047
A05ZZ200-00048 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00048
A05ZZ200-00049 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00049
A05ZZ200-00050 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00050
A05ZZ200-00051 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00051
A05ZZ200-00052 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00052
A05ZZ200-00053 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00053
A05ZZ200-00054 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00054
A05ZZ200-00055 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00055
A05ZZ200-00056 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00056
A05ZZ200-00057 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00057
A05ZZ200-00058 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00058
A05ZZ200-00059 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00059
A05ZZ200-00060 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00060
A05ZZ200-00061 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00061
A05ZZ200-00062 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00062
A05ZZ200-00063 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00063
A05ZZ200-00064 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00064
A05ZZ200-00065 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00065
A05ZZ200-00066 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00066
A05ZZ200-00067 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00067
A05ZZ200-00068 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00068
A05ZZ200-00069 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00069
A05ZZ200-00070 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00070
A05ZZ200-00071 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00071
A05ZZ200-00072 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00072
A05ZZ200-00073 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00073
A05ZZ200-00074 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00074
A05ZZ200-00075 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00075
A05ZZ200-00076 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00076
A05ZZ200-00077 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00077
A05ZZ200-00078 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00078
A05ZZ200-00079 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00079
A05ZZ200-00080 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FE | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00080
A05ZZ200-00081 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00081
A05ZZ200-00082 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00082
A05ZZ200-00083 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00083
A05ZZ200-00084 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00084
A05ZZ200-00085 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00085
A05ZZ200-00086 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00086
A05ZZ200-00087 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00087
A05ZZ200-00088 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FF | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00088
A05ZZ200-00089 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00089
A05ZZ200-00090 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00090
A05ZZ200-00091 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00091
A05ZZ200-00092 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00092
A05ZZ200-00093 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00093
A05ZZ200-00094 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00094
A05ZZ200-00095 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00095
A05ZZ200-00096 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | FG | Corrugated Aluminum Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00096
A05ZZ200-00097 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00097
A05ZZ200-00098 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00098
A05ZZ200-00099 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00099
A05ZZ200-00100 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00100
A05ZZ200-00101 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00101
A05ZZ200-00102 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00102
A05ZZ200-00103 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00103
A05ZZ200-00104 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00104
A05ZZ200-00105 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00105
A05ZZ200-00106 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00106
A05ZZ200-00107 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00107
A05ZZ200-00108 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00108
A05ZZ200-00109 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00109
A05ZZ200-00110 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00110
A05ZZ200-00111 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00111
A05ZZ200-00112 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00112
A05ZZ200-00113 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00113
A05ZZ200-00114 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00114
A05ZZ200-00115 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00115
A05ZZ200-00116 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00116
A05ZZ200-00117 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00117
A05ZZ200-00118 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00118
A05ZZ200-00119 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00119
A05ZZ200-00120 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 03 | Mineral Wool (Rock Wool) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00120
A05ZZ200-00121 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00121
A05ZZ200-00122 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00122
A05ZZ200-00123 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00123
A05ZZ200-00124 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00124
A05ZZ200-00125 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00125
A05ZZ200-00126 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00126
A05ZZ200-00127 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00127
A05ZZ200-00128 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DE | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: N/A |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00128
A05ZZ200-00129 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00129
A05ZZ200-00130 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00130
A05ZZ200-00131 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00131
A05ZZ200-00132 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00132
A05ZZ200-00133 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00133
A05ZZ200-00134 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00134
A05ZZ200-00135 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00135
A05ZZ200-00136 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DF | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 1-hr |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00136
A05ZZ200-00137 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00137
A05ZZ200-00138 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00138
A05ZZ200-00139 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00139
A05ZZ200-00140 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00140
A05ZZ200-00141 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 32 | 50mm≤THK<70mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00141
A05ZZ200-00142 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 33 | 70mm≤THK<100mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00142
A05ZZ200-00143 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 34 | 100mm≤THK<150mm |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00143
A05ZZ200-00144 | AR | A05 | Cladding Work | ZZ | - | 200 | Sandwich Panel | DG | Stainless Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs |  |  |  |  | 04 | Glass Wool (Fiberglass) | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  | 35 | 150mm≤THK |  | THK=( )mm | [7 empty] | M2 | M2 | A05ZZ200 | A05ZZ200-00144
A05ZZ201-00001 | AR | A05 | Cladding Work | ZZ | - | 201 | FRP Translucent Panel w/ Accessories | [8 empty] | 08 | for Wall | 32 | w/ Accessories | [13 empty] | M2 | M2 | A05ZZ201 | A05ZZ201-00001
A05ZZ201-00002 | AR | A05 | Cladding Work | ZZ | - | 201 | FRP Translucent Panel w/ Accessories | [8 empty] | 15 | for Roof | 32 | w/ Accessories | [13 empty] | M2 | M2 | A05ZZ201 | A05ZZ201-00002
A05ZZ202-00001 | AR | A05 | Cladding Work | ZZ | - | 202 | Glass Panel | DH | Straight Type | [8 empty] | 48 | w/ Frame, Accessories | [13 empty] | M2 | M2 | A05ZZ202 | A05ZZ202-00001
A05ZZ202-00002 | AR | A05 | Cladding Work | ZZ | - | 202 | Glass Panel | DJ | Curved Type | [8 empty] | 48 | w/ Frame, Accessories | [13 empty] | M2 | M2 | A05ZZ202 | A05ZZ202-00002
A05ZZ203-00001 | AR | A05 | Cladding Work | ZZ | - | 203 | Fabric Roof | DK | Fabric Type | [6 empty] | 16 | for Car Parking Shelter | 32 | w/ Accessories | [13 empty] | M2 | M2 | A05ZZ203 | A05ZZ203-00001
A05ZZ204-00001 | AR | A05 | Cladding Work | ZZ | - | 204 | Gutter | DL | Galvanized Steel Eave Gutter w/ Coating | [8 empty] | 32 | w/ Accessories | [5 empty] | THK=( )mm | [7 empty] | M | M | A05ZZ204 | A05ZZ204-00001
A05ZZ204-00002 | AR | A05 | Cladding Work | ZZ | - | 204 | Gutter | DM | Galvanized Steel Valley Gutter w/ Coating | [8 empty] | 32 | w/ Accessories | [5 empty] | THK=( )mm | [7 empty] | M | M | A05ZZ204 | A05ZZ204-00002
A05ZZ204-00003 | AR | A05 | Cladding Work | ZZ | - | 204 | Gutter | DN | Aluminum Eave Gutter w/ Coating | [8 empty] | 32 | w/ Accessories | [5 empty] | THK=( )mm | [7 empty] | M | M | A05ZZ204 | A05ZZ204-00003
A05ZZ204-00004 | AR | A05 | Cladding Work | ZZ | - | 204 | Gutter | DP | Aluminum Valley Gutter w/ Coating | [8 empty] | 32 | w/ Accessories | [5 empty] | THK=( )mm | [7 empty] | M | M | A05ZZ204 | A05ZZ204-00004
A06BB297-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 297 | Demolition Work of Concrete Structure | [8 empty] | 18 | for Foundation & Structure(Reinforced) Demoliton | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | M3 | M3 | A06BB297 | A06BB297-00001
A06BB298-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 298 | Cutting and Breaking Reinforced Conc. | [8 empty] | 19 | for Floor Openings | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | M2 | M2 | A06BB298 | A06BB298-00001
A06BB298-00002 | AR | A06 | Demolition Work | BB | Revamping Work | 298 | Cutting and Breaking Reinforced Conc. | [8 empty] | 20 | for Wall Openings | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | M2 | M2 | A06BB298 | A06BB298-00002
A06BB299-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 299 | Demolition Work of Masonry | [8 empty] | 21 | for Masonry Wall incl. Plastering, Any Type of Lining and etc. | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | M2 | M2 | A06BB299 | A06BB299-00001
A06BB300-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 300 | Demolition Work of Roof Waterproofing System | [8 empty] | 22 | for Roof Waterproofing System incl. Conc. Tile, Conc. Screed for Protection, Waterproofing Membrane, Rigid Insulation and etc. | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | M2 | M2 | A06BB300 | A06BB300-00001
A06BB301-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 301 | Demolition Work of Finishing Material | [8 empty] | 23 | for Existing Floor Finish incl. Flooring Tile, Mortar Bed and etc. | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | M2 | M2 | A06BB301 | A06BB301-00001
A06BB301-00002 | AR | A06 | Demolition Work | BB | Revamping Work | 301 | Demolition Work of Finishing Material | [8 empty] | 24 | for Existing Wall Finish incl. Wall Tile, Plastering and etc. | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | M2 | M2 | A06BB301 | A06BB301-00002
A06BB301-00003 | AR | A06 | Demolition Work | BB | Revamping Work | 301 | Demolition Work of Finishing Material | [8 empty] | 25 | for Existing False Ceiling System incl. Any Material of False Ceiling System | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | M2 | M2 | A06BB301 | A06BB301-00003
A06BB302-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 302 | Demolition Work of Door | [10 empty] | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | EA | EA | A06BB302 | A06BB302-00001
A06BB303-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 303 | Demolition Work of Window | [10 empty] | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | EA | EA | A06BB303 | A06BB303-00001
A06BB304-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 304 | Demolition Work of Cladding | [8 empty] | 26 | for Existing Roof Cladding | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | M2 | M2 | A06BB304 | A06BB304-00001
A06BB304-00002 | AR | A06 | Demolition Work | BB | Revamping Work | 304 | Demolition Work of Cladding | [8 empty] | 27 | for Existing Wall Cladding | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | M2 | M2 | A06BB304 | A06BB304-00002
A06BB305-00001 | AR | A06 | Demolition Work | BB | Revamping Work | 305 | Demolition Work of Fence & Gates | [10 empty] | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | M2 | M2 | A06BB305 | A06BB305-00001
A06BC306-00001 | AR | A06 | Demolition Work | BC | Demolition Work | 306 | Demolition Work of RC Structure Building | [8 empty] | 28 | for All Structural and Architectural Components Below and Above Ground Level | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | LOT | LOT | A06BC306 | A06BC306-00001
A06BC307-00001 | AR | A06 | Demolition Work | BC | Demolition Work | 307 | Demolition Work of Steel Structure Shelter | [8 empty] | 28 | for All Structural and Architectural Components Below and Above Ground Level | 56 | Including Scaffolding, Strutting, Disposal and Any Work to Complete The Work | [13 empty] | LOT | LOT | A06BC307 | A06BC307-00001
F00ZZ000-00001 | FP | F00 | FP-Dummy | ZZ | - | 000 | - | [25 empty] | LOT | LOT | F00ZZ000 | F00ZZ000-00001
F01AA000-00001 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 01 | 0.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F01AA000 | F01AA000-00001
F01AA000-00002 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 02 | 1 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F01AA000 | F01AA000-00002
F01AA000-00003 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 03 | 1.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F01AA000 | F01AA000-00003
F01AA000-00004 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 04 | 2 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F01AA000 | F01AA000-00004
F01AA000-00005 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 05 | 2.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F01AA000 | F01AA000-00005
F01AA000-00006 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 06 | 3 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F01AA000 | F01AA000-00006
F01AA000-00007 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 07 | 3.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F01AA000 | F01AA000-00007
F01AA000-00008 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 08 | 4 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F01AA000 | F01AA000-00008
F01AA000-00009 | FP | F01 | Building/Shelter Fire Proofing Work | AA | Dense Concrete | 000 | - | 09 | Others (UL1709 rating) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F01AA000 | F01AA000-00009
F01AB000-00001 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 01 | 0.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F01AB000 | F01AB000-00001
F01AB000-00002 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 02 | 1 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F01AB000 | F01AB000-00002
F01AB000-00003 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 03 | 1.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F01AB000 | F01AB000-00003
F01AB000-00004 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 04 | 2 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F01AB000 | F01AB000-00004
F01AB000-00005 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 05 | 2.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F01AB000 | F01AB000-00005
F01AB000-00006 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 06 | 3 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F01AB000 | F01AB000-00006
F01AB000-00007 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 07 | 3.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F01AB000 | F01AB000-00007
F01AB000-00008 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 08 | 4 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F01AB000 | F01AB000-00008
F01AB000-00009 | FP | F01 | Building/Shelter Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 09 | Others (UL1709 rating) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F01AB000 | F01AB000-00009
F01AC000-00001 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 01 | 0.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00001
F01AC000-00002 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 02 | 1 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00002
F01AC000-00003 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 03 | 1.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00003
F01AC000-00004 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 04 | 2 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00004
F01AC000-00005 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 05 | 2.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00005
F01AC000-00006 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 06 | 3 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00006
F01AC000-00007 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 07 | 3.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00007
F01AC000-00008 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 08 | 4 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00008
F01AC000-00009 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 10 | 0.5 hr. rating (UL 263) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00009
F01AC000-00010 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 11 | 1 hr. rating (UL 263) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00010
F01AC000-00011 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 12 | 1.5 hr. rating (UL 263) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00011
F01AC000-00012 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 13 | 2 hr. rating (UL 263) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00012
F01AC000-00013 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 14 | 2.5 hr. rating (UL 263) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00013
F01AC000-00014 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 15 | 3 hr. rating (UL 263) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00014
F01AC000-00015 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 16 | 3.5 hr. rating (UL 263) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00015
F01AC000-00016 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 17 | 4 hr. rating (UL 263) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00016
F01AC000-00017 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 18 | Others (UL263 rating) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00017
F01AC000-00018 | FP | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 09 | Others (UL1709 rating) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AC000 | F01AC000-00018
F01AD000-00001 | FP | F01 | Building/Shelter Fire Proofing Work | AD | Top Coat for Cementitious Fire Proofing | 000 | - | [16 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F01AD000 | F01AD000-00001
F02AA000-00001 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AA | Dense Concrete | 000 | - | 01 | 0.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F02AA000 | F02AA000-00001
F02AA000-00002 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AA | Dense Concrete | 000 | - | 02 | 1 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F02AA000 | F02AA000-00002
F02AA000-00003 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AA | Dense Concrete | 000 | - | 03 | 1.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F02AA000 | F02AA000-00003
F02AA000-00004 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AA | Dense Concrete | 000 | - | 04 | 2 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F02AA000 | F02AA000-00004
F02AA000-00005 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AA | Dense Concrete | 000 | - | 05 | 2.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F02AA000 | F02AA000-00005
F02AA000-00006 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AA | Dense Concrete | 000 | - | 06 | 3 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F02AA000 | F02AA000-00006
F02AA000-00007 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AA | Dense Concrete | 000 | - | 07 | 3.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F02AA000 | F02AA000-00007
F02AA000-00008 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AA | Dense Concrete | 000 | - | 08 | 4 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F02AA000 | F02AA000-00008
F02AA000-00009 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AA | Dense Concrete | 000 | - | 09 | Others (UL1709 rating) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F02AA000 | F02AA000-00009
F02AB000-00001 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 01 | 0.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F02AB000 | F02AB000-00001
F02AB000-00002 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 02 | 1 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F02AB000 | F02AB000-00002
F02AB000-00003 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 03 | 1.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F02AB000 | F02AB000-00003
F02AB000-00004 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 04 | 2 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F02AB000 | F02AB000-00004
F02AB000-00005 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 05 | 2.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F02AB000 | F02AB000-00005
F02AB000-00006 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 06 | 3 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F02AB000 | F02AB000-00006
F02AB000-00007 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 07 | 3.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F02AB000 | F02AB000-00007
F02AB000-00008 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 08 | 4 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F02AB000 | F02AB000-00008
F02AB000-00009 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 09 | Others (UL1709 rating) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F02AB000 | F02AB000-00009
F02AC000-00001 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 01 | 0.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F02AC000 | F02AC000-00001
F02AC000-00002 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 02 | 1 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F02AC000 | F02AC000-00002
F02AC000-00003 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 03 | 1.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F02AC000 | F02AC000-00003
F02AC000-00004 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 04 | 2 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F02AC000 | F02AC000-00004
F02AC000-00005 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 05 | 2.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F02AC000 | F02AC000-00005
F02AC000-00006 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 06 | 3 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F02AC000 | F02AC000-00006
F02AC000-00007 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 07 | 3.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F02AC000 | F02AC000-00007
F02AC000-00008 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 08 | 4 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F02AC000 | F02AC000-00008
F02AC000-00009 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AC | Intumescent Coating Type | 000 | - | 09 | Others (UL1709 rating) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F02AC000 | F02AC000-00009
F02AD000-00001 | FP | F02 | Pipe Rack/Equipment Steel Structure Fire Proofing Work | AD | Top Coat for Cementitious Fire Proofing | 000 | - | [16 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F02AD000 | F02AD000-00001
F03AA000-00001 | FP | F03 | Equipment Fire Proofing Work | AA | Dense Concrete | 000 | - | 01 | 0.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F03AA000 | F03AA000-00001
F03AA000-00002 | FP | F03 | Equipment Fire Proofing Work | AA | Dense Concrete | 000 | - | 02 | 1 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F03AA000 | F03AA000-00002
F03AA000-00003 | FP | F03 | Equipment Fire Proofing Work | AA | Dense Concrete | 000 | - | 03 | 1.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F03AA000 | F03AA000-00003
F03AA000-00004 | FP | F03 | Equipment Fire Proofing Work | AA | Dense Concrete | 000 | - | 04 | 2 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F03AA000 | F03AA000-00004
F03AA000-00005 | FP | F03 | Equipment Fire Proofing Work | AA | Dense Concrete | 000 | - | 05 | 2.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F03AA000 | F03AA000-00005
F03AA000-00006 | FP | F03 | Equipment Fire Proofing Work | AA | Dense Concrete | 000 | - | 06 | 3 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F03AA000 | F03AA000-00006
F03AA000-00007 | FP | F03 | Equipment Fire Proofing Work | AA | Dense Concrete | 000 | - | 07 | 3.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F03AA000 | F03AA000-00007
F03AA000-00008 | FP | F03 | Equipment Fire Proofing Work | AA | Dense Concrete | 000 | - | 08 | 4 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F03AA000 | F03AA000-00008
F03AA000-00009 | FP | F03 | Equipment Fire Proofing Work | AA | Dense Concrete | 000 | - | 09 | Others (UL1709 rating) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M3 | M3 | F03AA000 | F03AA000-00009
F03AB000-00001 | FP | F03 | Equipment Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 01 | 0.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F03AB000 | F03AB000-00001
F03AB000-00002 | FP | F03 | Equipment Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 02 | 1 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F03AB000 | F03AB000-00002
F03AB000-00003 | FP | F03 | Equipment Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 03 | 1.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F03AB000 | F03AB000-00003
F03AB000-00004 | FP | F03 | Equipment Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 04 | 2 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F03AB000 | F03AB000-00004
F03AB000-00005 | FP | F03 | Equipment Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 05 | 2.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F03AB000 | F03AB000-00005
F03AB000-00006 | FP | F03 | Equipment Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 06 | 3 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F03AB000 | F03AB000-00006
F03AB000-00007 | FP | F03 | Equipment Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 07 | 3.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F03AB000 | F03AB000-00007
F03AB000-00008 | FP | F03 | Equipment Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 08 | 4 hr. rating (UL 1709) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F03AB000 | F03AB000-00008
F03AB000-00009 | FP | F03 | Equipment Fire Proofing Work | AB | Lightweight Cementitious | 000 | - | 09 | Others (UL1709 rating) | [14 empty] | Material: ( ) | THK=( )mm | [7 empty] | M2 | M2 | F03AB000 | F03AB000-00009
F03AD000-00001 | FP | F03 | Equipment Fire Proofing Work | AD | Top Coat for Cementitious Fire Proofing | 000 | - | [16 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F03AD000 | F03AD000-00001
F03AE000-00001 | FP | F03 | Equipment Fire Proofing Work | AE | Epoxy Based Intumescent Coating Type | 000 | - | 01 | 0.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F03AE000 | F03AE000-00001
F03AE000-00002 | FP | F03 | Equipment Fire Proofing Work | AE | Epoxy Based Intumescent Coating Type | 000 | - | 02 | 1 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F03AE000 | F03AE000-00002
F03AE000-00003 | FP | F03 | Equipment Fire Proofing Work | AE | Epoxy Based Intumescent Coating Type | 000 | - | 03 | 1.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F03AE000 | F03AE000-00003
F03AE000-00004 | FP | F03 | Equipment Fire Proofing Work | AE | Epoxy Based Intumescent Coating Type | 000 | - | 04 | 2 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F03AE000 | F03AE000-00004
F03AE000-00005 | FP | F03 | Equipment Fire Proofing Work | AE | Epoxy Based Intumescent Coating Type | 000 | - | 05 | 2.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F03AE000 | F03AE000-00005
F03AE000-00006 | FP | F03 | Equipment Fire Proofing Work | AE | Epoxy Based Intumescent Coating Type | 000 | - | 06 | 3 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F03AE000 | F03AE000-00006
F03AE000-00007 | FP | F03 | Equipment Fire Proofing Work | AE | Epoxy Based Intumescent Coating Type | 000 | - | 07 | 3.5 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F03AE000 | F03AE000-00007
F03AE000-00008 | FP | F03 | Equipment Fire Proofing Work | AE | Epoxy Based Intumescent Coating Type | 000 | - | 08 | 4 hr. rating (UL 1709) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F03AE000 | F03AE000-00008
F03AE000-00009 | FP | F03 | Equipment Fire Proofing Work | AE | Epoxy Based Intumescent Coating Type | 000 | - | 09 | Others (UL1709 rating) | [14 empty] | Material: ( ) | DFT=( )㎛ | [7 empty] | M2 | M2 | F03AE000 | F03AE000-00009
S00ZZ000-00001 | SS | S00 | SS-Dummy | ZZ | - | 000 | - | [25 empty] | LOT | LOT | S00ZZ000 | S00ZZ000-00001
S01AA001-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 001 | Heavy Steel - Standard (Weight≥90KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AA001 | S01AA001-00001
S01AA002-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 002 | Medium Steel - Standard (90KG/M>Weight≥30KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AA002 | S01AA002-00001
S01AA003-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 003 | Light Steel - Standard (30KG/M>Weight) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AA003 | S01AA003-00001
S01AA004-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 004 | Heavy Steel - Built up (Weight≥90KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AA004 | S01AA004-00001
S01AA005-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 005 | Medium Steel - Built up (90KG/M>Weight≥30KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AA005 | S01AA005-00001
S01AA006-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 006 | Light Steel - Built up (30KG/M>Weight) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AA006 | S01AA006-00001
S01AA007-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 007 | Girth & Purlin | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AA007 | S01AA007-00001
S01AA008-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 008 | P.E.B. (Pre-Engineered Building) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AA008 | S01AA008-00001
S01AA009-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 009 | Plates - Gusset, Stiffener, ETC | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AA009 | S01AA009-00001
S01AA010-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 010 | Steel Painting/Coating | 01 | for Non-Fireproofed Steel Surface, Surface Preparation, Primer, Second & Final Coat | [18 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S01AA010 | S01AA010-00001
S01AA010-00002 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 010 | Steel Painting/Coating | 02 | for Fireproofed Steel Surface, Surface Preparation & Primer Coat | [18 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S01AA010 | S01AA010-00002
S01AA010-00003 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 010 | Steel Painting/Coating | 03 | Hot-Dip Galvanizing w/ Surface Preparation | [18 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S01AA010 | S01AA010-00003
S01AA010-00004 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 010 | Steel Painting/Coating | 04 | Hot-Dip Galvanizing w/ Surface Preparation and Additional Painting Coat | [18 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S01AA010 | S01AA010-00004
S01AA011-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 011 | High Strength Bolts&Nuts | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AA011 | S01AA011-00001
S01AA012-00001 | SS | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 012 | Common Bolts&Nuts | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AA012 | S01AA012-00001
S01AB001-00001 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 001 | Heavy Steel - Standard (Weight≥90KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AB001 | S01AB001-00001
S01AB002-00001 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 002 | Medium Steel - Standard (90KG/M>Weight≥30KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AB002 | S01AB002-00001
S01AB003-00001 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 003 | Light Steel - Standard (30KG/M>Weight) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AB003 | S01AB003-00001
S01AB004-00001 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 004 | Heavy Steel - Built up (Weight≥90KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AB004 | S01AB004-00001
S01AB005-00001 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 005 | Medium Steel - Built up (90KG/M>Weight≥30KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AB005 | S01AB005-00001
S01AB006-00001 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 006 | Light Steel - Built up (30KG/M>Weight) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AB006 | S01AB006-00001
S01AB009-00001 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 009 | Plates - Gusset, Stiffener, ETC | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AB009 | S01AB009-00001
S01AB010-00001 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 010 | Steel Painting/Coating | 01 | for Non-Fireproofed Steel Surface, Surface Preparation, Primer, Second & Final Coat | [18 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S01AB010 | S01AB010-00001
S01AB010-00002 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 010 | Steel Painting/Coating | 02 | for Fireproofed Steel Surface, Surface Preparation & Primer Coat | [18 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S01AB010 | S01AB010-00002
S01AB010-00003 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 010 | Steel Painting/Coating | 03 | Hot-Dip Galvanizing w/ Surface Preparation | [18 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S01AB010 | S01AB010-00003
S01AB010-00004 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 010 | Steel Painting/Coating | 04 | Hot-Dip Galvanizing w/ Surface Preparation and Additional Painting Coat | [18 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S01AB010 | S01AB010-00004
S01AB011-00001 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 011 | High Strength Bolts&Nuts | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AB011 | S01AB011-00001
S01AB012-00001 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 012 | Common Bolts&Nuts | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AB012 | S01AB012-00001
S01AB013-00001 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 013 | Plate for Reinforcing/Modification/Supplement (Field install) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AB013 | S01AB013-00001
S01AB014-00001 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 014 | DTI Washer | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AB014 | S01AB014-00001
S01AB016-00001 | SS | S01 | Main Steel Structure Fabrication Work | AB | Pipe Rack | 016 | Structural Steel - Standard - Others | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AB016 | S01AB016-00001
S01AD001-00001 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 001 | Heavy Steel - Standard (Weight≥90KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AD001 | S01AD001-00001
S01AD002-00001 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 002 | Medium Steel - Standard (90KG/M>Weight≥30KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AD002 | S01AD002-00001
S01AD003-00001 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 003 | Light Steel - Standard (30KG/M>Weight) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AD003 | S01AD003-00001
S01AD004-00001 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 004 | Heavy Steel - Built up (Weight≥90KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AD004 | S01AD004-00001
S01AD005-00001 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 005 | Medium Steel - Built up (90KG/M>Weight≥30KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AD005 | S01AD005-00001
S01AD006-00001 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 006 | Light Steel - Built up (30KG/M>Weight) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AD006 | S01AD006-00001
S01AD009-00001 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 009 | Plates - Gusset, Stiffener, ETC | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AD009 | S01AD009-00001
S01AD010-00001 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 010 | Steel Painting/Coating | 01 | for Non-Fireproofed Steel Surface, Surface Preparation, Primer, Second & Final Coat | [18 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S01AD010 | S01AD010-00001
S01AD010-00002 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 010 | Steel Painting/Coating | 02 | for Fireproofed Steel Surface, Surface Preparation & Primer Coat | [18 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S01AD010 | S01AD010-00002
S01AD010-00003 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 010 | Steel Painting/Coating | 03 | Hot-Dip Galvanizing w/ Surface Preparation | [18 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S01AD010 | S01AD010-00003
S01AD010-00004 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 010 | Steel Painting/Coating | 04 | Hot-Dip Galvanizing w/ Surface Preparation and Additional Painting Coat | [18 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S01AD010 | S01AD010-00004
S01AD011-00001 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 011 | High Strength Bolts&Nuts | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AD011 | S01AD011-00001
S01AD012-00001 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 012 | Common Bolts&Nuts | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AD012 | S01AD012-00001
S01AD013-00001 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 013 | Plate for Reinforcing/Modification/Supplement (Field install) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AD013 | S01AD013-00001
S01AD014-00001 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 014 | DTI Washer | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AD014 | S01AD014-00001
S01AD016-00001 | SS | S01 | Main Steel Structure Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 016 | Structural Steel - Standard - Others | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S01AD016 | S01AD016-00001
S02AA017-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 017 | Checkered/Flooring Plate | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M2 | M2 | S02AA017 | S02AA017-00001
S02AA018-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 018 | Grating | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M2 | M2 | S02AA018 | S02AA018-00001
S02AA019-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 019 | Steel Stairs | [20 empty] | Material: ( ) |  |  |  |  | M | M | S02AA019 | S02AA019-00001
S02AA020-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 020 | Steel Handrails | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S02AA020 | S02AA020-00001
S02AA021-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 021 | Steel Handrails - Removable | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S02AA021 | S02AA021-00001
S02AA022-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 022 | Stainless Steel Handrail | [23 empty] | H=( )mm |  | M | M | S02AA022 | S02AA022-00001
S02AA023-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 023 | Steel Ladder | 05 | With Cage | [18 empty] | Material: ( ) |  |  |  |  | M | M | S02AA023 | S02AA023-00001
S02AA023-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 023 | Steel Ladder | 06 | Without Cage | [18 empty] | Material: ( ) |  |  |  |  | M | M | S02AA023 | S02AA023-00002
S02AA024-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 024 | Galvanized Steel Deck Plate | [22 empty] | THK=( )mm |  |  | M2 | M2 | S02AA024 | S02AA024-00001
S02AA025-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 01 | M12 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00001
S02AA025-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 02 | M16 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00002
S02AA025-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 03 | M20 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00003
S02AA025-00004 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 04 | M22 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00004
S02AA025-00005 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 05 | M24 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00005
S02AA025-00006 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 06 | M30 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00006
S02AA025-00007 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 07 | M33 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00007
S02AA025-00008 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 08 | M36 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00008
S02AA025-00009 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 09 | M42 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00009
S02AA025-00010 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 10 | M48 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00010
S02AA025-00011 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 11 | M52 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00011
S02AA025-00012 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 12 | M56 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00012
S02AA025-00013 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 13 | M64 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00013
S02AA025-00014 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 14 | M72 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00014
S02AA025-00015 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 15 | M76 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00015
S02AA025-00016 | SS | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) |  |  | 16 | Over M76 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AA025 | S02AA025-00016
S02AB017-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 017 | Checkered/Flooring Plate | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M2 | M2 | S02AB017 | S02AB017-00001
S02AB018-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 018 | Grating | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M2 | M2 | S02AB018 | S02AB018-00001
S02AB019-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 019 | Steel Stairs | [20 empty] | Material: ( ) |  |  |  |  | M | M | S02AB019 | S02AB019-00001
S02AB020-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 020 | Steel Handrails | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S02AB020 | S02AB020-00001
S02AB021-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 021 | Steel Handrails - Removable | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S02AB021 | S02AB021-00001
S02AB022-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 022 | Stainless Steel Handrail | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S02AB022 | S02AB022-00001
S02AB023-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 023 | Steel Ladder | 05 | With Cage | [18 empty] | Material: ( ) |  |  |  |  | M | M | S02AB023 | S02AB023-00001
S02AB023-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 023 | Steel Ladder | 06 | Without Cage | [18 empty] | Material: ( ) |  |  |  |  | M | M | S02AB023 | S02AB023-00002
S02AB024-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 024 | Galvanized Steel Deck Plate | [22 empty] | THK=( )mm |  |  | M2 | M2 | S02AB024 | S02AB024-00001
S02AB025-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 01 | M12 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00001
S02AB025-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 02 | M16 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00002
S02AB025-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 03 | M20 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00003
S02AB025-00004 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 04 | M22 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00004
S02AB025-00005 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 05 | M24 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00005
S02AB025-00006 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 06 | M30 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00006
S02AB025-00007 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 07 | M33 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00007
S02AB025-00008 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 08 | M36 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00008
S02AB025-00009 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 09 | M42 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00009
S02AB025-00010 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 10 | M48 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00010
S02AB025-00011 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 11 | M52 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00011
S02AB025-00012 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 12 | M56 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00012
S02AB025-00013 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 13 | M64 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00013
S02AB025-00014 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 14 | M72 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00014
S02AB025-00015 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 15 | M76 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00015
S02AB025-00016 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 025 | Anchor Bolt (Straight Type) |  |  | 16 | Over M76 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB025 | S02AB025-00016
S02AB026-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AB | Pipe Rack | 026 | Safety Gate | [20 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AB026 | S02AB026-00001
S02AD017-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 017 | Checkered/Flooring Plate | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M2 | M2 | S02AD017 | S02AD017-00001
S02AD018-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 018 | Grating | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M2 | M2 | S02AD018 | S02AD018-00001
S02AD019-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 019 | Steel Stairs | [20 empty] | Material: ( ) |  |  |  |  | M | M | S02AD019 | S02AD019-00001
S02AD020-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 020 | Steel Handrails | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S02AD020 | S02AD020-00001
S02AD021-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 021 | Steel Handrails - Removable | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S02AD021 | S02AD021-00001
S02AD022-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 022 | Stainless Steel Handrail | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S02AD022 | S02AD022-00001
S02AD023-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 023 | Steel Ladder | 05 | With Cage | [18 empty] | Material: ( ) |  |  |  |  | M | M | S02AD023 | S02AD023-00001
S02AD023-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 023 | Steel Ladder | 06 | Without Cage | [18 empty] | Material: ( ) |  |  |  |  | M | M | S02AD023 | S02AD023-00002
S02AD024-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 024 | Galvanized Steel Deck Plate | [22 empty] | THK=( )mm |  |  | M2 | M2 | S02AD024 | S02AD024-00001
S02AD025-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 01 | M12 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00001
S02AD025-00002 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 02 | M16 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00002
S02AD025-00003 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 03 | M20 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00003
S02AD025-00004 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 04 | M22 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00004
S02AD025-00005 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 05 | M24 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00005
S02AD025-00006 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 06 | M30 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00006
S02AD025-00007 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 07 | M33 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00007
S02AD025-00008 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 08 | M36 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00008
S02AD025-00009 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 09 | M42 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00009
S02AD025-00010 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 10 | M48 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00010
S02AD025-00011 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 11 | M52 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00011
S02AD025-00012 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 12 | M56 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00012
S02AD025-00013 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 13 | M64 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00013
S02AD025-00014 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 14 | M72 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00014
S02AD025-00015 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 15 | M76 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00015
S02AD025-00016 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 025 | Anchor Bolt (Straight Type) |  |  | 16 | Over M76 | [16 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD025 | S02AD025-00016
S02AD026-00001 | SS | S02 | Miscellaneous Steel Fabrication Work | AD | Equipment Structure (Civil structure except of Piperack) | 026 | Safety Gate | [20 empty] | Material: ( ) |  |  |  |  | EA | EA | S02AD026 | S02AD026-00001
S03AA007-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 007 | Girth & Purlin | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S03AA007 | S03AA007-00001
S03AA008-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 008 | P.E.B. (Pre-Engineered Building) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S03AA008 | S03AA008-00001
S03AA027-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 027 | Heavy Steel (Weight≥90KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S03AA027 | S03AA027-00001
S03AA028-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 028 | Medium Steel (90KG/M>Weight≥30KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S03AA028 | S03AA028-00001
S03AA029-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 029 | Light Steel (30KG/M>Weight) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S03AA029 | S03AA029-00001
S03AA030-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 030 | Non-Shrink Grouting | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M3 | M3 | S03AA030 | S03AA030-00001
S03AA031-00001 | SS | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 031 | Epoxy Grouting | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M3 | M3 | S03AA031 | S03AA031-00001
S03AB013-00001 | SS | S03 | Main Steel Structure Erection Work | AB | Pipe Rack | 013 | Plate for Reinforcing/Modification/Supplement (Field install) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S03AB013 | S03AB013-00001
S03AB027-00001 | SS | S03 | Main Steel Structure Erection Work | AB | Pipe Rack | 027 | Heavy Steel (Weight≥90KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S03AB027 | S03AB027-00001
S03AB028-00001 | SS | S03 | Main Steel Structure Erection Work | AB | Pipe Rack | 028 | Medium Steel (90KG/M>Weight≥30KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S03AB028 | S03AB028-00001
S03AB029-00001 | SS | S03 | Main Steel Structure Erection Work | AB | Pipe Rack | 029 | Light Steel (30KG/M>Weight) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S03AB029 | S03AB029-00001
S03AB030-00001 | SS | S03 | Main Steel Structure Erection Work | AB | Pipe Rack | 030 | Non-Shrink Grouting | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M3 | M3 | S03AB030 | S03AB030-00001
S03AB031-00001 | SS | S03 | Main Steel Structure Erection Work | AB | Pipe Rack | 031 | Epoxy Grouting | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M3 | M3 | S03AB031 | S03AB031-00001
S03AD013-00001 | SS | S03 | Main Steel Structure Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 013 | Plate for Reinforcing/Modification/Supplement (Field install) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S03AD013 | S03AD013-00001
S03AD027-00001 | SS | S03 | Main Steel Structure Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 027 | Heavy Steel (Weight≥90KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S03AD027 | S03AD027-00001
S03AD028-00001 | SS | S03 | Main Steel Structure Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 028 | Medium Steel (90KG/M>Weight≥30KG/M) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S03AD028 | S03AD028-00001
S03AD029-00001 | SS | S03 | Main Steel Structure Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 029 | Light Steel (30KG/M>Weight) | [20 empty] | Material: ( ) |  |  |  |  | TON | TON | S03AD029 | S03AD029-00001
S03AD030-00001 | SS | S03 | Main Steel Structure Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 030 | Non-Shrink Grouting | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M3 | M3 | S03AD030 | S03AD030-00001
S03AD031-00001 | SS | S03 | Main Steel Structure Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 031 | Epoxy Grouting | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M3 | M3 | S03AD031 | S03AD031-00001
S03AE015-00001 | SS | S03 | Main Steel Structure Erection Work | AE | Structural Steel | 015 | Steel Painting | [20 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S03AE015 | S03AE015-00001
S04AA017-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 017 | Checkered/Flooring Plate | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M2 | M2 | S04AA017 | S04AA017-00001
S04AA018-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 018 | Grating | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M2 | M2 | S04AA018 | S04AA018-00001
S04AA019-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 019 | Steel Stairs | [20 empty] | Material: ( ) |  |  |  |  | M | M | S04AA019 | S04AA019-00001
S04AA020-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 020 | Steel Handrails | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S04AA020 | S04AA020-00001
S04AA021-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 021 | Steel Handrails - Removable | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S04AA021 | S04AA021-00001
S04AA022-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 022 | Stainless Steel Handrail | [23 empty] | H=( )mm |  | M | M | S04AA022 | S04AA022-00001
S04AA023-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 023 | Steel Ladder | 05 | With Cage | [18 empty] | Material: ( ) |  |  |  |  | M | M | S04AA023 | S04AA023-00001
S04AA023-00002 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 023 | Steel Ladder | 06 | Without Cage | [18 empty] | Material: ( ) |  |  |  |  | M | M | S04AA023 | S04AA023-00002
S04AA024-00001 | SS | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 024 | Galvanized Steel Deck Plate | [22 empty] | THK=( )mm |  |  | M2 | M2 | S04AA024 | S04AA024-00001
S04AB017-00001 | SS | S04 | Miscellaneous Steel Erection Work | AB | Pipe Rack | 017 | Checkered/Flooring Plate | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M2 | M2 | S04AB017 | S04AB017-00001
S04AB018-00001 | SS | S04 | Miscellaneous Steel Erection Work | AB | Pipe Rack | 018 | Grating | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M2 | M2 | S04AB018 | S04AB018-00001
S04AB019-00001 | SS | S04 | Miscellaneous Steel Erection Work | AB | Pipe Rack | 019 | Steel Stairs | [20 empty] | Material: ( ) |  |  |  |  | M | M | S04AB019 | S04AB019-00001
S04AB020-00001 | SS | S04 | Miscellaneous Steel Erection Work | AB | Pipe Rack | 020 | Steel Handrails | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S04AB020 | S04AB020-00001
S04AB021-00001 | SS | S04 | Miscellaneous Steel Erection Work | AB | Pipe Rack | 021 | Steel Handrails - Removable | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S04AB021 | S04AB021-00001
S04AB022-00001 | SS | S04 | Miscellaneous Steel Erection Work | AB | Pipe Rack | 022 | Stainless Steel Handrail | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S04AB022 | S04AB022-00001
S04AB023-00001 | SS | S04 | Miscellaneous Steel Erection Work | AB | Pipe Rack | 023 | Steel Ladder | 05 | With Cage | [18 empty] | Material: ( ) |  |  |  |  | M | M | S04AB023 | S04AB023-00001
S04AB023-00002 | SS | S04 | Miscellaneous Steel Erection Work | AB | Pipe Rack | 023 | Steel Ladder | 06 | Without Cage | [18 empty] | Material: ( ) |  |  |  |  | M | M | S04AB023 | S04AB023-00002
S04AB024-00001 | SS | S04 | Miscellaneous Steel Erection Work | AB | Pipe Rack | 024 | Galvanized Steel Deck Plate | [22 empty] | THK=( )mm |  |  | M2 | M2 | S04AB024 | S04AB024-00001
S04AB026-00001 | SS | S04 | Miscellaneous Steel Erection Work | AB | Pipe Rack | 026 | Safety Gate | [20 empty] | Material: ( ) |  |  |  |  | EA | EA | S04AB026 | S04AB026-00001
S04AD017-00001 | SS | S04 | Miscellaneous Steel Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 017 | Checkered/Flooring Plate | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M2 | M2 | S04AD017 | S04AD017-00001
S04AD018-00001 | SS | S04 | Miscellaneous Steel Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 018 | Grating | [20 empty] | Material: ( ) |  | THK=( )mm |  |  | M2 | M2 | S04AD018 | S04AD018-00001
S04AD019-00001 | SS | S04 | Miscellaneous Steel Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 019 | Steel Stairs | [20 empty] | Material: ( ) |  |  |  |  | M | M | S04AD019 | S04AD019-00001
S04AD020-00001 | SS | S04 | Miscellaneous Steel Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 020 | Steel Handrails | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S04AD020 | S04AD020-00001
S04AD021-00001 | SS | S04 | Miscellaneous Steel Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 021 | Steel Handrails - Removable | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S04AD021 | S04AD021-00001
S04AD022-00001 | SS | S04 | Miscellaneous Steel Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 022 | Stainless Steel Handrail | [20 empty] | Material: ( ) |  |  | H=( )mm |  | M | M | S04AD022 | S04AD022-00001
S04AD023-00001 | SS | S04 | Miscellaneous Steel Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 023 | Steel Ladder | 05 | With Cage | [18 empty] | Material: ( ) |  |  |  |  | M | M | S04AD023 | S04AD023-00001
S04AD023-00002 | SS | S04 | Miscellaneous Steel Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 023 | Steel Ladder | 06 | Without Cage | [18 empty] | Material: ( ) |  |  |  |  | M | M | S04AD023 | S04AD023-00002
S04AD024-00001 | SS | S04 | Miscellaneous Steel Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 024 | Galvanized Steel Deck Plate | [22 empty] | THK=( )mm |  |  | M2 | M2 | S04AD024 | S04AD024-00001
S04AD026-00001 | SS | S04 | Miscellaneous Steel Erection Work | AD | Equipment Structure (Civil structure except of Piperack) | 026 | Safety Gate | [20 empty] | Material: ( ) |  |  |  |  | EA | EA | S04AD026 | S04AD026-00001
S04AE015-00001 | SS | S04 | Miscellaneous Steel Erection Work | AE | Structural Steel | 015 | Steel Painting | [20 empty] | Material: ( ) |  |  |  |  | M2 | M2 | S04AE015 | S04AE015-00001
S05AF032-00001 | SS | S05 | Demolition Work | AF | Revamping Work (Shelter/Building) | 032 | Demolition Work of Steel for Building/Shelter | [25 empty] | TON | TON | S05AF032 | S05AF032-00001
S05AG033-00001 | SS | S05 | Demolition Work | AG | Demolition Work | 033 | Structural Steel for Piperack/ Equipment structure etc. (Civil) | [25 empty] | TON | TON | S05AG033 | S05AG033-00001
S05AG034-00001 | SS | S05 | Demolition Work | AG | Demolition Work | 034 | Miscellaneous Steel for Piperack/ Equipment structure etc. (Civil) | [25 empty] | TON | TON | S05AG034 | S05AG034-00001
S05AG035-00001 | SS | S05 | Demolition Work | AG | Demolition Work | 035 | Misc. Steel Item (bolt, plate, etc) | [25 empty] | TON | TON | S05AG035 | S05AG035-00001

## Building List
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 21 |  | 23 |  | 20 |  | 25 |  | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38
1 | [8 empty] | BUILDING LIST
2 | [8 empty] | [고창 해상 풍력] | [7 empty] | Rev.A | 2023.10.16 | [Interior Finish Schedule] | [7 empty] | [Exterior Finish Schedule]
3 | NO. | Plot Plan NO. | Building Name | Structure | Q'ty | Story | Floor | Room NO. | Room Name | Width (m) | Length (m) | Height (m) | C.H (m) | Building Area (m2) | Floor Total Area (m2) | Volume (m3) | Lifting Facility | Remark | Floor |  | Base |  | Wall |  | Ceiling |  | Ext. Wall-1 | Ext. Wall-2 | Roof.-1 | Roof.-2 | Dicipline | Dicipline Colour | Dicipline ID | Occupancy | Room KKS ID | Rotate | Adjacent Dicipline | Adjacent Room
4 | 1 |  | 154kV 제어동 | RC | 1 | 2 |  |  |  | 14 | 24 | 10 |  | 336 | 711.69 | 3479.07
5 | [6 empty] | Ground FL |  |  | 14 | 24 | 6 |  |  | 336 | 2016 | [12 empty] | Deck Slab
17 | [6 empty] | 1F | 1101 | Swichgear Room | [5 empty] | 0 |  |  |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01A | Acrylic Emulsion Paint on Fair Faced Concrete | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
16 | [6 empty] | 1F | 1102 | 소화가스실 | [5 empty] | 0 |  |  |  | F06A | Non-Slip Epoxy Paint on Steel Trowel Finish | B03 | Epoxy Paint | W01A | Acrylic Emulsion Paint on Fair Faced Concrete | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
65 | [6 empty] | 1F | 1103 | 모니터링실 | [5 empty] | 0 |  |  |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01A | Acrylic Emulsion Paint on Fair Faced Concrete | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
19 | [6 empty] | 1F | 1104 | 통신실 | [5 empty] | 0 |  |  |  | F91 | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor | B35A | Coved Vinyl Tile | W01A | Acrylic Emulsion Paint on Fair Faced Concrete | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
21 | [6 empty] | 1F | 1105 | 화장실(남) | [5 empty] | 0 |  |  |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W32D | Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar)
20 | [6 empty] | 1F | 1106 | 계단실 | [5 empty] | 0 |  |  |  | F41 | Porcelain Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01A | Acrylic Emulsion Paint on Fair Faced Concrete | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
23
5 | [6 empty] | 2nd FL |  |  | 14 | 24 | 4 |  |  | 336 | 1344 | [12 empty] | Deck Slab
17 | [6 empty] | 2F | 2101 | 사무실(탕비실, 문서고) | [5 empty] | 0 |  |  |  | F34B | Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01A | Acrylic Emulsion Paint on Fair Faced Concrete | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
16 | [6 empty] | 2F | 2102 | 대표실 | [5 empty] | 0 |  |  |  | F34B | Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01A | Acrylic Emulsion Paint on Fair Faced Concrete | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
65 | [6 empty] | 2F | 2103 | 회의실 | [5 empty] | 0 |  |  |  | F34B | Vinyl Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01A | Acrylic Emulsion Paint on Fair Faced Concrete | C95A | Suspended Acoustic Tiled Ceiling (T-Bar)
19 | [6 empty] | 2F | 2104 | 화장실(여) | [5 empty] | 0 |  |  |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W32D | Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar)
21 | [6 empty] | 2F | 2105 | 화장실(남) | [5 empty] | 0 |  |  |  | F31B | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | B32 | Coved Ceramic Tile | W32D | Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100) on Cement Plaster | C96A | Suspended Moisture Resistant Tiled Ceiling (T-Bar)
20 | [6 empty] | 2F | 2106 | 계단실 | [5 empty] | 0 |  |  |  | F41 | Porcelain Tile on Steel Trowel Finish | B35A | Coved Vinyl Tile | W01A | Acrylic Emulsion Paint on Fair Faced Concrete | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
23
5 | [6 empty] | Roof |  |  | 6.3 | 6.3 | 3 |  |  | 39.69 | 119.07 | [12 empty] | Deck Slab
20 | [6 empty] | Roof | 3101 | 계단실 | [5 empty] | 0 |  |  |  | F41 | Porcelain Tile on Steel Trowel Finish | B01 | Acrylic Emulsion Paint | W01A | Acrylic Emulsion Paint on Fair Faced Concrete | C01 | Acrylic Emulsion Paint on Fair Faced Concrete
23

## 적용 규칙
[Building List, 입찰 Tool 적용 규칙]
No. | Item | 팀 기준 | 참고 | 비고
1 | LOD100 | Room 객체만 모델링 | 모든 물량은 Room 객체의 면적비, 부피비에 따라 산정
2 | LOD200 | 1. 내부 마감 물량 : Room 객체의 정보에 따라 산출 - 수량 정보 (면적, 길이) : Room Family - WM 정보 : Room Family | - 개별 마감, 마감 복합 Family : No Modeling - Building List의 내부마감 정보 => Room Family에 반영 | No Modeling
|  | 2. 외부 마감 물량 : Roof - 수량 정보 (면적, 길이) : Room Family - WM : Room Family | - 개별 마감, 마감 복합 Family : No Modeling - Building List의 내부마감 정보 => Room Family에 반영 | No Modeling
|  | 3. 외부 마감 물량 : Wall - 수량 정보 (면적, 길이) : Room Family - WM : Room Family | - 개별 마감, 마감 복합 Family : No Modeling - Building List의 내부마감 정보 => Room Family에 반영 | No Modeling
|  | 4. 내벽 Base Material - 수량 정보 (면적, 길이) : 내벽 Family (Base Material Only) - WM : 내벽 Family (Base Material Only) | - Room Arrange에 따라 Room Family에서 내벽구간 자동 인식 - 모델링 자동, 벽체 Family 속성은 수동 지정 (RC Wall 포함) | Modeling
|  | 5. 외벽 Base Material - 수량 정보 (면적, 길이) : 외벽 Family (Base Material Only) - WM : 외벽 Family (Base Material Only) | - Room Arrange에 따라 Room Family에서 외벽구간 자동 인식 - 모델링 자동, 벽체 Family 속성은 수동 지정 (RC Wall 포함) | Modeling
|  | 6. 구조 기초 물량 - 수량 정보 (면적, 길이) : 기초 Family - WM : 기초 Family (Cat.2 &3 물량 포함) | - 기초 터파기, UG Protection 반영된 기초 Family 사용 | Modeling
|  | 7. 구조 기둥 물량 - 수량 정보 (면적, 길이) : 기둥 Family - WM : 기둥 Family (Cat.2 &3 물량 포함) | - 기둥 마감 물량은 Room Family에 의해 산출 | Modeling
|  | 8. 구조 보 물량 - 수량 정보 (면적, 길이) : 보 Family - WM : 보 Family (Cat.2 &3 물량 포함) | - 보 마감 물량은 Room Family에 의해 산출 | Modeling
|  | 9. 구조 슬라브 물량 - 수량 정보 (면적, 길이) : Floor Family - WM : Floor Family (Cat.2 &3 물량 포함) | - Roof 구체 Slab 포함 | Modeling
| Wall Base | Interior Wall의 Finish와 Base Height만큼 중복 추가 산출 - Interior Wall의 Finish 산출 면적에서 Base면적 공제 미적용

## E-Space Form
[AR] Building List (Issued)
As of 2023-10-05
No. | Unit | Project Facility Code | Building Tag | Database Code | Building Name | BD w/o BM | Building/Shelter |  |  |  |  | Green/ Brown | NOS | Size | [12 empty] | Pile Spec. | Blast Design |  |  | Fire Proofing | OHC/Hoist | Sanitary | Remark
[7 empty] | Type | Superstructure | Project WBS |  |  |  |  | Story |  | Floor |  |  | W (m) | L (m) | H (m) | Area (m2) | Area Deduction (m2) | Including Total Area (m2) | Total Area (m2) | Volume (m3) |  | Resistance/ Resilence | Pso (psi) | Duration (ms)
[14 empty] | Total | (Count) | Floor |  | Info.
1 | _ | 00.20.00 | STB | A302 | Steam Turbine Building |  | BD | ST | Building(Steel) |  |  | Green | 1 | 2 |  |  |  |  | 28 | 50 | 21 |  |  |  | 1773.41 | 12974.48 | N/A | N/A
1.1 | [14 empty] | O | Ground |  |  | 28 | 50 | 5 | 1400 |  | O
1.2 | [14 empty] | O | Mezz. |  |  | 8.5 | 43.93 | 16 | 373.41 |  | O
2 | _ | 00.20.00 | STF | A313 | Steam Turbine Foundation |  | FD | RC | Shelter |  |  | Green | 1 | 1 |  |  |  |  | 8 | 15.7 | 2 |  |  |  | 125.6 | 251.2 | N/A | N/A
2.1 | [14 empty] | O | Basement |  |  | 8 | 15.7 | 2 | 125.6 |  | O
3 | _ | 00.70.00 | CCB | A201 | Central Control & Administration Building |  | BD | RC | Building(RC) |  |  | Green | 1 | 4 |  |  |  |  | 17 | 66 | 19.7 |  |  |  | 4096 | 20462.6 | N/A | N/A
3.1 | [14 empty] | O | Ground |  |  | 17 | 52 | 5.4 | 884 |  | O
3.2 | [15 empty] | Ground |  |  | 23 | 14 | 5.4 | 322 |  | O
3.3 | [14 empty] | O | 2nd |  |  | 17 | 52 | 3 | 884 |  | O
3.4 | [14 empty] | O | 3rd |  |  | 17 | 66 | 5.5 | 1122 |  | O
3.5 | [14 empty] | O | 4th |  |  | 17 | 52 | 5.8 | 884 |  | O
4 | _ | 00.10.00 | SGB | A504 | Service Gas Building |  | BD | RS | Building(Steel) |  |  | Green | 1 | 1 |  |  |  |  | 10 | 15 | 4.9 |  |  |  | 150 | 735 | N/A | N/A
4.1 | [14 empty] | O | Ground |  |  | 10 | 15 | 4.9 | 150 |  | O
5 | _ | 00.50.00 | CDSH | A103 | Chemical Dosing Shelter for HRSG |  | OS | ST | Shelter |  |  | Green | 1 | 1 |  |  |  |  | 5 | 11 | 5 |  |  |  | 55 | 275 | N/A | N/A
5.1 | [14 empty] | O | Ground |  |  | 5 | 11 | 5 | 55 |  | O
6 | _ | 00.50.00 | CDSC | A103 | Chemical Dosing Shelter for Cooling Tower |  | OS | ST | Shelter |  |  | Green | 1 | 1 |  |  |  |  | 6 | 23 | 8 |  |  |  | 138 | 1104 | N/A | N/A
6.1 | [14 empty] | O | Ground |  |  | 6 | 23 | 8 | 138 |  | O
7 | _ | 00.21.00 | GCBS | A901 | GCB Shelter for GT |  | OS | ST | Shelter |  |  | Green | 1 | 2 |  |  |  |  | 6 | 9 | 13.5 |  |  |  | 108 | 729 | N/A | N/A
7.1 | [14 empty] | O | Platform |  |  | 6 | 9 | 9 | 54 |  | O
7.2 | [14 empty] | O | Platform |  |  | 6 | 9 | 4.5 | 54 |  | O
8 | _ | 00.50.00 | ASTS | A901 | Ammonia Storage Shelter |  | OS | ST | Shelter |  |  | Green | 1 | 1 |  |  |  |  | 7.5 | 13 | 7.5 |  |  |  | 97.5 | 731.25 | N/A | N/A
8.1 | [14 empty] | O | Ground |  |  | 7.5 | 13 | 7.5 | 97.5 |  | O
9 | _ | 00.43.00 | FGSS | A510 | Fuel Gas Supply System Shelter |  | OS | ST | Shelter |  |  | Green | 1 | 1 |  |  |  |  | 14 | 22 | 8 |  |  |  | 308 | 2464 | N/A | N/A
9.1 | [14 empty] | O | Ground |  |  | 14 | 22 | 8 | 308 |  | O
10 | _ | 00.43.00 | FGGT | A510 | Fuel Gas Supply Shelter for GT |  | OS | ST | Shelter |  |  | Green | 1 | 1 |  |  |  |  | 10 | 21 | 8 |  |  |  | 210 | 1680 | N/A | N/A
10.1 | [14 empty] | O | Ground |  |  | 10 | 21 | 8 | 210 |  | O
11 | _ | 00.10.00 | GTF | A313 | Gas Turbine Foundation |  | FD | RC | Shelter |  |  | Green | 1 | 1 |  |  |  |  | 10.8 | 31.7 | 2 |  |  |  | 301.44 | 816.3 | N/A | N/A
11.1 | [14 empty] | O | Basement |  | TG bay | 10.8 | 17.98 | 2 | 194.18 |  | O
11.2 | [15 empty] | Basement |  | Gen. bay | 7.84 | 13.68 | 3.99 | 107.25 |  | O
12 | _ | 00.21.00 | TRB | A312 | Transformer Building |  | BD | RC | Building(RC) |  |  | Green | 1 | 1 |  |  |  |  | 8.4 | 26.9 | 5.5 |  |  |  | 225.96 | 1242.78 | N/A | N/A
12.1 | [14 empty] | O | Ground |  |  | 8.4 | 26.9 | 5.5 | 225.96 |  | O
| History Memo |  |  |  |  | Building Q'ty Summary |  |  |  |  | Building Area Summary
[6 empty] | BD (Building) : |  |  |  | 4 | BD (Building) : | [5 empty] | 6245.37
[6 empty] | OS (Open Shelter) : |  |  |  | 6 | OS (Open Shelter) : | [5 empty] | 916.5
[6 empty] | PS (Partially Open Shelter) : |  |  |  | 0 | PS (Partially Open Shelter) : | [5 empty] | 0
[6 empty] | FD (Foundation) : |  |  |  | 2 | FD (Foundation) : | [5 empty] | 427.04
[6 empty] | Total : |  |  |  | 12 | Total : | [5 empty] | 7588.91

## E-Space Room List
Project : 현대오일뱅크 대산 지역열병합 발전소 건설 공사
Building : Central Control & Administration Building
Floor : Ground
Room Name | Standard Room | EA | Occupancy | Width (m) | Length (m) | C.H. or Height (m) | Area (m2) | Rate (m2/1p) | Remark | Sort No.
101 Central Control Room | Central Control Room | 1 | 0 | 13.2 | 15 | 3 | 198 | 198 | 기본 면적으로 적용함. (Serverroom 면적 포함) | 0
102 Server Room | Server Room | 1 | 0 | 6 | 0 | 0 | 0 | 0 |  | 0
103 Computer Room | Computer Room | 1 | 0 | 3.8 | 7.5 | 3 | 28.5 | 28.5 |  | 0
104 Engineering Room | Engineering Work Room | 1 | 0 | 3.8 | 7.5 | 3 | 28.5 | 28.5 |  | 0
105 Meeting Room | Meeting Room | 1 | 0 | 8 | 4 | 3 | 32 | 32 |  | 0
106 Document Library | Document Room | 1 | 0 | 8 | 7.5 | 3 | 60 | 60 |  | 0
107 Air Lock | Air Lock | 1 | 0 | 3.1 | 3.5 | 3 | 10.85 | 10.85 |  | 0
108 Lobby | Reception | 1 | 0 | 2.9 | 3.5 | 3 | 10.15 | 10.15 |  | 0
109 Corridor | Corridor | 1 | 0 | 3 | 33.35 | 3 | 100.05 | 100.05 |  | 0
110 Conference Room | Conference Room | 1 | 0 | 6 | 11.5 | 3 | 69 | 69 |  | 0
111 Canteen | Canteen (Dining Room) | 1 | 0 | 6 | 11 | 3 | 66 | 66 |  | 0
112 Rest Room(M) | Rest Room | 1 | 0 | 7.35 | 6 | 3 | 44.1 | 44.1 |  | 0
113 Rest Room(W) | Rest Room | 1 | 0 | 7 | 2.6 | 3 | 18.2 | 18.2 |  | 0
114 SFC Room | FM200 cylinder room | 1 | 0 | 3.35 | 5.4 | 5.4 | 18.09 | 18.09 |  | 0
115 F.O. Tank Room | Oil Room | 1 | 0 | 3.65 | 5.4 | 5.4 | 19.71 | 19.71 |  | 0
118 Locker room | Locker room | 1 | 0 | 7.5 | 8 | 3 | 60 | 60 |  | 0
119 Shower room | Shower room | 1 | 0 | 3.5 | 8 | 2.7 | 28 | 28 |  | 0
122 Toilet(M) | Toilet | 1 | 0 | 5.9 | 4 | 2.7 | 23.6 | 23.6 |  | 0
123 Toilet(W) | Toilet | 1 | 0 | 5.4 | 3.5 | 2.7 | 18.9 | 18.9 |  | 0
124 Toilet(UA-M) | Toilet | 1 | 0 | 4 | 2.1 | 2.7 | 8.4 | 8.4 |  | 0
125 Toilet(UA-W) | Toilet | 1 | 0 | 3.5 | 2.6 | 2.7 | 9.1 | 9.1 |  | 0
126 Stair case | Stair case | 1 | 0 | 3.65 | 9 | 5.4 | 32.85 | 32.85 |  | 0
Area Validation
[6 empty] | Total Room Area (m2, A) : |  | 884
Total Floor Area (m2, B) :
[6 empty] | Deviation (m2, B-A) : |  | -884