## Int Finish Style
# B칼럼에는 노란색 행을 제외하면 콜론( : ) 이 들어가서는 안됨
팀 표준 Style Name & Numbering - Interior Finish (Floor, Skirt, Wall, Ceiling)
* 동일 Finish Material 의 두께, Size, 높이가 다른 경우 => 별도 구분 않함.
※ Finish Style Schedule - |  | (기본 입력된 정보)
※ Finish Schedule - |  | (설계자의 설계 추가 입력 정보) |  | 실제 적용 두께, Size
Room Family - 객체 Family 적용 기준
기준 | Room Family |  |  |  | 1. Interial Finish Schedule 도면 작성과 일치 되도록 작성
2. 내부마감물량은 Room Family에서 산출
객체 Family, Room Family 구분
Case 1 : Paint
Case 2 : Screed, Plaster
Case 3 : Tile
Case 4 : Raised Floor, Suspended Ceiling
Floor Finish: | [11 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
기준 | Interior Finish Schedule 도면상에서 Base Material - Finish의 분류 기준 |  |  |  | 하기표의 Style No, Floor Finish Style Name, Base Material 분류 적용
| Floor Finish 의 Family 반영 |  |  |  | 하기표의 분류에서 Base Material을 제외한 Floor Finish만 Room Family에 반영
| Floor Finish 물량 산출 기준 |  |  |  | Room Family에서 산출
| Tile + Screed 적용 기준 |  |  |  | Toilt, Shower 등 Drain을 위한 Slope이 필요한 경우 (Tile 자체 WM에 Mortar Bond Coat or Adhesive 포함)
| Hardener위 Epoxy 기준 ? |  |  |  | Hardener위 Epoxy 작업 어려움
| Epoxy Paint / Epoxy Based Sealer / Epoxy Lining 기준 ? |  |  |  | 두께 : Epoxy Paint < Epoxy Coating < Self-Leveling Epoxy
# | Floor Finish Style No | Floor Finish Style Name | Floor Base Material | BIM Family 구성 Case | Floor-Base Material-1 | Floor-Base Material-2 | Floor-Base Material-3 | Floor-Base Material-4 | Floor-Base Material-5 | Floor Finish-1 | Floor Finish-2 | Floor Finish Remark
| (Key Name) | (Interior Finish Schedule - Finish 도면 표기) | (Interior Finish Schedule - Base Material 도면 표기) |  | Floor Family-1 |  | Floor Family-2 |  |  | Room Family -Floor
[5 empty] | BM | BM | BM | BM | No BM | BM | BM
Painting | F01 | Acrylic Emulsion Paint | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Acrylic Emulsion Paint
| F02 | Water Emulsion Paint | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Water Emulsion Paint
| F03 | Acid Resistant Paint | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Acid/Alkaline Resistant Paint
| F04 | Oil Based Paint | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Oil Based Paint
| F05 | Anti-Dust Paint | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Anti-Dust Paint
| F06A | Non-Slip Epoxy Paint | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Epoxy Paint |  | *WM 기준 확인 필요 Epoxy Paint (용제형, 0.1mm 이하) : epoxy resin + polyamine hardener(경화제)
| F06B | Non-Slip Epoxy Paint | Concrete Slab / Screed | Case 2 | Concrete Slab |  | Screed |  |  | Epoxy Paint |  | *WM 기준 확인 필요 Epoxy Paint (용제형, 0.1mm 이하) : epoxy resin + polyamine hardener(경화제)
| F07A | Epoxy Based Sealer | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Epoxy Based Sealer |  | *WM 기준 확인 필요 Epoxy Coating (무용제형, 3mm 전후), : epoxy resin + polyamine hardener(경화제)
| F07B | Epoxy Coating | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Epoxy Based Sealer |  | *WM 기준 확인 필요 Epoxy Coating (무용제형, 3mm 전후), : epoxy resin + polyamine hardener(경화제)
| F07C | Epoxy Screed and Seal Coat | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Epoxy Based Sealer |  | *WM 기준 확인 필요 Epoxy Screed (Mortar 5~20mm), : epoxy resin mortar+ polyamine hardener
| F08 | Heavy Duty Self-Leveling Epoxy | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Epoxy Lining |  | 5mm Self-Leveling Epoxy Floors
| F09 | Road Marker Paint | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Road Marker Paint
| F10 | White Strips for Parking Place | Paving | Case 1 | Paving |  |  |  |  | White Strips for Parking Place
| F11 | Non-Slip Chemical Resistant Epoxy Paint | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Chemical Resistant Paint
[5 empty] | Floor Family-1 |  | Floor Family-2 |  |  | Room Family -Floor
[5 empty] | BM | BM | BM | BM | No BM | BM | BM
Tile | F31A | Non-Slip Unglazed Ceramic Tile | Concrete Slab / Steel Trowel Finish | Case 3 | Concrete Slab | Steel Trowel Finish |  |  | Ceramic Tile | Ceramic Tile |  | *WM : Bonding용 Mortar은 Tile에 포함 *Slope 용 Screed만 별도 구분 (Concrete 바닥 단차 발생하는 경우 Only)
| F31B | Non-Slip Unglazed Ceramic Tile | Concrete Slab / Screed / Liquid Waterproofing | Case 3 | Concrete Slab |  | Screed | Liquid Waterproofing | Ceramic Tile | Ceramic Tile
| F31C | Non-Slip Unglazed Ceramic Tile | Concrete Slab / Screed / Liquid Waterproof Membrane | Case 3 | Concrete Slab |  | Screed | Waterproof Membrane | Ceramic Tile | Ceramic Tile
| F32A | Acid Resistant Ceramic Tile | Concrete Slab / Steel Trowel Finish | Case 3 | Concrete Slab | Steel Trowel Finish |  |  | Acid/Alkaline Resistant Tile | Acid/Alkaline Resistant Tile |  | *WM : Bonding용 Mortar은 Tile에 포함 *Slope 용 Screed만 별도 구분 (Concrete 바닥 단차 발생하는 경우 Only)
| F32B | Acid Resistant Ceramic Tile | Concrete Slab / Screed / Liquid Waterproofing | Case 3 | Concrete Slab |  | Screed | Liquid Waterproofing | Acid/Alkaline Resistant Tile | Acid/Alkaline Resistant Tile
| F33 | Terrazzo Tile | Concrete Slab / Steel Trowel Finish | Case 3 | Concrete Slab | Steel Trowel Finish |  |  | Terrazzo Tile | Terrazzo Tile |  | *WM : Bonding용 Mortar은 Tile에 포함 *Slope 용 Screed만 별도 구분 (Concrete 바닥 단차 발생하는 경우 Only)
| F34A | Vinyl Tile | Concrete Slab / Steel Trowel Finish | Case 3 | Concrete Slab | Steel Trowel Finish |  |  | Vinyl Tile | Vinyl Tile
| F34B | Vinyl Tile | Concrete Slab / Screed | Case 3 | Concrete Slab |  | Screed |  | Vinyl Tile | Vinyl Tile
| F35 | Anti-Static Vinyl Tile | Concrete Slab / Steel Trowel Finish | Case 3 | Concrete Slab | Steel Trowel Finish |  |  | Anti-Static Vinyl Tile | Anti-Static Vinyl Tile
| F36 | Granite Tile | Concrete Slab / Steel Trowel Finish | Case 3 | Concrete Slab | Steel Trowel Finish |  |  | Granite Tile | Granite Tile
| F37 | Marble Tile | Concrete Slab / Steel Trowel Finish | Case 3 | Concrete Slab | Steel Trowel Finish |  |  | Marble Tile | Marble Tile
| F38 | Stone Tile | Concrete Slab / Steel Trowel Finish | Case 3 | Concrete Slab | Steel Trowel Finish |  |  | Stone Tile | Stone Tile
| F39 | Concrete Tile | Concrete Slab / Steel Trowel Finish | Case 3 | Concrete Slab | Steel Trowel Finish |  |  | Concrete Tile | Concrete Tile
| F40 | Mosaic Tile | Concrete Slab / Steel Trowel Finish | Case 3 | Concrete Slab | Steel Trowel Finish |  |  | Mosaic Tile | Mosaic Tile
| F41 | Porcelain Tile | Concrete Slab / Steel Trowel Finish | Case 3 | Concrete Slab | Steel Trowel Finish |  |  | Porcelain Tile | Porcelain Tile
| F42 | Rubber Tile | Concrete Slab / Steel Trowel Finish | Case 3 | Concrete Slab | Steel Trowel Finish |  |  | Rubber Tile | Rubber Tile
| F43 | Carpet Tile | Concrete Slab / Steel Trowel Finish | Case 3 | Concrete Slab | Steel Trowel Finish |  |  | Concrete Tile | Carpet Tile
[5 empty] | Floor Family-1 |  | Floor Family-2 |  |  | Room Family -Floor
[5 empty] | BM | BM | BM | BM | No BM | BM | BM
Hardener | F51 | Steel Trowel Finish | Concrete Slab | Case 1 | Concrete Slab | Steel Trowel Finish
| F52 | Brushed(Broom) Finish | Concrete Slab | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Brushed(Broom) Finish
| F53A | Hardener Finish(Powder Type) | Concrete Slab | Case 1 | Concrete Slab |  |  |  |  | Hardener Finish(Powder Type) |  | Hardener Finish(Powder Type)은 Steel Trowel Finish작업을 포함.
| F53B | Epoxy Paint on Hardener Finish(Powder Type) | Concrete Slab | Case 1 | Concrete Slab |  |  |  |  | Hardener Finish(Powder Type) | Epoxy Paint | Hardener Finish(Powder Type)은 Steel Trowel Finish작업을 포함.
| F54A | Hardener Finish(Liquid Type) | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Hardener Finish(Liquid Type)
| F54B | Non-Slip Epoxy Paint with Epoxy Hardener | Concrete Slab / Steel Trowel Finish | Case 1 | Concrete Slab | Steel Trowel Finish |  |  |  | Hardener Finish(Liquid Type) | Epoxy Paint
[5 empty] | Floor Family-1 |  | Floor Family-2 |  |  | Room Family -Floor
[5 empty] | BM | BM | BM | BM | No BM | BM | BM
Mat | F71 | Carpet | (기존 Floor Finish) | 별도 Family | Carpet | [6 empty] | * 기존 Floor Finsh 위에 Mat 의 설치면적 만큼 별도의 Family 적용
| F72 | Matwell | (기존 Floor Finish) | 별도 Family | Recess Floor Mat | [6 empty] | * 기존 Floor Finsh 위에 Mat 의 설치면적 만큼 별도의 Family 적용
| F73 | Entrance Floor Mats and Frame | (기존 Floor Finish) | 별도 Family | Entrance Floor Mats and Frame | [6 empty] | * 기존 Floor Finsh 위에 Mat 의 설치면적 만큼 별도의 Family 적용
[5 empty] | Floor Family-1 |  | Floor Family-2 |  |  | Room Family -Floor
[5 empty] | BM | BM | BM | BM | No BM | BM | BM
Raised Floor | F91 | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | Concrete Slab / Steel Trowel Finish | Case 4 | Concrete Slab | Steel Trowel Finish |  |  | Raised Floor_Anti-Static Vinyl Tile | Anti-Dust Paint | Raised Floor_Anti-Static Vinyl Tile | 600x600, H=1000
| F92 | Anti-Dust Epoxy Paint / Carpet Tile on Raised Floor | Concrete Slab / Steel Trowel Finish | Case 4 | Concrete Slab | Steel Trowel Finish |  |  | Raised Floor_Carpet Tile | Anti-Dust Paint | Raised Floor_Carpet Tile
| F93 | Anti-Dust Epoxy Paint / Marble Tile on Raised Floor | Concrete Slab / Steel Trowel Finish | Case 4 | Concrete Slab | Steel Trowel Finish |  |  | Raised Floor_Marble | Anti-Dust Paint | Raised Floor_Marble
| N.A | N.A
Skirt Finish: | [11 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
기준 | Skirting의 Base Material 표현 |  |  |  | Skirting의 Base Material은 Wall과 동일하므로 Skirting Style Name에서 생략
# | Skirt Finish Style No | Skirt Finish Style Name | Skirt Base Material | BIM Family 구성 Case | Skirt-Base Material-1 | Skirt-Base Material-2 | Skirt-Base Material-3 | Skirt-Base Material-4 | Skirt-Base Material-5 | Skirt Finish-1 | Skirt Finish-2 | Skirt Finish Remark
| (Key Name) | (Interior Finish Schedule - Finish 도면 표기) | (Interior Finish Schedule - Base Material 도면 표기) |  | Base Family-1 |  | Base Family-2 |  |  | Room Family -Base
[5 empty] | BM | BM | BM | BM | No BM | BM | BM
Painting | B01 | Acrylic Emulsion Paint | Same as Wall | Room Family (Finish Only) | [5 empty] | Acrylic Emulsion Paint
| B02 | Acid Resistant Paint | Same as Wall | Room Family (Finish Only) | [5 empty] | Acid/Alkaline Resistant Paint
| B03 | Epoxy Paint | Same as Wall | Room Family (Finish Only) | [5 empty] | Epoxy Paint |  | SACE
| B04 | Chemical Resistant Epoxy Paint | Same as Wall | Room Family (Finish Only) | [5 empty] | Chemical Resistant Paint
[5 empty] | Base Family-1 |  | Base Family-2 |  |  | Room Family -Base
[5 empty] | BM | BM | BM | BM | No BM | BM | BM
Tile | B31 | Unglazed Ceramic Tile | Same as Wall | Room Family (Finish Only) | [5 empty] | Unglazed Ceramic Tile
| B32 | Coved Ceramic Tile | Same as Wall | Room Family (Finish Only) | [5 empty] | Glazed Ceramic Tile
| B33 | Acid Resistant Ceramic Tile | Same as Wall | Room Family (Finish Only) | [5 empty] | Acid/Alkaline Resistant Tile
| B34 | Terrazzo Tile | Same as Wall | Room Family (Finish Only) | [5 empty] | Terrazzo Tile
| B35 | Coved Vinyl Tile | Same as Wall | Room Family (Finish Only) | [5 empty] | Vinyl Tile |  | Vinyl Tile = PVC Tile (polyvinyl chloride)
| B36 | Anti-Static Vinyl Tile | Same as Wall | Room Family (Finish Only) | [5 empty] | Anti-Static Vinyl Tile
| B37 | Granite Tile | Same as Wall | Room Family (Finish Only) | [5 empty] | Granite Tile
| B38 | Marble Tile | Same as Wall | Room Family (Finish Only) | [5 empty] | Marble Tile
| B39 | Stone Tile | Same as Wall | Room Family (Finish Only) | [5 empty] | Stone Tile
| B40 | Concrete Tile | Same as Wall | Room Family (Finish Only) | [5 empty] | Concrete Tile
| B41 | Porcelain Tile | Same as Wall | Room Family (Finish Only) | [5 empty] | Porcelain Tile
| B42 | Coved Rubber Skirting | Same as Wall | Room Family (Finish Only) | [5 empty] | Coved Rubber Skirting
| N.A | N.A | Same as Wall
Wall Finish: | [11 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
기준 | Tile Plastering 적용 기준? |  |  |  | Tile 자체 Work Master에 Mortar Bond Coat or Adhesive 포함 되어 있으므로 Plastering WM 미적용
Acrylic Emulsion / Water Emulsion / Latex Paint 기준
# | Wall Finish Style No | Wall Finish Style Name | Wall Base Material | BIM Family 구성 Case | Wall-Base Material-1 | Wall-Base Material-2 | Wall-Base Material-3 | Wall-Base Material-4 | Wall-Base Material-5 | Wall Finish-1 | Wall Finish-2 | Wall Finish Remark
| (Key Name) | (Interior Finish Schedule - Finish 도면 표기) | (Interior Finish Schedule - Base Material 도면 표기) |  | Wall Family-1 |  | Wall Family-2 |  |  | Room Family -Wall
[5 empty] | BM | BM | BM | BM | No BM | BM | BM
Painting | W01A | Acrylic Emulsion Paint | Concrete Wall / Fair Faced Concrete | Case 1 | Concrete Wall | (Fair Faced Concrete) |  |  |  | Acrylic Emulsion Paint
| W01B | Acrylic Emulsion Paint | Masonry Wall / Cement Plaster | Case 2 | Masonry Wall |  | Plastering |  |  | Acrylic Emulsion Paint |  | T13 Plaster
| W01C | Acrylic Emulsion Paint | Gypsum Board Wall | Case 1 | Gypsum Board Wall |  |  |  |  | Acrylic Emulsion Paint
| W02A | Water Emulsion Paint | Concrete Wall / Fair Faced Concrete | Case 1 | Concrete Wall | (Fair Faced Concrete) |  |  |  | Water Emulsion Paint
| W02B | Water Emulsion Paint | Masonry Wall / Cement Plaster | Case 2 | Masonry Wall |  | Plastering
| W02C | Water Emulsion Paint | Gypsum Board Wall | Case 1 | Gypsum Board Wall
| W03A | Latex Paint | Concrete Wall / Fair Faced Concrete | Case 1 | Concrete Wall | (Fair Faced Concrete) |  |  |  | Latex Paint
| W03B | Latex Paint | Masonry Wall / Cement Plaster | Case 2 | Masonry Wall |  | Plastering |  |  | Latex Paint
| W03C | Latex Paint | Gypsum Board Wall | Case 1 | Gypsum Board Wall
| W04A | Acid Resistant Paint | Concrete Wall / Fair Faced Concrete | Case 1 | Concrete Wall | (Fair Faced Concrete) |  |  |  | Acid/Alkaline Resistant Paint
| W04B | Acid Resistant Paint | Masonry Wall / Cement Plaster | Case 2 | Masonry Wall |  | Plastering |  |  | Acid/Alkaline Resistant Paint |  | T13 Plaster
| W04C | Acid Resistant Paint | Gypsum Board Wall | Case 1 | Gypsum Board Wall
| W05A | Epoxy Paint | Concrete Wall / Fair Faced Concrete | Case 1 | Concrete Wall | (Fair Faced Concrete) |  |  |  | Epoxy Paint
| W05B | Epoxy Paint | Masonry Wall / Cement Plaster | Case 2 | Masonry Wall |  | Plastering |  |  | Epoxy Paint
| W05C | Epoxy Paint | Gypsum Board Wall | Case 1 | Gypsum Board Wall
| W06 | Stucco Finish |  |  | Concrete Wall / Masonry Wall / Dry Wall | (Fair Faced Concrete) | Plastering |  |  | Stucco Finish
| W07 | Anti-Dust Paint |  |  | Concrete Wall / Masonry Wall / Dry Wall | (Fair Faced Concrete) | Plastering |  |  | Anti-Dust Paint
| W08 | Epoxy Based Sealer |  |  | Concrete Wall / Masonry Wall / Dry Wall | (Fair Faced Concrete) | Plastering |  |  | Epoxy Based Sealer
| W09A | Chemical Resistant Paint | Concrete Wall / Fair Faced Concrete | Case 1 | Concrete Wall | (Fair Faced Concrete) |  |  |  | Chemical Resistant Paint |  | T13 Plaster
| W09B | Chemical Resistant Paint | Masonry Wall / Cement Plaster | Case 2 | Masonry Wall |  | Plastering |  |  | Chemical Resistant Paint
| W09C | Chemical Resistant Paint | Gypsum Board Wall | Case 1 | Gypsum Board Wall |  |  |  |  | Chemical Resistant Paint
[5 empty] | Wall Family-1 |  | Wall Family-2 |  |  | Room Family -Wall
[5 empty] | BM | BM | BM | BM | No BM | BM | BM
Tile | W31A | Unglazed Ceramic Tile | Concrete Wall | Case 3 | Concrete Wall |  |  |  | Unglazed Ceramic Tile | Unglazed Ceramic Tile |  | *WM : Bonding용 Mortar은 Tile에 포함
| W31B | Unglazed Ceramic Tile | Masonry Wall | Case 3 | Masonry Wall |  |  |  | Unglazed Ceramic Tile | Unglazed Ceramic Tile
| W32A | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | Concrete Wall / Liquid Waterproofing | Case 3 | Concrete Wall |  |  | Liquid Waterproofing | Glazed Ceramic Tile | Glazed Ceramic Tile |  | Below Suspended Ceiling Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100)
| W32B | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | Masonry Wall / Liquid Waterproofing | Case 3 | Masonry Wall |  |  | Liquid Waterproofing | Glazed Ceramic Tile | Glazed Ceramic Tile |  | Below Suspended Ceiling Glazed Ceramic Tile(≤C.H+100) + Liquid Waterproofing / No Paint (>C.H+100)
| W32C | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | Concrete Wall | Case 3 | Concrete Wall |  |  | No Waterproofing | Glazed Ceramic Tile | Glazed Ceramic Tile |  | Below Suspended Ceiling Glazed Ceramic Tile(≤C.H+100) / No Paint (>C.H+100)
| W32D | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | Masonry Wall | Case 3 | Masonry Wall |  |  | No Waterproofing | Glazed Ceramic Tile | Glazed Ceramic Tile |  | Below Suspended Ceiling Glazed Ceramic Tile(≤C.H+100) / No Paint (>C.H+100)
| W32E | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | Concrete Wall / Waterproof Membrane |  | Concrete Wall |  |  | Waterproof Membrane | Glazed Ceramic Tile | Glazed Ceramic Tile |  | Below Suspended Ceiling Glazed Ceramic Tile(≤C.H+100) + Waterproofing Membrane / No Paint (>C.H+100)
| W32F | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | Masonry Wall / Waterproof Membrane |  | Masonry Wall |  |  | Waterproof Membrane | Glazed Ceramic Tile | Glazed Ceramic Tile |  | Below Suspended Ceiling Glazed Ceramic Tile(≤C.H+100) + Waterproofing Membrane / No Paint (>C.H+100)
| W33A | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | Concrete Wall / Liquid Waterproofing | Case 3 | Concrete Wall |  |  | Liquid Waterproofing | Glazed Ceramic Tile | Glazed Ceramic Tile |  | H=1200 Glazed Ceramic Tile + Liquid Waterproofing (≤1200) / Acrylic Emulsion Paint (>1200)
| W33B | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | Masonry Wall / Liquid Waterproofing | Case 3 | Masonry Wall |  |  | Liquid Waterproofing | Glazed Ceramic Tile | Glazed Ceramic Tile |  | H=1200 Glazed Ceramic Tile + Liquid Waterproofing (≤1200) / Acrylic Emulsion Paint (>1200)
| W33C | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | Concrete Wall | Case 3 | Concrete Wall |  |  | No Waterproofing | Glazed Ceramic Tile | Glazed Ceramic Tile |  | H=1200 Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200)
| W33D | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | Masonry Wall | Case 3 | Masonry Wall |  |  | No Waterproofing | Glazed Ceramic Tile | Glazed Ceramic Tile |  | H=1200 Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200)
| W33E | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | Concrete Wall / Waterproof Membrane | Case 3 | Concrete Wall |  |  | Waterproof Membrane | Glazed Ceramic Tile | Glazed Ceramic Tile |  | H=1200 Glazed Ceramic Tile + Waterproof Membrane (≤1200) / Acrylic Emulsion Paint (>1200)
| W33F | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | Masonry Wall / Waterproof Membrane | Case 3 | Masonry Wall |  |  | Waterproof Membrane | Glazed Ceramic Tile | Glazed Ceramic Tile |  | H=1200 Glazed Ceramic Tile + Waterproof Membrane (≤1200) / Acrylic Emulsion Paint (>1200)
| W34A | Glazed Ceramic Tile | Concrete Wall / Liquid Waterproofing | Case 3 | Concrete Wall |  |  | Liquid Waterproofing | Glazed Ceramic Tile | Glazed Ceramic Tile |  | No Ceiling Full Height
| W34B | Glazed Ceramic Tile | Masonry Wall / Liquid Waterproofing | Case 3 | Masonry Wall |  |  | Liquid Waterproofing | Glazed Ceramic Tile | Glazed Ceramic Tile |  | No Ceiling Full Height
| W34C | Glazed Ceramic Tile | Concrete Wall | Case 3 | Concrete Wall |  |  | No Waterproofing | Glazed Ceramic Tile | Glazed Ceramic Tile |  | No Ceiling Full Height
| W34D | Glazed Ceramic Tile | Masonry Wall | Case 3 | Masonry Wall |  |  | No Waterproofing | Glazed Ceramic Tile | Glazed Ceramic Tile |  | No Ceiling Full Height
| W34E | Glazed Ceramic Tile | Concrete Wall / Waterproof Membrane | Case 3 | Concrete Wall |  |  | Waterproof Membrane | Glazed Ceramic Tile | Glazed Ceramic Tile |  | No Ceiling Full Height
| W34F | Glazed Ceramic Tile | Masonry Wall / Waterproof Membrane | Case 3 | Masonry Wall |  |  | Waterproof Membrane | Glazed Ceramic Tile | Glazed Ceramic Tile |  | No Ceiling Full Height
| W35A | ACID Resistant Ceramic Tile (≤CH+100) / Acrylic Emulsion Paint (>CH+100) | Concrete Wall / Liquid Waterproofing | Case 3 | Concrete Wall |  |  | Liquid Waterproofing | Acid/Alkaline Resistant Tile | Acid/Alkaline Resistant Tile |  | Below Suspended Ceiling ACID Resistant Ceramic Tile (≤CH+100) / Acrylic Emulsion Paint (>CH+100)
| W35B | ACID Resistant Ceramic Tile (≤CH+100) / Acrylic Emulsion Paint (>CH+100) | Masonry Wall / Liquid Waterproofing | Case 3 | Masonry Wall |  |  | Liquid Waterproofing | Acid/Alkaline Resistant Tile | Acid/Alkaline Resistant Tile |  | Below Suspended Ceiling ACID Resistant Ceramic Tile (≤CH+100) / Acrylic Emulsion Paint (>CH+100)
| W36A | ACID Resistant Ceramic Tile | Concrete Wall / Liquid Waterproofing | Case 3 | Concrete Wall |  |  | Liquid Waterproofing | Acid/Alkaline Resistant Tile | Acid/Alkaline Resistant Tile |  | No Ceiling Full Height
| W36B | ACID Resistant Ceramic Tile | Masonry Wall / Liquid Waterproofing | Case 3 | Masonry Wall |  |  | Liquid Waterproofing | Acid/Alkaline Resistant Tile | Acid/Alkaline Resistant Tile |  | No Ceiling Full Height
| W41 | Granite Tile |  | Case 3 | Concrete Wall / Masonry Wall |  |  |  | Granite Tile | Granite Tile
| W42 | Marble Tile |  | Case 3 | Concrete Wall / Masonry Wall |  |  |  | Marble Tile | Marble Tile
| W43 | Stone Tile |  | Case 3 | Concrete Wall / Masonry Wall |  |  |  | Stone Tile | Stone Tile
| W44 | Mosaic Tile |  | Case 3 | Concrete Wall / Masonry Wall |  |  |  | Mosaic Tile | Mosaic Tile
| W45 | Acoustic Tile |  | Case 3 | Concrete Wall / Masonry Wall |  |  |  | Acoustic Tile | Acoustic Tile
| W46 | Porcelain Tile |  | Case 3 | Concrete Wall / Masonry Wall |  |  |  | Porcelain Tile | Porcelain Tile
| N.A | N.A
Ceiling Finish: | [11 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
기준
# | Ceiling Finish Style No | Ceiling Finish Style Name | Ceiling Base Material | Ceiling Finish Ref. | Ceiling-Base Material-1 | Ceiling-Base Material-2 | Ceiling-Base Material-3 | Ceiling-Base Material-4 | Ceiling-Base Material-5 | Ceiling Finish-1 | Ceiling Finish-2 | Ceiling Finish Remark
| (Key Name) | (Interior Finish Schedule - Finish 도면 표기) | (Interior Finish Schedule 도면 표기) |  | Ceiling Family-1 |  | Ceiling Family-2 |  |  | Room Family -Ceiling
[5 empty] | No BM | BM | BM | BM | No BM | BM | BM
Painting | C01 | Acrylic Emulsion Paint | Concrete Slab / Fair Faced Concrete | Room Family (Finish Only) | (Concrete Slab) |  |  |  |  | Acrylic Emulsion Paint |  | SACE
| C02 | Water Emulsion Paint | Concrete Slab / Fair Faced Concrete | Room Family (Finish Only) | (Concrete Slab) |  |  |  |  | Water Emulsion Paint
| C03 | Latex Paint | Concrete Slab / Fair Faced Concrete | Room Family (Finish Only) | (Concrete Slab) |  |  |  |  | Latex Paint
| C04 | Acid Resistant Paint | Concrete Slab / Fair Faced Concrete | Room Family (Finish Only) | (Concrete Slab) |  |  |  |  | Acid/Alkaline Resistant Paint
| C05 | Anti-Dust Paint | Concrete Slab / Fair Faced Concrete | Room Family (Finish Only) | (Concrete Slab) |  |  |  |  | Anti-Dust Paint
| C06 | Epoxy Paint | Concrete Slab / Fair Faced Concrete | Room Family (Finish Only) | (Concrete Slab) |  |  |  |  | Epoxy Paint
[5 empty] | Ceiling Family-1 |  | Ceiling Family-2 |  |  | Room Family -Ceiling
[5 empty] | No BM | No BM | BM | BM | No BM | BM | BM
System Ceiling | C91A | Suspended Fiber Board Ceiling (M-Bar) | Concrete Slab / Fair Faced Concrete | Case 4 | (Concrete Slab) | (Fair Faced Concrete) |  |  | Fiber Board Ceiling System M-bar | Fiber Board Ceiling System M-bar
| C91B | Suspended Fiber Board Ceiling (T-Bar) | Concrete Slab / Fair Faced Concrete | Case 4 | (Concrete Slab) | (Fair Faced Concrete) |  |  | Fiber Board Ceiling System T-bar | Fiber Board Ceiling System T-bar
| C92 | Suspended Gypsum Plaster Board Ceiling (M-Bar) | Concrete Slab / Fair Faced Concrete | Case 4 | (Concrete Slab) | (Fair Faced Concrete) |  |  | Gypsum Plaster Board Ceiling System | Gypsum Plaster Board Ceiling System
| C93 | Suspended Moisture Resistant Gypsum Plaster Board Ceiling (M-Bar) | Concrete Slab / Fair Faced Concrete | Case 4 | (Concrete Slab) | (Fair Faced Concrete) |  |  | Moisture Resistant Gypsum Plaster Board Ceiling System | Moisture Resistant Gypsum Plaster Board Ceiling System
| C94A | Suspended Cement Board Ceiling (M-Bar) | Concrete Slab / Fair Faced Concrete | Case 4 | (Concrete Slab) | (Fair Faced Concrete) |  |  | Cement Board Ceiling System, M-Bar | Cement Board Ceiling System, M-Bar
| C94B | Suspended Cement Board Ceiling (T-Bar) | Concrete Slab / Fair Faced Concrete | Case 4 | (Concrete Slab) | (Fair Faced Concrete) |  |  | Cement Board Ceiling System, T-Bar | Cement Board Ceiling System, T-Bar
| C95A | Suspended Acoustic Tiled Ceiling (M-Bar) | Concrete Slab / Fair Faced Concrete | Case 4 | (Concrete Slab) | (Fair Faced Concrete) |  |  | Acoustic Tiled Ceiling System (M-Bar) | Acoustic Tiled Ceiling System (M-Bar)
| C95B | Suspended Acoustic Tiled Ceiling (T-Bar) | Concrete Slab / Fair Faced Concrete | Case 4 | (Concrete Slab) | (Fair Faced Concrete) |  |  | Acoustic Tiled Ceiling System (T-Bar) | Acoustic Tiled Ceiling System (T-Bar) |  | 600x600 T Bar
| C96A | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | Concrete Slab / Fair Faced Concrete | Case 4 | (Concrete Slab) | (Fair Faced Concrete) |  |  | Moisture Resistant Tiled Ceiling System (M-Bar) | Moisture Resistant Tiled Ceiling System (M-Bar)
| C96B | Suspended Moisture Resistant Tiled Ceiling (T-Bar) | Concrete Slab / Fair Faced Concrete | Case 4 | (Concrete Slab) | (Fair Faced Concrete) |  |  | Moisture Resistant Tiled Ceiling System (T-Bar) | Moisture Resistant Tiled Ceiling System (T-Bar) |  | 600x600 T bar
| C97 | Suspended Aluminum Spandrel Ceiling (M-Bar) | Concrete Slab / Fair Faced Concrete | Case 4 | (Concrete Slab) | (Fair Faced Concrete) |  |  | Aluminum Spandrel Ceiling System (M-Bar) | Aluminum Spandrel Ceiling System (M-Bar)
| C98 | Metal Open Cell Ceiling (M-Bar) | Concrete Slab / Fair Faced Concrete | Case 4 | (Concrete Slab) | (Fair Faced Concrete) |  |  | Metal Open Cell Ceiling (T-Bar) | Metal Open Cell Ceiling (T-Bar)
| N.A | N.A

## Int Finish 사례
팀 기준 사양 : Interior Finish | [15 empty] | 프로젝트 적용 현황
* 동일 Finish Material 의 두께, Size, 높이가 다른 경우 => 별도 구분 않함.
Building | Room | Description | Floor |  |  | Base |  |  | Wall |  |  | Ceiling |  |  | Remark | Project | Building | Room | Description | Floor | Base | Wall | Ceiling | Remark
|  |  | Style No | Base Material | Finish (Style, Key Name) | Style No | Base Material | Finish (Style, Key Name) | Style No | Base Material | Finish (Style, Key Name) | Style No | Base Material | Finish (Style, Key Name)
| Office |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar)
Control Building(RC) | Shift Superintendent |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Shift Superintendent |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | OPS Shift Co-Ordinator |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | OPS Shift Co-Ordinator |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Library |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Library |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Visitor Office |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Visitor Office |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Day Shift Co-Ordinator |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Day Shift Co-Ordinator |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Relief Foreman |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Relief Foreman |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Warehouse (ST) | Office |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B31 | Same as Wall | Unglazed Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | ALOM | ALOM | Warehouse (ST) | Office |  | Unglazed Ceramic Tile on Cement Screed | Unglazed Ceramic Tile on THK.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete or THK.15 Cement Plaster | Suspended Acoustic Ceiling
Workshop(ST) | Office |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | Vung Ang | Vung Ang | Workshop(ST) | Office |  | Ceramic Tile | Ceramic Skirting | Emulsion Paint | Suspended Acoustic Mineral Panel
Trainign Center & First Aid Room | Manager Room, Office, Corridor, First Aid Room, Meeting Room |  | F33 | Concrete Slab / Steel Trowel Finish | Terrazzo Tile | B34 | Same as Wall | Terrazzo Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | ZAWA | ZAWA | Trainign Center & First Aid Room | Manager Room, Office, Corridor, First Aid Room, Meeting Room |  | Terrazzo Tile on Cement Screed | Terrazzo Tile on thk15 Cement Screed | Emulsion Paint on Thk.15 Cement Mortar | Suspended Mineral Fiber Board Panel
Control Building(RC) | Office |  | F34A | Concrete Slab / Steel Trowel Finish | Vinyl Tile | B35A | #N/A | #N/A | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Control Building(RC) | Office |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Warehouse & Workshop (RC) | Manager Office |  | F34A | Concrete Slab / Steel Trowel Finish | Vinyl Tile | B35A | #N/A | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Warehouse & Workshop (RC) | Manager Office |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Warehouse & Workshop (RC) | Office |  | F34A | Concrete Slab / Steel Trowel Finish | Vinyl Tile | B35A | #N/A | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Warehouse & Workshop (RC) | Office |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Admin & Control Building(RC) | General Office |  | F34B | Concrete Slab / Screed | Vinyl Tile | B35A | #N/A | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | RAPO | RAPO | Admin & Control Building(RC) | General Office |  | PVC Tile | Thk2 PVC Skirting on Cement Mortar (H=100) | Emulsion Paint on Thk.15 Cement Mortar | Suspended Mineral Board (CH=3150)
Admin Building | General Office |  | F34A | Concrete Slab / Steel Trowel Finish | Vinyl Tile | B35A | #N/A | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Admin Building | General Office |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Water Treatment Building | Office, Corridor |  | F41 | Concrete Slab / Steel Trowel Finish | Porcelain Tile | B41 | Same as Wall | Porcelain Tile | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | ZAWA | ZAWA | Water Treatment Building | Office, Corridor |  | Gres Pine Porcelain on Steel Trowel Finish | Gres Pine Porcelain on thk15 Cement Plaster | Emulsion Paint on Thk.15 Cement Mortar | Suspended Mineral Fiber Board Panel
Warehouse (ST) | Manager Office |  | F41 | Concrete Slab / Steel Trowel Finish | Porcelain Tile | B41 | Same as Wall | Porcelain Tile | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | ALOM | ALOM | Warehouse (ST) | Manager Office |  | Porcelain Stoneware Tile | Porcelain Stoneware Tile | Emulsion Paint | Suspended Acoustic Ceiling
Warehouse (ST) | Office |  | F41 | Concrete Slab / Steel Trowel Finish | Porcelain Tile | B41 | Same as Wall | Porcelain Tile | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | ALOM | ALOM | Warehouse (ST) | Office |  | Porcelain Stoneware Tile | Porcelain Stoneware Tile | Emulsion Paint | Suspended Acoustic Ceiling
Admin Building | Manager Office |  | F72 | (기존 Floor Finish) | Matwell | B35A | #N/A | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Admin Building | Manager Office |  | Carpet Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
CCB, Workshop Building | Office, Inspection Room, Reception Room |  | F33 | Concrete Slab / Steel Trowel Finish | Terrazzo Tile | B34 | Same as Wall | Terrazzo Tile | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | KUSU | KUSU | CCB, Workshop Building | Office, Inspection Room, Reception Room |  | Carpet Tile on thk30 Terrazzo Tile | Terrazzo Tile | Acrylic Latex Paint on thk15 Cement Plaster | Suspended Al. Strip Panel w/ thk25 Acoustic Blanket
[16 empty] | HNCC | Process Control Building | Office |  | Deco Tile on cement mortar (by Interior) | Vinyl Base (H=100) | Fabric Panel (by Interior) | Sound absorbing soft fiber board on suspended ceiling system (by Interior)
[16 empty] | HNCC | Laboratory Building | Office |  | Deco Tile on cement mortar (by Interior) | Vinyl Base (H=100) | Vinyl Paint (by Interior) | Suspended mineral fibre board ceiling system (600x600)
[16 empty] | AFEC (FEED) | Admin. and Control Bldg | Office |  | Carpet Tile | PVC Tile | Emulsion Paint | Suspended Acoustic ceiling
| Meeting Room |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar)
Control Building(RC) | Meeting Room |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Meeting Room |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Meeting Room |  | F34A | Concrete Slab / Steel Trowel Finish | Vinyl Tile | B42 | Same as Wall | Coved Rubber Skirting | W03B | Masonry Wall / Cement Plaster | Latex Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | TVEP | TVEP | Control Building(RC) | Meeting Room |  | PVC Tile w/ Adhesive on Steel Troweled Concrete Slab | Rubber Base (H=100) | Latex Paint on Thk15 Cement Plaster | Suspended Mineral Fiberboard Panel(600x600)
[16 empty] | HNCC | Process Control Building | Meeting Room |  | Carpet Tile on cement mortar (by Interior) | Vinyl Base (H=100) | Vinyl Paint (by Interior) | Sound absorbing soft fiber board on suspended ceiling system (by Interior)
| Break Room |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar)
Control Building(RC) | Break Room |  | F34A | Concrete Slab / Steel Trowel Finish | Vinyl Tile | B35A | #N/A | #N/A | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Break Room |  | Vinyl Tile on Screed | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Moisture Resistant Tiled Ceiling (600x600)
[16 empty] | HNCC | Process Control Building | Rest Room |  | Wood Tile on cement mortar (by Inrerior) | Vinyl Base (H=100) | Vinyl Paint (by Interior) | Thk9.5 gypsum board 2ply w/Vinyl paint on suspended ceiling system
[16 empty] | AFEC (FEED) | Admin. and Control Bldg | Rest/Break Room |  | Ceramic Tile | Ceramic Tile | Ceramic Tile | Suspended Acoustic ceiling
| Prayer Room |  | F72 | (기존 Floor Finish) | Matwell | B35A | #N/A | #N/A | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar)
Control Building(RC) | Prayer Room |  | F72 | (기존 Floor Finish) | Matwell | B35A | #N/A | #N/A | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Prayer Room |  | Carpet Tile on Screed | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Prayer Room |  | F72 | (기존 Floor Finish) | Matwell | B35A | #N/A | #N/A | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Control Building(RC) | Prayer Room |  | Carpet Tile on Screed | Coved Vinyl (H=100) | Acrylic Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
| Corridor |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar)
Control Building(RC) | Corridor |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Corridor |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Corridor |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Control Building(RC) | Corridor |  | Ceramic Mosaic Tile on Screed | Ceramic Tile (H=600) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Warehouse (ST) | Corridor |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B31 | Same as Wall | Unglazed Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | ALOM | ALOM | Warehouse (ST) | Corridor |  | Unglazed Ceramic Tile on Cement Screed | Unglazed Ceramic Tile on THK.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete or THK.15 Cement Plaster | Suspended Acoustic Ceiling
Substation(RC) | Corridor |  | F42 | Concrete Slab / Steel Trowel Finish | Rubber Tile | B42 | Same as Wall | Coved Rubber Skirting | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C01 | Concrete Slab / Fair Faced Concrete | Acrylic Emulsion Paint | BONE | BONE | Substation(RC) | Corridor-B |  | THK.3mm Rubber Tile on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
[16 empty] | HNCC | Process Control Building | Corridor |  | Deco Tile on cement mortar (by Interior) | Vinyl Base (H=100) | Vinyl Paint (by Interior) | Thk9.5 gypsum board 2ply w/Vinyl paint on suspended ceiling system
| Stair Case |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C01 | Concrete Slab / Fair Faced Concrete | Acrylic Emulsion Paint
Substation(RC) | Stair Case |  | F42 | Concrete Slab / Steel Trowel Finish | Rubber Tile | B42 | Same as Wall | Coved Rubber Skirting | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C01 | Concrete Slab / Fair Faced Concrete | Acrylic Emulsion Paint | BONE | BONE | Substation(RC) | Stair Case |  | THK.3mm Rubber Tile on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
Fire Station | Stair Case |  | F34A | Concrete Slab / Steel Trowel Finish | Vinyl Tile | B35 | Same as Wall | Coved Vinyl Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C01 | Concrete Slab / Fair Faced Concrete | Acrylic Emulsion Paint | KLNG | KLNG | Fire Station | Stair Case |  | Vinyl Composition Tile on Screed | - | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
[16 empty] | HNCC | Process Control Building | Corridor |  | Deco Tile on cement mortar (by Interior) | Vinyl Base (H=100) | Emulsion Paint | Emulsion Paint on Fair faced concrete
[16 empty] | AFEC | Admin. and Control Bldg | Stair |  | PVC Tile | PVC Tile | Emulsion Paint | No finish
| Air Lock Room |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | *연계된 Room마감과 연속 적용
Substation(RC) | Air Lock |  | F06A | Concrete Slab / Steel Trowel Finish | Non-Slip Epoxy Paint | B03 | Same as Wall | Epoxy Paint | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Substation(RC) | Air Lock |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Control Building(RC) | Air Lock |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Air Lock |  | Non-Slip Unglazed Ceramic Tile on Screed + Matwell | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Air Lock |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Control Building(RC) | Air Lock |  | Ceramic Mosaic Tile on Screed + Matwell | Ceramic Tile (H=600) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Substation(RC) | Air Lock Lobby |  | F42 | Concrete Slab / Steel Trowel Finish | Rubber Tile | B42 | Same as Wall | Coved Rubber Skirting | W01A | Concrete Wall / Fair Faced Concrete | Acrylic Emulsion Paint | C01 | Concrete Slab / Fair Faced Concrete | Acrylic Emulsion Paint | BONE | BONE | Substation(RC) | Air Lock Lobby |  | THK.3mm Rubber Tile on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Air Lock |  | F42 | Concrete Slab / Steel Trowel Finish | Rubber Tile | B42 | Same as Wall | Coved Rubber Skirting | W01C | Gypsum Board Wall | Acrylic Emulsion Paint | C01 | Concrete Slab / Fair Faced Concrete | Acrylic Emulsion Paint | BONE | BONE | Substation(RC) | Air Lock |  | THK. 6mm Rubber Tile (Anti Static Surface, Chemical and Slip Resistant) on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
[16 empty] | HNCC | Process Control Building | Entrance |  | Polishing Tile on cement mortar (by Interior) | Vinyl Base (H=100) | Vinyl Paint (by Interior) | Thk9.5 gypsum board 2ply w/Vinyl paint on suspended ceiling system
[16 empty] | AFEC | Admin. and Control Bldg | Entry Air Lock |  | Granite Tile | Granite Tile | Emulsion Paint | SMC Panel
| Lobby |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar)
Control Building(RC) | Reception/Waiting Area |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Reception/Waiting Area |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Lobby |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Lobby |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile (H=100) | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Admin & Control Building | Reception (Lobby) |  | F37 | Concrete Slab / Steel Trowel Finish | Marble Tile | B38 | Same as Wall | Marble Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | RAPO | RAPO | Admin & Control Building | Reception (Lobby) |  | Thk20 Marble Floor Tile | Marble Tile (H=100) | Emulsion Paint on Thk.15 Cement Mortar | Suspended Mineral Board (CH=3150)
Admin Building | Reception (Air Lock) |  | F37 | Concrete Slab / Steel Trowel Finish | Marble Tile | B38 | Same as Wall | Marble Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Admin Building | Reception (Air Lock) |  | Marble Tile on Screed | Marble Tile (H=200) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
| Locker Room |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W32A | Concrete Wall / Liquid Waterproofing | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | *바닥+벽 방수 미적용
Control Building(RC) | Locker Room |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W32A | Concrete Wall / Liquid Waterproofing | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Locker Room |  | Non-Slip Unglazed Ceramic Tile on Screed | Coved Ceramic Tile | Glazed Ceramic Tile(≤2100) / Acrylic Emulsion paint (>2100) on Cement Plaster | Suspended Moisture Resistant Tiled Ceiling (600x600)
Warehouse (ST) | Changing Room |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | B31 | Same as Wall | Unglazed Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | ALOM | ALOM | Warehouse (ST) | Changing Room |  | Unglazed Ceramic Tile on Cement Screed | Unglazed Ceramic Tile on THK.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete or THK.15 Cement Plaster | Suspended Moisture Resistant Acoustic Ceiling
Workshop(ST) | Changing Room |  | F31A | Concrete Slab / Steel Trowel Finish | Non-Slip Unglazed Ceramic Tile | N.A | Same as Wall | N.A | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | Vung Ang | Vung Ang | Workshop(ST) | Changing Room |  | Ceramic Tile on Cement Screed | - | Emulsion Paint on Fair Faced Concrete or THK.15 Cement Plaster | Suspended Acoustic Mineral Panel
Warehouse & Workshop (RC) | Locker Room |  | F34A | Concrete Slab / Steel Trowel Finish | Vinyl Tile | B35 | Same as Wall | Coved Vinyl Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C95A | Concrete Slab / Fair Faced Concrete | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Warehouse & Workshop (RC) | Locker Room |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
[16 empty] | HNCC | Process Control Building | Rest Room |  | Wood Tile on cement mortar (by Inrerior) | Vinyl Base (H=100) | Vinyl Paint (by Interior) | Thk9.5 gypsum board 2ply w/Vinyl paint on suspended ceiling system
| Shower Room |  | F31B | Concrete Slab / Screed / Liquid Waterproofing | Non-Slip Unglazed Ceramic Tile | N.A | Same as Wall | N.A | W32B | Masonry Wall / Liquid Waterproofing | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | *바닥+벽 방수 적용
Warehouse (ST) | Shower Room |  | F31C | Concrete Slab / Screed / Liquid Waterproof Membrane | Non-Slip Unglazed Ceramic Tile | N.A | Same as Wall | N.A | W32F | Masonry Wall / Waterproof Membrane | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | ALOM | ALOM | Warehouse (ST) | Shower Room |  | Unglazed Ceramic Tile on Cement Screed on Waterproof Membrane | - | Glazed Ceramic Tile on Cement Plaster on Waterproof Membrane | Suspended Moisture Resistant Acoustic Ceiling
Workshop(ST) | Shower Room |  | F31C | Concrete Slab / Screed / Liquid Waterproof Membrane | Non-Slip Unglazed Ceramic Tile | N.A | Same as Wall | N.A | W01A | Concrete Wall / Fair Faced Concrete | Acrylic Emulsion Paint | C97 | Concrete Slab / Fair Faced Concrete | Suspended Aluminum Spandrel Ceiling (M-Bar) | Vung Ang | Vung Ang | Workshop(ST) | Shower Room |  | Unglazed Ceramic Tile on Cement Screed on Waterproof Membrane | - | Emulsion Paint on Fair Faced Concrete or THK.15 Cement Plaster | Suspended AL. Panel
Warehouse & Workshop (RC) | Shower Room |  | F31B | Concrete Slab / Screed / Liquid Waterproofing | Non-Slip Unglazed Ceramic Tile | N.A | Same as Wall | N.A | W32B | Masonry Wall / Liquid Waterproofing | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | KLNG | KLNG | Warehouse & Workshop (RC) | Shower Room |  | Non-Slip Ceramic Tile on Screed + Liquid Waterproofing | - | Ceramic Tile + Liquid Waterproofing (H=1800) on Cement plaster | Suspended Acoustic Tile Ceiling (600x600, Sag and Humidity Resistant)
[16 empty] | HNCC | Process Control Building | Shower Room |  | Non-Slip Ceramic Tile on Screed w/Polyurethane Waterproofing coating (by Interior) | - | Ceramic Tile w/Polyurethane Waterproofing coating (H=2000) (by Interior) | SMC(300x300) on Suspended ceiling system (by Interior)
[16 empty] | AFEC | Admin and Control Bldg | Locker and Shower Room |  | Non-Slip Ceramic Tile | Ceramic Tile | Ceramic Tile | Suspended Moisture-Resistant Gypsumboard ceiling
| Ablution |  | F31B | Concrete Slab / Screed / Liquid Waterproofing | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W33B | Masonry Wall / Liquid Waterproofing | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | *바닥+벽 방수 적용
Control Building(RC) | Hamman/Ablutions |  | F31B | Concrete Slab / Screed / Liquid Waterproofing | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W33B | Masonry Wall / Liquid Waterproofing | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Hamman/Ablutions |  | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | Coved Ceramic Tile | Glazed Ceramic Tile(≤2100) / Acrylic Emulsion paint (>2100) on Cement Plaster | Suspended Moisture Resistant Tiled Ceiling (600x600)
Control Building(RC) | Ablution Room |  | F31B | Concrete Slab / Screed / Liquid Waterproofing | Non-Slip Unglazed Ceramic Tile | N.A | Same as Wall | N.A | W33B | Masonry Wall / Liquid Waterproofing | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | KLNG | KLNG | Control Building(RC) | Ablution Room |  | Non-Slip Ceramic Tile on Screed + Liquid Waterproofing | - | Ceramic Tile + Liquid Waterproofing (H=1200) on Cement plaster | Suspended Acoustic Tile Ceiling (600x600, Sag and Humidity Resistant)
| Toilet |  | F31B | Concrete Slab / Screed / Liquid Waterproofing | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W32D | Masonry Wall | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | *바닥만 방수 적용
Control Building(RC) | Ladies/Disabled Toilet |  | F31B | Concrete Slab / Screed / Liquid Waterproofing | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W32D | Masonry Wall | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Ladies/Disabled Toilet |  | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | Coved Ceramic Tile | Glazed Ceramic Tile(≤2100) / Acrylic Emulsion paint (>2100) on Cement Plaster | Suspended Moisture Resistant Tiled Ceiling (600x600)
Control Building(RC) | Shift Superintendent Toilet |  | F31B | Concrete Slab / Screed / Liquid Waterproofing | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W32D | Masonry Wall | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Shift Superintendent Toilet |  | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | Coved Ceramic Tile | Glazed Ceramic Tile(≤2100) / Acrylic Emulsion paint (>2100) on Cement Plaster | Suspended Moisture Resistant Tiled Ceiling (600x600)
Control Building(RC) | Toilet (M & F) |  | F31B | Concrete Slab / Screed / Liquid Waterproofing | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W33B | Masonry Wall / Liquid Waterproofing | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | KLNG | KLNG | Control Building(RC) | Toilet (M & F) |  | Non-Slip Ceramic Tile on Screed + Liquid Waterproofing | - | Ceramic Tile + Liquid Waterproofing (H=1200) on Cement plaster | Suspended Acoustic Tile Ceiling (600x600, Sag and Humidity Resistant)
Warehouse & Workshop (RC) | Toilet (M & F) |  | F31B | Concrete Slab / Screed / Liquid Waterproofing | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W33B | Masonry Wall / Liquid Waterproofing | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | KLNG | KLNG | Warehouse & Workshop (RC) | Toilet (M & F) |  | Non-Slip Ceramic Tile on Screed + Liquid Waterproofing | - | Ceramic Tile + Liquid Waterproofing (H=1200) on Cement plaster | Suspended Acoustic Tile Ceiling (600x600, Sag and Humidity Resistant)
Warehouse (ST) | Toilet |  | F31C | Concrete Slab / Screed / Liquid Waterproof Membrane | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W32B | Masonry Wall / Liquid Waterproofing | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A | Concrete Slab / Fair Faced Concrete | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | ALOM | ALOM | Warehouse (ST) | Toilet (M & F) |  | Unglazed Ceramic Tile on Cement Screed on Waterproof Membrane | - | Glazed Ceramic Tile on THK.15 Cement Plaster on Waterproof Membrane | Suspended Moisture Resistant Acoustic Ceiling
Workshop(ST) | Toilet (M & F) |  | F31C | Concrete Slab / Screed / Liquid Waterproof Membrane | Non-Slip Unglazed Ceramic Tile | B32 | Same as Wall | Coved Ceramic Tile | W01B | Masonry Wall / Cement Plaster | Acrylic Emulsion Paint | C97 | Concrete Slab / Fair Faced Concrete | Suspended Aluminum Spandrel Ceiling (M-Bar) | Vung Ang | Vung Ang | Workshop(ST) | Toilet (M & F) |  | Unglazed Ceramic Tile on Cement Screed on Waterproof Membrane | - | Emulsion Paint | Suspended AL. Panel
[16 empty] | HNCC | Process Control Building | Toilet |  | Non-Slip Ceramic Tile on Screed w/Liquid Waterproofing 2Ply (by Interior) | - | Ceramic Tile w/Liquid Waterproofing 2Ply (H=1500) (by Interior) | Thk9.5 gypsum board 2ply w/Vinyl paint on suspended ceiling system
| Janitor |  | F31B |  | Non-Slip Unglazed Ceramic Tile | B32 |  | Coved Ceramic Tile | W32A |  | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A |  | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | *바닥만 방수 적용
Control Building(RC) | Janitor |  | F31B |  | Non-Slip Unglazed Ceramic Tile | B32 |  | Coved Ceramic Tile | W32A |  | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A |  | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Janitor |  | Non-Slip Unglazed Ceramic Tile on Screed + Liquid Waterproofing | Coved Ceramic Tile | Glazed Ceramic Tile(≤2100) / Acrylic Emulsion paint (>2100) on Cement Plaster | Suspended Moisture Resistant Tiled Ceiling (600x600)
Control Building(RC) | Janitor |  | F31B |  | Non-Slip Unglazed Ceramic Tile | N.A |  | N.A | W32D |  | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A |  | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | KLNG | KLNG | Control Building(RC) | Janitor |  | Non-Slip Ceramic Tile on Screed + Liquid Waterproofing | - | Ceramic Tile + Liquid Waterproofing (H=1200) on Cement plaster | Suspended Acoustic Tile Ceiling (600x600, Sag and Humidity Resistant)
| First Aid Room |  | F31A |  | Non-Slip Unglazed Ceramic Tile | B32 |  | Coved Ceramic Tile | W32A |  | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | *바닥+벽 방수 미적용
Main Building(ST) | First Aid Room |  | F34B |  | Vinyl Tile | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | UTCC | UTCC | Main Building(ST) | First Aid Room |  | 1. THK 3 Heavy Duty PVC Tile 2. Steel Trowel Finish | PVC Skirting | Emulsion Paint on Gypsum Board 12.5mm 2 Piles | Suspended Acoustic Mineral Board
Admin Building | Emergency Treatment |  | F34B |  | Vinyl Tile | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Admin Building | Emergency Treatment |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
| Dining Room | *별도의 식당동 | F34B |  | Vinyl Tile | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar)
Canteen(RC) | Dining Room |  | F34B |  | Vinyl Tile | B42 |  | Coved Rubber Skirting | W03B |  | Latex Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | TVEP | TVEP | Canteen(RC) | Dining Room |  | PVC Tile on Steel Trowel Finish | Rubber Base (H=100) | Latex Paint on Thk15 Cement Plaster | Suspended Mineral Fiberboard Panel(600x600)
[16 empty] | HNCC | Process Control Building | Cafeteria |  | Wood Tile on cement mortar (by Inrerior) | Vinyl Base (H=100) | Vinyl Paint (by Interior) | Thk9.5 gypsum board 2Ply w/Vinyl paint on suspended ceiling system (by Interior)
[16 empty] | HNCC | Subcontractor Building | Mess Hall |  | Wood Tile on cement mortar (by Inrerior) | Vinyl Base (H=100) | Vinyl Paint (by Interior) | Thk9.5 gypsum board 2Ply w/Vinyl paint on suspended ceiling system (by Interior)
[16 empty] | AFEC (FEED) | Admin. and Control Bldg | Rest Room w/Kitchen |  | Ceramic Tile | Ceramic Tile | Ceramic Tile | Suspended Acoustic ceiling
| Cooking Room |  | F31B |  | Non-Slip Unglazed Ceramic Tile | B32 |  | Coved Ceramic Tile | W32D |  | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A |  | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | *바닥+벽 방수 적용
Canteen(RC) | Cold Food Area (Cooking Area) |  | F31C |  | Non-Slip Unglazed Ceramic Tile | B32 |  | Coved Ceramic Tile | W32H |  | #N/A | C96A |  | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | TVEP | TVEP | Canteen(RC) | Cold Food Area |  | Unglazed Ceramic Tile on Cement Screed w/ Water Proofing Mambrane |  | Glazed Ceramic Tile on Thk15 Cement Plaster w/ Water Proofing(≤1200) / Latex Paint on Cement Plaster (>1200) | Suspended Moisture Resistant Panel(600x600)
Canteen(RC) | Hot Food Area (Cooking Area) |  | F31C |  | Non-Slip Unglazed Ceramic Tile | B32 |  | Coved Ceramic Tile | W32H |  | #N/A | C96A |  | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | TVEP | TVEP | Canteen(RC) | Cold Food Area |  | Unglazed Ceramic Tile on Cement Screed w/ Water Proofing Mambrane |  | Glazed Ceramic Tile on Thk15 Cement Plaster w/ Water Proofing(≤1200) / Latex Paint on Cement Plaster (>1200) | Suspended Moisture Resistant Panel(600x600)
[16 empty] | HNCC | Subcontractor Building | Kitchen Catering room |  | Thk7 Non-Slip Ucrete Lining on Cement mortar w/Polyurethane waterpfroofing coating |  | Ceramic Tile w/Polyurethane waterpfroofing coating(H=2000) (by Interior) | SMC(300x300) on Suspended ceiling system (by Interior)
| Dish Washing Area |  | F31B |  | Non-Slip Unglazed Ceramic Tile | B32 |  | Coved Ceramic Tile | W32D |  | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C96A |  | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | *바닥+벽 방수 적용
Canteen(RC) | Dish Washing Area |  | F31C |  | Non-Slip Unglazed Ceramic Tile | B32 |  | Coved Ceramic Tile | W32H |  | #N/A | C96A |  | Suspended Moisture Resistant Tiled Ceiling (M-Bar) | TVEP | TVEP | Canteen(RC) | Dish Washing Area |  | Unglazed Ceramic Tile on Cement Screed w/ Water Proofing Mambrane |  | Glazed Ceramic Tile on Thk15 Cement Plaster w/ Water Proofing(≤1200) / Latex Paint on Cement Plaster (>1200) | Suspended Moisture Resistant Panel(600x600)
[16 empty] | HNCC | Subcontractor Building | Washing room |  | Thk7 Non-Slip Ucrete Lining on Cement mortar w/Polyurethane waterpfroofing coating |  | Ceramic Tile w/Polyurethane waterpfroofing coating(H=2000) (by Interior) | SMC(300x300) on Suspended ceiling system (by Interior)
| Food Receiving & Preparation Area |  | F31B |  | Non-Slip Unglazed Ceramic Tile | B32 |  | Coved Ceramic Tile | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | *바닥만 방수 적용
Canteen(RC) | Food Receiving & Preparation Area |  | F31C |  | Non-Slip Unglazed Ceramic Tile | B31 |  | Unglazed Ceramic Tile | W03B |  | Latex Paint | C03 |  | Latex Paint | TVEP | TVEP | Canteen(RC) | Receiving & Preparation Area |  | Unglazed Ceramic Tile on Cement Screed w/ Water Proofing Mambrane | Unglazed Ceramic Tile (H=100) | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
| Food Storage |  | F31B |  | Non-Slip Unglazed Ceramic Tile | B32 |  | Coved Ceramic Tile | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | *바닥만 방수 적용
Canteen(RC) | Food Storage |  | F31C |  | Non-Slip Unglazed Ceramic Tile | B31 |  | Unglazed Ceramic Tile | W03B |  | Latex Paint | C03 |  | Latex Paint | TVEP | TVEP | Canteen(RC) | Food Storage |  | Unglazed Ceramic Tile on Cement Screed w/ Water Proofing Mambrane | Unglazed Ceramic Tile (H=100) | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
[16 empty] | HNCC | Subcontractor Building | Storage |  | Thk7 Non-Slip Ucrete Lining on Cement mortar w/Polyurethane waterpfroofing coating |  | Ceramic Tile w/Polyurethane waterpfroofing coating(H=2000) (by Interior) | SMC(300x300) on Suspended ceiling system (by Interior)
| Store (Document) | *문서용도 | F34A |  | Vinyl Tile | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar)
Control Building(RC) | Store | 문서 | F34A |  | Vinyl Tile | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Store |  | Vinyl Tile on Screed | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Record Room |  | F34A |  | Vinyl Tile | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Control Building(RC) | Record Room |  | Vinyl Composition Tile on Screed | Coved Vinyl (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
Control Building(RC) | PPE Store | 안전장비 | F34A |  | Vinyl Tile | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | PPE Store |  | Vinyl Tile on Screed | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
| Store (Material) | *자재용도 | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
Substation(RC) | 자재보관실 |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | LECO | LECO | Substation(RC) | 자재보관실 |  | Steel Trowel Finish w/ Epoxy Paint | Epoxy Paint | Emulsion Paint on Gypsum Board | Emulsion Paint on Fair Faced Concrete
Warehouse (ST) | Storage Area |  | F07B |  | Epoxy Coating | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | ALOM | ALOM | Warehouse (ST) | Storage Area |  | Resin coating | Resin coating | Emulsion Paint (Up to FL.+1.6M) | Exposed Thermal Insulated Metal Cladding
Warehouse (ST) | Hazardous Material Store |  | F07B |  | Epoxy Coating | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | ALOM | ALOM | Warehouse (ST) | Hazardous Material Store |  | Resin coating | Resin coating | Emulsion Paint | Exposed Thermal Insulated Metal Cladding
Warehouse (ST) | Instrument Spare Part Room |  | F07B |  | Epoxy Coating | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | ALOM | ALOM | Warehouse (ST) | Instrument Spare Part Room |  | Resin coating | Resin coating | Emulsion Paint | Exposed Thermal Insulated Metal Cladding
Warehouse (ST) | Perishiable Material Room |  | F07B |  | Epoxy Coating | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | ALOM | ALOM | Warehouse (ST) | Perishiable Material Room |  | Resin coating | Resin coating | Emulsion Paint | Exposed Thermal Insulated Metal Cladding
Warehouse & Workshop (RC) | Warehouse |  | F07B |  | Epoxy Coating | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Warehouse & Workshop (RC) | Warehouse |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
Workshop(ST) | KHO Store |  | F53A |  | Hardener Finish(Powder Type) | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | Vung Ang | Vung Ang | Workshop(ST) | KHO Store |  | Hardener Finish | Epoxy Paint | Emulsion Paint | Exposed Thermal Insulated Metal Cladding
| Tool Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A
Workshop(ST) | Tool Room |  | F54A |  | Hardener Finish(Liquid Type) | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | Vung Ang | Vung Ang | Workshop(ST) | Tool Room |  | Hardener Finish | Epoxy Paint | Emulsion Paint | Exposed Thermal Insulated Metal Cladding
Warehouse & Workshop (RC) | Tool Store |  | F07B |  | Epoxy Coating | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Warehouse & Workshop (RC) | Tool Store |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
| Mechanical Workshop |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A
Workshop(ST) | Workshop |  | F54A |  | Hardener Finish(Liquid Type) | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | Vung Ang | Vung Ang | Workshop(ST) | Workshop |  | Hardener Finish | Epoxy Paint | Emulsion Paint | Exposed Thermal Insulated Metal Cladding
Warehouse (ST) | Mechanical Workshop Area |  | F06B |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | ALOM | ALOM | Warehouse (ST) | Workshop Area |  | Epoxy Paint on Cement Screed | Epoxy Paint on Fairfaced concrete or THK.15 Cement Plaster | Emulsion Paint on THK.15 Cement Plaster (Up to FL.+1.6M) | Exposed Thermal Insulated Metal Cladding
Warehouse & Workshop (RC) | Mechanical Workshop |  | F06B |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Warehouse & Workshop (RC) | Mechanical Workshop |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
| Instrument Workshop |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A
Warehouse (ST) | Instrument Workshop |  | F06B |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | ALOM | ALOM | Warehouse (ST) | Instrument Workshop |  | Epoxy Paint on Cement Screed | Epoxy Paint on Fairfaced concrete or THK.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete or THK.15 Cement Plaster | Exposed Metal Deck
Warehouse & Workshop (RC) | Instrument Workshop |  | F06B |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Warehouse & Workshop (RC) | Instrument Workshop |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
| Control Room | *계장 | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar)
Control Building(RC) | Main Control Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Main Control Room |  | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000) | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Control Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Control Building(RC) | Control Room |  | Epoxy Coating on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1030) | Coved Vinyl (H=100) | Above Raised Floor : Emulsion Paint on Thk.15 Cement Plaster Under Raised Floor : Epoxy Paint | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
[16 empty] | HNCC | Process Control Building | Control Room |  | Epoxy Paint on Steel trowel Finish + Access Floor(H=730) w/Conduction Tile | Vinyl Base (H=200) + Epoxy Paint(under access floor) | Vinyl Paint (by Interior) | Sound absorbing soft fiber board on Suspended ceiling system (by Interior)
| Control Room | *환경 | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
WTB(RC) | Control Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W03B |  | Latex Paint | C03 |  | Latex Paint | TVEP | TVEP | WTB(RC) | Control Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
Anti-Static Vinyl Tile 사례 추가
화공 Access FL 사례 추가
| Engineering Room | *CCR연속배치 | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar)
Control Building(RC) | Engineering Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Engineering Room |  | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000) | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | OTS Training Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | OTS Training Room |  | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000) | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | OTS Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Control Building(RC) | OTS Room |  | Epoxy Coating on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1030) | Coved Vinyl (H=100) | Above Raised Floor : Emulsion Paint on Thk.15 Cement Plaster Under Raised Floor : Epoxy Paint | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
[16 empty] | HNCC | Process Control Building | OTS Room |  | Epoxy Paint on Steel trowel Finish + Access Floor(H=730) w/Conduction Tile | Vinyl Base (H=200) + Epoxy Paint(under access floor) | Vinyl Paint (by Interior) | Sound absorbing soft fiber board on Suspended ceiling system (by Interior)
| Telecom Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | *CCR연속배치시 CCR과 동일 마감
Control Building(RC) | Telecoms Room |  | F34A |  | Vinyl Tile | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | SACE | SACE | Control Building(RC) | Telecoms Room |  | Vinyl Tile on Screed | Coved Vinyl H=100 | 2 Coats of Non-Conductive & Fire Retardant White Color Paint on Thk.13 Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Telecom Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | BONE | BONE | Substation(RC) | Telecom Room |  | Steel Trowel Finish w/ Dust Proof Coating (Epoxy) + 600x600 Access Floor System w/Noncombustible Laminated Plastic Finish (H=600) | Laminated Plastic Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
Control Building(RC) | Telecoms Equipment Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | SACE | SACE | Control Building(RC) | Telecoms Equipment Room |  | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000) | Coved Vinyl H=100 | 2 Coats of Non-Conductive & Fire Retardant White Color Paint on Thk.13 Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
Control Building(RC) | Communication Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Control Building(RC) | Communication Room |  | Epoxy Coating on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1030) | Coved Vinyl (H=100) | Above Raised Floor : Emulsion Paint on Thk.15 Cement Plaster Under Raised Floor : Epoxy Paint | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
[16 empty] | HNCC | Process Control Building | Communication Room |  | Epoxy Paint on Steel trowel Finish + Access Floor(H=1000) w/Conduction Tile | Vinyl Base (H=100) + Epoxy Paint(under access floor) | Emulsion Paint | Emulsion Paint on fair faced concrete
| Rack Room (CCB) |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | *CCR연속배치시 CCR과 동일 마감
Control Building(RC) | Rack Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | Rack Room |  | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000) | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | OTS Rack Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | OTS Rack Room |  | Anti-Dust Epoxy Paint on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000) | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Control Building(RC) | Server Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | KLNG | KLNG | Control Building(RC) | Server Room |  | Epoxy Coating on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1030) | Coved Vinyl (H=100) | Above Raised Floor : Emulsion Paint on Thk.15 Cement Plaster Under Raised Floor : Epoxy Paint | Suspended Acoustic Tiled Ceiling (600x600, T-Bar)
| Rack Room (Local) |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
Substation(RC) | Rack Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | LECO | LECO | Substation(RC) | Rack Room |  | Epoxy Paint + Raised Floor W/Conductive Tile | PVC Tile | Emulsion Paint on Gypsum Board | Emulsion Paint on Fair Faced Concrete
Substation(RC) | Rack Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Substation(RC) | Rack Room |  | Epoxy Coating on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1000, H=1100) | Coved Vinyl (H=100) | Above Raised Floor : Emulsion Paint on Thk.15 Cement Plaster Under Raised Floor : Epoxy Paint | Emulsion Paint on Fair Faced Concrete
Substation(RC) | Rack Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | IKAN | IKAN | Substation(RC) | Rack Room |  | Epoxy Paint + Raised Floor | PVC Tile | Arcylic Emulsion Paint on Fair Faced Concrete | Suspended Acoustic Ceiling
[16 empty] | HNCC | 154Kv Substation | Rack Room |  | Epoxy Paint on Trowel finish + Access Floor(H=1000) w/Conduction Tile | Epoxy Paint(Under Access floor)+Vinyl Base(H=100) | Emulsion Paint | Emulsion Paint on Fair Faced Concrete
[16 empty] | HNCC | Process Control Building | Panel Room |  | Epoxy Paint on Steel trowel Finish + Access Floor(H=1000) w/Conduction Tile | Vinyl Base (H=100) + Epoxy Paint(under access floor) | Emulsion Paint | Emulsion Paint on fair faced concrete
| Relay & Control Panel Room | *Local | F35 |  | Anti-Static Vinyl Tile | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
Substation(RC) | Relay & Control Panel Room |  | F42 |  | Rubber Tile | B42 |  | Coved Rubber Skirting | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | BONE | BONE | Substation(RC) | Relay & Control Panel Room |  | THK. 6mm Rubber Tile (Anti Static Surface, Chemical and Slip Resistant) on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
*Access FL사례 조사
| Electrical Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
Control Building(RC) | Electrical Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | SACE | SACE | Control Building(RC) | Electrical Room |  | Non-Slip Epoxy Paint on Screed | Epoxy Paint H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
Workshop(ST) | Electrical Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | Vung Ang | Vung Ang | Workshop(ST) | Electrical Room |  | Epoxy Paint | Epoxy Paint | Emulsion Paint | Suspended Acoustic Mineral Panel
WTB(RC) | Electrical Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W03B |  | Latex Paint | C03 |  | Latex Paint | TVEP | TVEP | WTB(RC) | Equipment Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
Warehouse & Workshop (RC) | Electrical Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Warehouse & Workshop (RC) | Electrical Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
Warehouse (ST) | Electrical Room |  | F06B |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | ALOM | ALOM | Warehouse (ST) | Electrical Room |  | Epoxy Paint on Cement Screed | Epoxy Paint on Fairfaced concrete or THK.15 Cement Plaster | Emulsion Paint on THK.15 Cement Plaster (Up to FL.+1.6M) | Exposed Metal Deck
Substation(RC) | Electrical Room |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Substation(RC) | Electrical Room |  | Epoxy Coating on Steel trowel Finish + Anti-Static Vinyl Tile on Raised Floor(600x600, H=1030) | Coved Vinyl (H=100) | Above Raised Floor : Emulsion Paint on Thk.15 Cement Plaster Under Raised Floor : Epoxy Paint | Emulsion Paint on Fair Faced Concrete
[16 empty] | HNCC | Process Control Building | Electrical Room |  | Epoxy Paint on Steel trowel Finish + Access Floor(H=1000) w/Conduction Tile | Vinyl Base (H=100) + Epoxy Paint(under access floor) | Emulsion Paint | Emulsion Paint on fair faced concrete
| Switchgear Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
Substation(RC) | Switchgear Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Substation(RC) | Switchgear Room |  | Epoxy Coating on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
Central Control Building(RC) | Switchgear Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W03B |  | Latex Paint | C03 |  | Latex Paint | TVEP | TVEP | Central Control Building(RC) | Switchgear Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Fair Faced Concrete | Latex Paint on Fair Faced Concrete
Substation(RC) | Switchgear Room |  | F42 |  | Rubber Tile | B01 |  | Acrylic Emulsion Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | IKAN | IKAN | Substation(RC) | Switchgear Room |  | Steel Trowel Finish w/ Rubber Flooring Tile (THK. 6mm) | Acrylic Emulsion Paint | Arcylic Emulsion Paint on Cement Plaster (THK. 16mm) | Arcylic Emulsion Paint
Substation(RC) | HV Switchgear Room |  | F42 |  | Rubber Tile | B42 |  | Coved Rubber Skirting | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | BONE | BONE | Substation(RC) | HV Switchgear Room |  | THK. 6mm Rubber Tile (Anti Static Surface, Chemical and Slip Resistant) on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | LV Switchgear Room |  | F42 |  | Rubber Tile | B42 |  | Coved Rubber Skirting | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | BONE | BONE | Substation(RC) | LV Switchgear Room |  | THK. 6mm Rubber Tile (Anti Static Surface, Chemical and Slip Resistant) on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
[16 empty] | HNCC | 154Kv Substation | Switchgear Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint (H=100) | Emulsion Paint | Emulsion Paint on Fair Faced Concrete
| MCC Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
Substation(RC) | MCC Room (type-1) |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | LECO | LECO | Substation(RC) | MCC Room (type-1) |  | Steel Trowel Finish w/ Epoxy Paint | Epoxy Paint | Emulsion Paint on Gypsum Board | Emulsion Paint on Fair Faced Concrete
Substation(RC) | MCC Room (type-2) |  | F91 |  | Anti-Dust Epoxy Paint / Anti-Static Vinyl Tile on Raised Floor | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | LECO | LECO | Substation(RC) | MCC Room (type-2) |  | Epoxy Paint + Raised Floor W/Conductive Tile | Epoxy Paint | Emulsion Paint on Gypsum Board | Emulsion Paint on Fair Faced Concrete
| UPS Room |  | F35 |  | Anti-Static Vinyl Tile | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
Substation(RC) | UPS Room |  | F42 |  | Rubber Tile | B42 |  | Coved Rubber Skirting | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | BONE | BONE | Substation(RC) | UPS Room |  | THK. 6mm Rubber Tile (Anti Static Surface, Chemical and Slip Resistant) on Screed | Coved Rubber Skirt | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
*Access FL사례 조사
[16 empty] | HNCC | 154Kv Substation | UPS Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint (H=100) | Emulsion Paint | Emulsion Paint on Fair Faced Concrete
| Battery Room |  | F03 |  | Acid Resistant Paint | B02 |  | Acid Resistant Paint | W04B |  | Acid Resistant Paint | C04 |  | Acid Resistant Paint | *바닥 Drain 구배 필요시 : 구체 구배
Control Building(RC) | Battery Room |  | F32 |  | #N/A | B33 |  | Acid Resistant Ceramic Tile | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | SACE | SACE | Control Building(RC) | Battery Room |  | Acid Resistant Ceramic Tile on Screed | Acid Resistant Ceramic Tile H=100 | Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Battery Room |  | F32 |  | #N/A | B33 |  | Acid Resistant Ceramic Tile | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | BONE | BONE | Substation(RC) | Battery Room |  | Steel Trowel Finish w/ Acid Resistant Stone Ware Gres Tile + 2coat Water Proofing | Acid Resistant Stone Ware Gres Tile | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Battery Room |  | F03 |  | Acid Resistant Paint | B02 |  | Acid Resistant Paint | W04B |  | Acid Resistant Paint | C04 |  | Acid Resistant Paint | IKAN | IKAN | Substation(RC) | Battery Room |  | Steel Trowel Finish w/ Acid Resistant Paint | Acid Resistant Paint | Acid Resistant Paint on Cement Plaster (THK. 16mm) | Acid Resistant Paint
Central Control Building(RC) | Battery Room |  | F03 |  | Acid Resistant Paint | B02 |  | Acid Resistant Paint | W04B |  | Acid Resistant Paint | C03 |  | Latex Paint | TVEP | TVEP | Substation(RC) | Battery Room |  | Acid Resistant Paint on Steel Trowel Concrete Slab | Acid Resistant Paint (H=100) | H=1.5m Acid Resistant Paint on Thk15 Cement Plaster Above 1.5m Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
Substation(RC) | Battery Room |  | F32 |  | #N/A | B33 |  | Acid Resistant Ceramic Tile | W33A |  | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Substation(RC) | Battery Room |  | Acid Resistant Tile on Screed | - | H=2m Acid Resistant Tile on Thk15 Cement Plaster Above 2m Epoxy Paint on Thk15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
[16 empty] | HNCC | 154Kv Substation | Battery Room |  | Acid Resistant Paint on Steel Trowel Finish | - | Emeulssion Paint+Acid Resistant Paint (H=300) | Emulsion Paint on Fair Faced Concrete
| Cable Cellar (Open type) |  | F51 |  | Steel Trowel Finish | N.A |  | N.A | N.A |  | N.A | N.A |  | N.A | *바닥 Concrete Paving 적용
Substation(RC) | Cable Cellar |  | F51 |  | Steel Trowel Finish | N.A |  | N.A | N.A |  | N.A | N.A |  | N.A | LECO | LECO | Substation(RC) | Cable Cellar |  | Steel Trowel Finish |  |  | insulation
Substation(RC) | Cable Cellar |  |  |  | Clean Sand Filling | [5 empty] | Cement Plaster (THK. 16mm) |  |  |  | IKAN | IKAN | Substation(RC) | Cable Cellar |  | Clean Sand Filling |  | Cement Plaster (THK. 16mm)
Substation(RC) | Cable Cellar |  |  |  | Sand Filling |  |  |  | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | BONE | BONE | Substation(RC) | Cable Cellar |  | Sand Filling |  | Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Cable Cellar |  |  |  | Sand Filling |  |  |  | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Substation(RC) | Cable Cellar |  | Sand Filling | - | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
[16 empty] | HNCC | 154Kv Substation | Cable Cellar | Close Type | Steel Trowel Finish | Fair Faced Concrete | Fair Faced Concrete | Fair Faced Concrete
| Cable Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | *바닥 Drain 구배 필요시 : 구체 구배
GIS Building(RC) | Cable Basement |  | F07C |  | Epoxy Screed and Seal Coat | B03 |  | Epoxy Paint | W01A |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | RAPO | RAPO | GIS Building(RC) | Cable Basement |  | 5mm Epoxy Screed and Seal Coat on Concrete Slab | Epoxy Paint (H=100) | Emulsion Paint on Fair Faced Concrete | Emulsion Paint on Fair Faced Concrete
Central Control Building(RC) | Cable Room(Basement) |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W03A |  | Latex Paint | C03 |  | Latex Paint | TVEP | TVEP | Central Control Building(RC) | Cable Room(Basement) |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Fair Faced Concrete | Latex Paint on Fair Faced Concrete
| EDG Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
Substation(RC) | EDG Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | LECO | LECO | Substation(RC) | EDG Room |  | Steel Trowel Finish w/ Epoxy Paint | Epoxy Paint | Emulsion Paint | Fair Faced Concrete
[16 empty] | HNCC | 154Kv Substation | EDG Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint (H=100) | Emulsion Paint | Emulsion Paint on Fair Faced Concrete
| Fire Gas Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
Substation(RC) | 소화약제실 |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | LECO | LECO | Substation(RC) | 소화약제실 |  | Steel Trowel Finish w/ Epoxy Paint | Epoxy Paint | Emulsion Paint on Gypsum Board | Emulsion Paint on Fair Faced Concrete
Substation(RC) | Fire Fighting Room |  | F07B |  | Epoxy Coating | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | BONE | BONE | Substation(RC) | Fire Fighting Room |  | THK.1 Epoxy Resin on Sceed | THK.1 Epoxy Resin on Sceed | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
Substation(RC) | Clean Agent Cylinder Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Substation(RC) | Clean Agent Cylinder Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
WTB(RC) | Fire Fighting Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C03 |  | Latex Paint | TVEP | TVEP | WTB(RC) | Fire Fighting Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
[16 empty] | HNCC | 154Kv Substation | Cylinder Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint (H=100) | Emulsion Paint | Emulsion paint on Fair Faced Concrete
[16 empty] | HNCC | Process Control Building | Cylinder Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint (H=100) | Emulsion Paint | Emulsion paint on Fair Faced Concrete
| Fire Water Pump Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
Fire Water Pump BLDG(RC) | Fire Water Pump Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W03B |  | Latex Paint | C03 |  | Latex Paint | TVEP | TVEP | Fire Water Pump BLDG(RC) | Fire Water Pump Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
| Fuel Tank Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
[16 empty] | HNCC | 154Kv Substation | F.O Day Tank Room |  | Epoxy Paint | Epoxy Paint (Up to Dike Top) | Fair Faced Concrete | Fair Faced Concrete
| GIS Equipment Room |  | F07B |  | Epoxy Coating | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | *발주처 Hardener 요구 확인
400kV GIS Building(RC) | GIS Room |  | F08 |  | Heavy Duty Self-Leveling Epoxy | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | RAPO | RAPO | 400kV GIS Building(RC) | GIS Room |  | 5mm Heavy Duty Self Leveling Epoxy | 100mm High Meranti Skirting | Emulsion Paint on Cement Plaster | Emulsion Paint on Fair Faced Concrete | * 5mm Heavy Duty Self-Leveling Epoxy : 계약사양
400kV GIS Building(RC) | GIS Room |  | F07C |  | Epoxy Screed and Seal Coat | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | Jebel-D | Jebel-D | 400kV GIS Building(RC) | GIS Room |  | 5mm Epoxy Screed and Seal Coat on Steel Trowel Finish | 100mm High Meranti Skirting | Emulsion Paint on Cement Plaster | Emulsion Paint on Fair Faced Concrete
230kV GIS Main Receiving Substation(RC) | 230kV GIS Switchgear Room |  | F54B |  | Non-Slip Epoxy Paint with Epoxy Hardener | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | SACE | SACE | 230kV GIS Main Receiving Substation(RC) | 230kV GIS Switchgear Room |  | Non-Slip Epoxy Paint with Epoxy Hardener on Steel Trowel Finish | Epoxy Paint H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
[16 empty] | HNCC | 154Kv Substation | GIS Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint (H=100) | Emulsion Paint | Fair Faced Concrete
| Gas Turbine Hall |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | *발주처 Hardener 요구 확인
Gas Turbine Building(ST) | Gas Turbine Hall |  | F54A |  | Hardener Finish(Liquid Type) | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | UTCC | UTCC | Gas Turbine Building(ST) | Gas Turbine Hall |  | 1. Hardener Finish 2. Steel Trowel Finish | Epoxy Paint | Emulsion Paint on Thk15 Cement Mortar Plastering (Up to 1200mm) | Exposed Structure
| Steam Turbine Hall |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | *발주처 Hardener 요구 확인
Steam Turbine Building(ST) | Steam Turbine Hall (only Laydown Area) |  | F07C |  | Epoxy Screed and Seal Coat | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | RAPO | RAPO | Steam Turbine Building(ST) | Steam Turbine Hall (only Laydown Area) |  | 5mm Epoxy Screed and Seal Coat on Concrete Slab | Epoxy Paint (H=100) | Emulsion Paint on Thk15 Cement Mortar (Up to 2500mm) | Exposed Roof | * 5mm Epoxy Screed and Seal Coat : 계약사양
Steam Turbine Building(ST) | Steam Turbine Hall (except Laydown Area) |  | F08 |  | Heavy Duty Self-Leveling Epoxy | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | RAPO | RAPO | Steam Turbine Building(ST) | Steam Turbine Hall (except Laydown Area) |  | 5mm Heavy Duty Self-Leveling Epoxy | Epoxy Paint (H=100) | Emulsion Paint on Thk15 Cement Mortar (Up to 2500mm) | Exposed Roof | * 5mm Heavy Duty Self-Leveling Epoxy : 계약사양
Steam Turbine Building(ST) | Steam Turbine Hall (Operating Floor) |  | F07C |  | Epoxy Screed and Seal Coat | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | RAPO | RAPO | Steam Turbine Building(ST) | Steam Turbine Hall (Operating Floor) |  | 5mm Epoxy Screed and Seal Coat on Concrete Slab | Exposed Exterior Wall | Emulsion Paint on Thk15 Cement Mortar (Up to 2500mm) | Exposed Roof | * 5mm Epoxy Screed and Seal Coat : 계약사양
Steam Turbine Building(ST) | Steam Turbine Hall |  | F54A |  | Hardener Finish(Liquid Type) | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | TVEP | TVEP | Steam Turbine Building(ST) | Steam Turbine Hall |  | Hardener Finish on Steel Trowel Finish | Epoxy Paint (H=100) | Latex Paint on Thk15 Cement Plaster | Exposed Roof
| HRSG Hall |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | *발주처 Hardener 요구 확인
HRSG Building(ST) | HRSG Hall |  | F54A |  | Hardener Finish(Liquid Type) | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | UTCC | UTCC | Gas Turbine Building(ST) | Gas Turbine Hall |  | 1. Hardener Finish 2. Steel Trowel Finish | Epoxy Paint | Emulsion Paint on Thk15 Cement Mortar Plastering (Up to 1200mm) | Exposed Roof
| Excitation Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A
Steam Turbine Building(ST) | Excitation Room |  | F07C |  | Epoxy Screed and Seal Coat | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | N.A |  | N.A | RAPO | RAPO | Steam Turbine Building(ST) | Excitation Room |  | 5mm Epoxy Screed and Seal Coat on Concrete Slab | Epoxy Paint (H=100) | Emulsion Paint on Thk15 Cement Mortar (Up to 2500mm) | Exposed Roof | * 5mm Epoxy Screed and Seal Coat : 계약사양
Steam Turbine Building(ST) | Excitation TR & Cubicle Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W03B |  | Latex Paint | N.A |  | N.A | TVEP | TVEP | Steam Turbine Building(ST) | Excitation TR & Cubicle Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Thk15 Cement Plaster | Exposed Deck
| Sampling Room |  | F11 |  | Non-Slip Chemical Resistant Epoxy Paint | B04 |  | Chemical Resistant Epoxy Paint | W09B |  | Chemical Resistant Paint | C01 |  | Acrylic Emulsion Paint | *바닥, 벽 Chemical 적용
Steam Turbine Building(ST) | Sampling Room |  | F11 |  | Non-Slip Chemical Resistant Epoxy Paint | B04 |  | Chemical Resistant Epoxy Paint | W09B |  | Chemical Resistant Paint | C03 |  | Latex Paint | TVEP | TVEP | Steam Turbine Building(ST) | Sampling Room |  | Chemical Resistant Paint on Steel Trowel Finish | Chemical Resistant Paint | Chemical Resistant Paint(≤3000) / Latex Paint (>3000) on Cement Plaster | Latex Paint on Fair Faced Concrete
| WT Equipment Room |  | F11 |  | Non-Slip Chemical Resistant Epoxy Paint | B04 |  | Chemical Resistant Epoxy Paint | W09B |  | Chemical Resistant Paint | C01 |  | Acrylic Emulsion Paint | *바닥, 벽 Chemical 적용
WTB(RC) | WT Equipment Room |  | F11 |  | Non-Slip Chemical Resistant Epoxy Paint | B04 |  | Chemical Resistant Epoxy Paint | W03B |  | Latex Paint | C03 |  | Latex Paint | TVEP | TVEP | WTB(RC) | WT Equipment Room |  | Chemical Resistant Paint on Steel Trowel Finish | Chemical Resistant Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
| Chemical Storage Room |  | F11 |  | Non-Slip Chemical Resistant Epoxy Paint | B04 |  | Chemical Resistant Epoxy Paint | W09B |  | Chemical Resistant Paint | C01 |  | Acrylic Emulsion Paint | *바닥, 벽 Chemical 적용
WTB(RC) | Chemical Storage Room |  | F11 |  | Non-Slip Chemical Resistant Epoxy Paint | B04 |  | Chemical Resistant Epoxy Paint | W09B |  | Chemical Resistant Paint | C03 |  | Latex Paint | TVEP | TVEP | WTB(RC) | Chemical Storage Room |  | Chemical Resistant Paint on Steel Trowel Finish | Chemical Resistant Paint | Chemical Resistant Paint(≤3000) / Latex Paint (>3000) on Cement Plaster | Latex Paint on Fair Faced Concrete
Laboratory & Inspection Building(RC) | Chemical Storage Room |  | F32 |  | #N/A | B33 |  | Acid Resistant Ceramic Tile | W04B |  | Acid Resistant Paint | C01 |  | Acrylic Emulsion Paint | SACE | SACE | Laboratory & Inspection Building(RC) | Chemical Storage Room |  | ACID Resistant Ceramic Tile on Screed | ACID Resistant Ceramic Tile | ACID Resistant Paint on THK13 on Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
| Dehydrator Room |  | F11 |  | Non-Slip Chemical Resistant Epoxy Paint | B04 |  | Chemical Resistant Epoxy Paint | W09B |  | Chemical Resistant Paint | C01 |  | Acrylic Emulsion Paint | *바닥, 벽 Chemical 적용
WTB(RC) | Dehydrator Room |  | F11 |  | Non-Slip Chemical Resistant Epoxy Paint | B04 |  | Chemical Resistant Epoxy Paint | W03B |  | Latex Paint | C03 |  | Latex Paint | TVEP | TVEP | WTB(RC) | Dehydrator Room |  | Chemical Resistant Paint on Steel Trowel Finish | Chemical Resistant Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
| Laboratory |  | F31A |  | Non-Slip Unglazed Ceramic Tile | B32 |  | Coved Ceramic Tile | W32A |  | Glazed Ceramic Tile (≤C.H+100) / No Paint (>C.H+100) | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | *바닥+벽 방수 미적용
Control Building(RC) | Laboratory |  | F06B |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Control Building(RC) | Laboratory |  | Epoxy Coating on Screed + Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
WTB(RC) | Laboratory |  | F32 |  | #N/A | B33 |  | Acid Resistant Ceramic Tile | W33A |  | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | TVEP | TVEP | WTB(RC) | Laboratory |  | ACID Resistant Ceramic Tile on Cement Screed w/ ACID Proofing Sealing |  | ACID Resistant Ceramic Tile on Cement Screed w/ ACID Proofing Sealing(≤1200) / Latex Paint (>1200) on Cement Plaster | Suspended Mineral Fiberboard Panel(600x600)
Laboratory & Inspection Building(RC) | Main Laboratory Testing Room |  | F32 |  | #N/A | B33 |  | Acid Resistant Ceramic Tile | W33A |  | Glazed Ceramic Tile (≤1200) / Acrylic Emulsion Paint (>1200) | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Laboratory & Inspection Building(RC) | Main Laboratory Testing Room |  | ACID Resistant Ceramic Tile on Screed | ACID Resistant Ceramic Tile | ACID Resistant Paint on THK13 on Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
Laboratory & Inspection Building(RC) | Sample Receiving Room |  | F32 |  | #N/A | B33 |  | Acid Resistant Ceramic Tile | W04B |  | Acid Resistant Paint | C01 |  | Acrylic Emulsion Paint | SACE | SACE | Laboratory & Inspection Building(RC) | Sample Receiving Room |  | ACID Resistant Ceramic Tile on Screed | ACID Resistant Ceramic Tile | ACID Resistant Paint on THK13 on Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
[16 empty] | HNCC | Laboratory Building | Laboratory room Sample reception room Analysis room |  | Non-Slip Ceramic Tile on Cement mortar | Ceramic Tile on Cement mortar (H=300) | Vinyl Paint (by Interior) | Suspended Mineral Fiberboard ceiling system (600x600)
[16 empty] | HNCC | Laboratory Building | Reagent Temporary Storage Sample Bottle Storage |  | Epoxy Paint on Thk30 cement mortar | Epoxy Paint (H=100) | Emulsion Paint | Emulsion Paint on Fair faced concrete
[16 empty] | HNCC | Laboratory Building | Mold Machine |  | Epoxy Paint on Thk50 cement mortar w/Wire mesh | Epoxy Paint (H=100) | Emulsion Paint | Emulsion Paint on Fair faced concrete
| Fire Water Pump Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
Fire Water Pump BLDG(RC) | Fire Water Pump Room |  | F54A |  | Hardener Finish(Liquid Type) | B03 |  | Epoxy Paint | W03B |  | Latex Paint | C03 |  | Latex Paint | TVEP | TVEP | Fire Water Pump BLDG(RC) | Fire Water Pump Room |  | Epoxy Paint on Steel Trowel Finish | Epoxy Paint | Latex Paint on Thk15 Cement Plaster | Latex Paint on Fair Faced Concrete
| HVAC Room |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint
Control Building(RC) | Mechanical Room |  | F54B |  | Non-Slip Epoxy Paint with Epoxy Hardener | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | SACE | SACE | Control Building(RC) | Mechanical Room |  | Non-Slip Epoxy Paint with Epoxy Hardener on Steel Trowel Finish | Epoxy Paint H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
Control Building(RC) | HVAC Room |  | F06B |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Control Building(RC) | HVAC Room |  | Epoxy Coating on Plain Concrete (w/wire mesh) + Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
Substation(RC) | HVAC Room |  | F06B |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | KLNG | KLNG | Substation(RC) | HVAC Room |  | Epoxy Coating on Plain Concrete (w/wire mesh) + Steel Trowel Finish | Epoxy Coating (H=100) | Emulsion Paint on Thk.15 Cement Plaster | Emulsion Paint on Fair Faced Concrete
Substation(RC) | HVAC Room |  | F07B |  | Epoxy Coating | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | BONE | BONE | Substation(RC) | HVAC Room |  | THK.1 Epoxy Resin on Sceed (Water Proofing Type) | THK.1 Epoxy Resin on Sceed | Acrylic Emulsion Paint on Fair Faced Concrete (or Cement Plaser or Gypsum Board) | Acrylic Emulsion Paint on Fair Faced Concrete
[16 empty] | HNCC | Process Control Building | HVAC Room |  | Epoxy paint on Steel trowel finish | Epoxy Paint (H=100) | Thk100 Sound Absorbing Materials | Thk100 Sound Absorbing Materials
| Blast Chamber |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | *Non-Typical Room
Control Building(RC) | Blast Chamber |  | F06A |  | Non-Slip Epoxy Paint | B03 |  | Epoxy Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | SACE | SACE | Control Building(RC) | Blast Chamber |  | Non-Slip Epoxy Paint on Steel Trowel Finish | Epoxy Paint H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Acrylic Emulsion Paint on Fair Faced Concrete
| EWH Room | *용도 확인 필요 | F34A |  | Vinyl Tile | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | *Non-Typical Room
Control Building(RC) | EWH Room |  | F34A |  | Vinyl Tile | B35A |  | #N/A | W01B |  | Acrylic Emulsion Paint | C95A |  | Suspended Acoustic Tiled Ceiling (M-Bar) | SACE | SACE | Control Building(RC) | EWH Room |  | Vinyl Tile on Screed | Coved Vinyl H=100 | Acrylic Emulsion Paint on Thk.13 Cement Plaster | Suspended Acoustic Tiled Ceiling (600x600)
| VSD Room | *전기실? 용도 확인 필요 | F06A |  | Non-Slip Epoxy Paint | B01 |  | Acrylic Emulsion Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | *Non-Typical Room
Substation(RC) | VSD Room |  | F42 |  | Rubber Tile | B01 |  | Acrylic Emulsion Paint | W01B |  | Acrylic Emulsion Paint | C01 |  | Acrylic Emulsion Paint | IKAN | IKAN | Substation(RC) | VSD Room |  | Steel Trowel Finish w/ Rubber Flooring Tile (THK. 6mm) | Acrylic Emulsion Paint | Arcylic Emulsion Paint on Cement Plaster (THK. 16mm) | Arcylic Emulsion Paint
Shelter | Room |  | Floor |  |  | Base |  |  | Wall |  |  | Ceiling |  |  | Remark | Project | Building | Room |  | Floor | Base | Wall | Ceiling
| Chemical Tank Shelter |  | F11 |  | Non-Slip Chemical Resistant Epoxy Paint
Chemical Tank Shelter(ST) | Chemical Tank Shelter |  | F11 |  | Non-Slip Chemical Resistant Epoxy Paint | N.A |  | N.A | N.A |  | N.A | N.A |  | N.A | TVEP | TVEP | Chemical Tank Shelter(ST) | Chemical Tank Shelter |  | Chemical Resistant Paint on Steel Trowel Finish | N.A | N.A | N.A
| Chemical Dosing Skid Shelter |  | F11 |  | Non-Slip Chemical Resistant Epoxy Paint
Chemical Dosing Skid Shelter(ST) | Chemical Dosing Skid Shelter |  | F11 |  | Non-Slip Chemical Resistant Epoxy Paint | N.A |  | N.A | N.A |  | N.A | N.A |  | N.A | RAPO | RAPO | Chemical Tank Shelter(ST) | Chemical Tank Shelter |  | 1mm Epoxy + 0.2mm Chemical Resistant Epoxy Paint on Steel Trowel Finish | N.A | N.A | N.A
| Ash Compressor Shelter |  | F06A |  | Non-Slip Epoxy Paint
Ash Compressor Shelter(ST) | Ash Compressor Shelter |  | F06A |  | Non-Slip Epoxy Paint | N.A |  | N.A | N.A |  | N.A | N.A |  | N.A | TVEP | TVEP | Ash Compressor Shelter(ST) | Ash Compressor Shelter |  | Epoxy Paint on Steel Trowel Finish | N.A | N.A | N.A
| Air Compressor Shelter |  | F06A |  | Non-Slip Epoxy Paint
Air Compressor Shelter(ST) | Air Compressor Shelter |  | F06A |  | Non-Slip Epoxy Paint | N.A |  | N.A | N.A |  | N.A | N.A |  | N.A | RAPO | RAPO | Air Compressor Shelter(ST) | Air Compressor Shelter |  | 1mm Epoxy + 0.2mm Chemical Resistant Epoxy Paint on Steel Trowel Finish | N.A | N.A | N.A
| Fuel Gas ESD Shelter |  | F06A |  | Non-Slip Epoxy Paint
Fuel Gas ESD Shelter(ST) | Fuel Gas ESD Shelter |  | F06A |  | Non-Slip Epoxy Paint | N.A |  | N.A | N.A |  | N.A | N.A |  | N.A | RAPO | RAPO | Fuel Gas ESD Shelter(ST) | Fuel Gas ESD Shelter |  | 1mm Epoxy + 0.2mm Chemical Resistant Epoxy Paint on Steel Trowel Finish | N.A | N.A | N.A

## Wall Style
# B칼럼에는 노란색 행을 제외하면 콜론( : ) 이 들어가서는 안됨
팀 표준 Style Name & Numbering - Wall
* 동일 Finish Material 의 두께, Size, 높이가 다른 경우 => 별도 구분 않함.
※ Wall Style Schedule - |  | (기본 입력된 정보)
※ Wall Schedule - |  | (설계자의 설계 추가 입력 정보) | Wall Detail : 실제 적용 두께, Size | Fire_Rating : Fire Rating
Exterior Wall: | [9 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Wall Style No | Wall Style Name | Wall Ref. | Wall_Finish-In | Wall_Base Material-1 | Wall_Base Material-2 | Wall_Base Material-3 | Wall_Finish-Ex |  | Wall_Style Remark
|  |  |  | 참고-Interior에서 결정 | Base Material Int. | Base Material Insulation | Base Material Ext. | Exterior Finish
Gypsum + Concrete |  |  |  |  | Wall Family-1 |  | Wall Family-2
| EW11 | Gypsum Board Wall+Mineral Wool Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete |  | Acrylic Emulsion Paint | 1-Layer Gypsum Board | Mineral Wool (Rock Wool)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete |  | WM : Plasterboard Dry Liner System (A04AS176-00001~00009) - Gypsum Board + Insulation (Gypsumboard THK=9.5 & 12.5 & 16 mm)
| EW12 | Gypsum Board Wall+Glass Wool Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete |  | Acrylic Emulsion Paint | 1-Layer Gypsum Board | Glass Wool (Fiberglass)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete
| EW12A | Gypsum Board Wall+Glass Wool Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete |  | Acrylic Emulsion Paint | 2-Layer Gypsum Board | Glass Wool (Fiberglass)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete
| EW13 | Gypsum Board Wall+Polystyrene Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete |  | Acrylic Emulsion Paint | 1-Layer Gypsum Board | Polystyrene Insulation+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete |  | Polystyrene (Extruded Polystyrene(XPS) - 압출법보온판 or Expanded Polystyrene(EPS) - 비드법보온판)
Gypsum + Masonry |  |  |  |  | Wall Family-1
| EW21 | Gypsum Board Wall+Mineral Wool Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board | Mineral Wool (Rock Wool)+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | WM : Plasterboard Dry Liner System (A04AS176-00001~00009) - Gypsum Board + Insulation (Gypsumboard THK=9.5 & 12.5 & 16 mm)
| EW22 | Gypsum Board Wall+Glass Wool Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board | Glass Wool (Fiberglass)+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster
| EW23 | Gypsum Board Wall+Polystyrene Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board | Polystyrene Insulation+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | Polystyrene (Extruded Polystyrene(XPS) - 압출법보온판 or Expanded Polystyrene(EPS) - 비드법보온판)
| EW24 | Gypsum Board Wall+Mineral Wool Insulation w/ Air Space+Concrete Brick Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | Mineral Wool (Rock Wool)+Air Space | Concrete Brick | Acrylic Emulsion Paint on Cement Plaster |  | WM : Plasterboard Dry Liner System (A04AS176-00001~00009) - Gypsum Board + Insulation (Gypsumboard THK=9.5 & 12.5 & 16 mm)
| EW25 | Gypsum Board Wall+Glass Wool Insulation w/ Air Space+Concrete Brick Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | Glass Wool (Fiberglass)+Air Space | Concrete Brick | Acrylic Emulsion Paint on Cement Plaster
| EW26 | Gypsum Board Wall+Polystyrene Insulation w/ Air Space+Concrete Brick Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | Polystyrene Insulation+Air Space | Concrete Brick | Acrylic Emulsion Paint on Cement Plaster |  | Polystyrene (Extruded Polystyrene(XPS) - 압출법보온판 or Expanded Polystyrene(EPS) - 비드법보온판)
| EW27 | Gypsum Board Wall+Mineral Wool Insulation w/ Air Space+Burnt Clay Brick Wall |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | Mineral Wool (Rock Wool)+Air Space | Burnt Clay Brick | N.A |  | WM : Plasterboard Dry Liner System (A04AS176-00001~00009) - Gypsum Board + Insulation (Gypsumboard THK=9.5 & 12.5 & 16 mm)
| EW28 | Gypsum Board Wall+Glass Wool Insulation w/ Air Space+Burnt Clay Brick Wall |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | Glass Wool (Fiberglass)+Air Space | Burnt Clay Brick | N.A
| EW29 | Gypsum Board Wall+Polystyrene Insulation w/ Air Space+Burnt Clay Brick Wall |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | Polystyrene Insulation+Air Space | Burnt Clay Brick | N.A |  | Polystyrene (Extruded Polystyrene(XPS) - 압출법보온판 or Expanded Polystyrene(EPS) - 비드법보온판)
Masonry + Masonry |  |  |  |  | Wall Family-1
| EW31 | Concrete Block Wall+Mineral Wool Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Mineral Wool (Rock Wool)+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster
| EW32 | Concrete Block Wall+Glass Wool Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Glass Wool (Fiberglass)+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster
| EW33 | Concrete Block Wall+Polystyrene Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Polystyrene Insulation+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | Polystyrene (Extruded Polystyrene(XPS) - 압출법보온판 or Expanded Polystyrene(EPS) - 비드법보온판)
| EW34 | Concrete Brick Wall+Mineral Wool Insulation w/ Air Space+Concrete Brick Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick | Mineral Wool (Rock Wool)+Air Space | Concrete Brick | Acrylic Emulsion Paint on Cement Plaster
| EW35 | Concrete Brick Wall+Glass Wool Insulation w/ Air Space+Concrete Brick Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick | Glass Wool (Fiberglass)+Air Space | Concrete Brick | Acrylic Emulsion Paint on Cement Plaster
| EW36 | Concrete Brick Wall+Polystyrene Insulation w/ Air Space+Concrete Brick Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick | Polystyrene Insulation+Air Space | Concrete Brick | Acrylic Emulsion Paint on Cement Plaster |  | Polystyrene (Extruded Polystyrene(XPS) - 압출법보온판 or Expanded Polystyrene(EPS) - 비드법보온판)
| EW37 | Concrete Brick Wall+Mineral Wool Insulation w/ Air Space+Burnt Clay Brick Wall |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick | Mineral Wool (Rock Wool)+Air Space | Burnt Clay Brick | N.A
| EW38 | Concrete Brick Wall+Glass Wool Insulation w/ Air Space+Burnt Clay Brick Wall |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick | Glass Wool (Fiberglass)+Air Space | Burnt Clay Brick | N.A
| EW39 | Concrete Brick Wall+Polystyrene Insulation w/ Air Space+Burnt Clay Brick Wall |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick | Polystyrene Insulation+Air Space | Burnt Clay Brick | N.A |  | Polystyrene (Extruded Polystyrene(XPS) - 압출법보온판 or Expanded Polystyrene(EPS) - 비드법보온판)
Masonry + Concrete |  |  |  |  | Wall Family-1 |  | Wall Family-2
| EW41 | Concrete Block Wall+Mineral Wool Insulation W/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Mineral Wool (Rock Wool)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete
| EW42 | Concrete Block Wall+Glass Wool Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Glass Wool (Fiberglass)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete
| EW43 | Concrete Block Wall+Polystyrene Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Polystyrene Insulation+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete |  | Polystyrene (Extruded Polystyrene(XPS) - 압출법보온판 or Expanded Polystyrene(EPS) - 비드법보온판)
| EW44 | Concrete Brick Wall+Mineral Wool Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick | Mineral Wool (Rock Wool)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete
| EW45 | Concrete Brick Wall+Glass Wool Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick | Glass Wool (Fiberglass)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete
| EW46 | Concrete Brick Wall+Polystyrene Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick | Polystyrene Insulation+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete |  | Polystyrene (Extruded Polystyrene(XPS) - 압출법보온판 or Expanded Polystyrene(EPS) - 비드법보온판)
Single Wall | [6 empty] | Wall Family-1
| EW51 | Concrete Wall+Fair Faced Concrete |  |  |  |  | Concrete Wall | Fair Faced Concrete
| EW51A | Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete | AG, Room 외벽 |  |  |  | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete
| EW51B | Concrete Wall+Bitumen Coating on Fair Faced Concrete | UG, Room 외벽 |  |  |  | Concrete Wall | Bitumen Coating on Fair Faced Concrete
| EW51C | Concrete Wall+Bitumen Coating on Fair Faced Concrete | UG, Pit, Trench Wall | Epoxy Paint |  |  | Concrete Wall | Bitumen Coating on Fair Faced Concrete
| EW52 | Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Cement Plaster |  |  | Concrete Block | Acrylic Emulsion Paint on Cement Plaster
| EW53 | Concrete Brick Wall+Acrylic Emulsion Paint on Cement Plaster |  | Acrylic Emulsion Paint on Cement Plaster |  |  | Concrete Brick | Acrylic Emulsion Paint on Cement Plaster
| EW54 | Burnt Clay Brick Wall |  | N.A |  |  | Burnt Clay Brick | N.A
| EW55 | AAC (Autoclaved Aerated Concrete) Block Wall |  | N.A |  |  | AAC (Autoclaved Aerated Concrete) Block | N.A
| N.A | N.A
기준 | Burnt Clay Brick 외부 미장 미적용, 내부 마감 미적용
AAC (Autoclaved Aerated Concrete) Block 내/외부 마감 미적용
외벽체의 내부마감 Gypsum은 WM : Plasterboard Dry Liner System 적용
WM : Plasterboard Dry Liner System은 외벽의 내부면에 적용
WM : Plasterboard Dry Liner System에서 Insulation 분리 검토
# | Wall Style No | Wall Style Name | Wall Ref. | Wall_Finish-In | Wall_Base Material-1 | Wall_Base Material-2 | Wall_Base Material-3 | Wall_Finish-Ex |  | Wall_Style Remark
[6 empty] | Cladding Sheet Material | Cladding Sheet Insulation
Cladding |  |  |  |  | Wall Family-1
| EW61A | Steel Sandwich Panel (Mineral Wool Insulation) |  |  |  | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool) |  |  | WM : Corrugated Galvanized Steel Sheet Sandwich Panel (THK=50~70, 70~100, 100~150, 150 이상 mm ) (Fire Rating : N.A, 1Hr, 2Hr)
| EW61B | Steel Sandwich Panel (Glass Wool Insulation) |  |  |  | Corrugated Galvanized Steel Sheet Sandwich Panel | Glass Wool (Fiberglass)
| EW62 | Steel Single Sheet Wall |  |  |  | Corrugated Galvanized Steel Sheet-Single
| EW65A | Aluminum Sandwich Panel (Mineral Wool Insulation) |  |  |  | Corrugated Aluminum Sheet Sandwich Panel | Mineral Wool (Rock Wool) |  |  | WM : Corrugated Aluminum Sheet Sandwich Panel (THK=50~70, 70~100, 100~150, 150 이상 mm ) (Fire Rating : N.A, 1Hr, 2Hr)
| EW65B | Aluminum Sandwich Panel (Glass Wool Insulation) |  |  |  | Corrugated Aluminum Sheet Sandwich Panel | Glass Wool (Fiberglass)
| EW69 | Perforated Steel Sandwich Panel (Mineral Wool Insulation) |  |  | Perforated Steel Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool) |  |  | WM 없음, for Sound Absorbing
Cladding + Gypsum/ Masonry |  |  |  |  | Wall Family-1
| EW91 | Steel Sandwich Panel (Mineral Wool Insulation)+Gypsum Board Wall |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool) |  |  | WM : Gypsumboard Partition Wall (Fixed Type) 1 Layer One Side (Gypsumboard THK=9.5 & 12.5 & 16 mm)
| EW92 | Steel Sandwich Panel (Mineral Wool Insulation)+Concrete Block |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool)
| EW93 | Steel Sandwich Panel (Mineral Wool Insulation)+Concrete Brick |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool)
| N.A | N.A
기준 | WM : Mineral, Glass Wool 두 종류만 있음. PIR등 신소재 반영 검토
# | Wall Style No | Wall Style Name | Wall Ref. | Wall_Finish-In | Wall_Base Material-1 | Wall_Base Material-2 | Wall_Base Material-3 | Wall_Finish-Ex |  | Wall_Style Remark
Exterior Wall Finish Only | [7 empty] | Wall Family-1
| EWF1 | Bitumen Coating+Membrane+Protection Board | [5 empty] | Bitumen Coating+Membrane+Protection Board
| N.A | N.A
기준
Interior Wall: | [9 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Wall Style No | Wall Style Name | Wall Ref. | Wall_Finish-In | Wall_Base Material-1 | Wall_Base Material-2 | Wall_Base Material-3 | Wall_Finish-Ex |  | Wall_Style Remark
|  |  |  | 참고-Interior에서 결정 (one side) | Base Material | Base Material Insulation | Base Material | 참고-Interior에서 결정 (other side) | Fire Rating
Gypsum |  |  |  |  | Wall Family-1
| IW11 | 1-Layer Gypsum Board to Both Sides_Mineral Wool Insulation |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board to Both Sides | Mineral Wool (Rock Wool) |  | Acrylic Emulsion Paint on Gypsum Board | N.A | WM : Gypsumboard Partition Wall (Fixed Type) - Both Sides (A04AS177-00007~00036) - Gypsum Board + Insulation (Gypsumboard THK=9.5 & 12.5 & 16 mm)
| IW12 | 1-Layer Gypsum Board to Both Sides_Glass Wool Insulation |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board to Both Sides | Glass Wool (Fiberglass) |  | Acrylic Emulsion Paint on Gypsum Board | N.A
| IW13 | 1-Layer Gypsum Board to Both Sides_w/o Insulation |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board to Both Sides | w/o Insulation |  | Acrylic Emulsion Paint on Gypsum Board | N.A
| IW14 | 2-Layer Gypsum Board to Both Sides_Mineral Wool Insulation |  | Acrylic Emulsion Paint on Gypsum Board | 2-Layer Gypsum Board to Both Sides | Mineral Wool (Rock Wool) |  | Acrylic Emulsion Paint on Gypsum Board | N.A, 1Hr, 2Hr | WM : Gypsumboard Partition Wall (Fixed Type) - Both Sides (A04AS177-00007~00036) - Gypsum Board + Insulation (Gypsumboard THK=9.5 & 12.5 & 16 mm)
| IW15 | 2-Layer Gypsum Board to Both Sides_Glass Wool Insulation |  | Acrylic Emulsion Paint on Gypsum Board | 2-Layer Gypsum Board to Both Sides | Glass Wool (Fiberglass) |  | Acrylic Emulsion Paint on Gypsum Board | N.A, 1Hr, 2Hr
| IW16 | 2-Layer Gypsum Board to Both Sides_w/o Insulation |  | Acrylic Emulsion Paint on Gypsum Board | 2-Layer Gypsum Board to Both Sides | w/o Insulation |  | Acrylic Emulsion Paint on Gypsum Board | N.A, 1Hr, 2Hr
Masonry |  |  |  |  | Wall Family-1
| IW21 | Block Wall |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Block |  |  | Acrylic Emulsion Paint on Cement Plaster |  | WM : Reinforced Concrete Block 50mm<THK≤100mm / 100mm<THK≤200mm / 200mm<THK
| IW22 | Brick Wall |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick |  |  | Acrylic Emulsion Paint on Cement Plaster |  | WM : Concrete Brick 50mm<THK≤100mm / 100mm<THK≤200mm / 200mm<THK
Concrete | IW31 | Concrete Wall |  | Acrylic Emulsion Paint on Cement Plaster | Concrete Wall |  |  | Acrylic Emulsion Paint on Cement Plaster
Masonry+Gypsum |  |  |  |  | Wall Family-1
| IW41 | 1-Layer Gypsum Board to One Side_Mineral Wool Insulation_Concrete Block |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board to One Side | Mineral Wool (Rock Wool) | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | WM : Gypsumboard Partition Wall (Fixed Type) - One Side (A04AS177-00001~00006) - Gypsum Board + Insulation (Gypsumboard THK=9.5 & 12.5 & 16 mm)
| IW42 | 1-Layer Gypsum Board to One Side_Mineral Wool Insulation_Concrete Brick |  | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board to One Side | Mineral Wool (Rock Wool) | Concrete Brick | Acrylic Emulsion Paint on Cement Plaster
| IW46 | 2-Layer Gypsum Board to One Side_Mineral Wool Insulation_Concrete Block |  | Acrylic Emulsion Paint on Gypsum Board | 2-Layer Gypsum Board to One Side | Mineral Wool (Rock Wool) | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | WM : Gypsumboard Partition Wall (Fixed Type) - One Side (A04AS177-00001~00006) - Gypsum Board + Insulation (Gypsumboard THK=9.5 & 12.5 & 16 mm)
| IW47 | 2-Layer Gypsum Board to One Side_Mineral Wool Insulation_Concrete Brick |  | Acrylic Emulsion Paint on Gypsum Board | 2-Layer Gypsum Board to One Side | Mineral Wool (Rock Wool) | Concrete Brick | Acrylic Emulsion Paint on Cement Plaster
| N.A | N.A
기준 | Burnt Clay Brick 내벽에는 미적용
# | Wall Style No | Wall Style Name | Wall Ref. | Wall_Finish-In | Wall_Base Material-1 | Wall_Base Material-2 | Wall_Base Material-3 | Wall_Finish-Ex |  | Wall_Style Remark
Interior Wall Finish Only | [7 empty] | Wall Family-1
| IWF1 | Plaster | [5 empty] | Plaster
| IWF2 | Glazed Ceramic Tile | [5 empty] | Glazed Ceramic Tile |  | *Tile : No BM (Dynamo 물량산출식=0) => Room Family에서 BM 산출
| IWF2A | Glazed Ceramic Tile+Liquid Waterproofing | [5 empty] | Glazed Ceramic Tile+Liquid Waterproofing |  | *Tile : No BM (Dynamo 물량산출식=0) => Room Family에서 BM 산출
| IWF2B | Glazed Ceramic Tile+Waterproof Membrane | [5 empty] | Glazed Ceramic Tile+Waterproof Membrane |  | *Tile : No BM (Dynamo 물량산출식=0) => Room Family에서 BM 산출
| IWF3 | ACID Resistant Ceramic Tile | [5 empty] | ACID Resistant Ceramic Tile |  | *Tile : No BM (Dynamo 물량산출식=0) => Room Family에서 BM 산출
| IWF3A | ACID Resistant Ceramic Tile+Liquid Waterproofing | [5 empty] | ACID Resistant Ceramic Tile+Liquid Waterproofing |  | *Tile : No BM (Dynamo 물량산출식=0) => Room Family에서 BM 산출
| IWF4 | Granite Tile | [5 empty] | Granite Tile |  | *Tile : No BM (Dynamo 물량산출식=0) => Room Family에서 BM 산출
| IWF5 | Marble Tile | [5 empty] | Marble Tile |  | *Tile : No BM (Dynamo 물량산출식=0) => Room Family에서 BM 산출
| N.A | N.A
기준

## Wall 사례
팀 기준 사양 : Wall (Interior & Exterior) | [10 empty] | 프로젝트 적용 현황
* 동일 Finish Material 의 두께, Size, 높이가 다른 경우 => 별도 구분 않함.
Exterial Wall | [10 empty] | Exterial Wall
Project | Building | Description | Style Number | Style Name (Key Name) | Interior Finish (참고) | Base Material Int. | Base Material Insulation | Base Material Ext. | Exterior Finish | Remark | Project | Building | Description | Interior Finish | Base Material Int. | Base Material Insulation | Base Material Ext. | Exterior Finish | Remark
Gypsum + Concrete |  |  | EW11 | Gypsum Board Wall+Mineral Wool Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint | 1-Layer Gypsum Board | Mineral Wool (Rock Wool)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete |  | Gypsum + Concrete
SACE | Control Building(RC) |  | EW11 | Gypsum Board Wall+Mineral Wool Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint | 1-Layer Gypsum Board | Mineral Wool (Rock Wool)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete |  | SACE | Control Building(RC) |  | Acrylic Emulsion Paint | THK16 'Regular' Gypsum Board / THK110 Metal Stud | Non-combustible Insulation | THK0.25 Vapor Barrier / THK250 Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete (Textured)
LECO | Main Control Building(RC) |  | EW11 | Gypsum Board Wall+Mineral Wool Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint | 1-Layer Gypsum Board | Mineral Wool (Rock Wool)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete |  | LECO | Main Control Building(RC) |  | Emulsion Paint | THK12.5 Gypsum Board 2Ply | THK10 Air Space / THK135 Insulation ("가"등급) | THK150 Concrete Wall | Emulsion Paint on Fair Faced Concrete
HNCC | Process Control Building |  | EW13 | Gypsum Board Wall+Polystyrene Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint | 1-Layer Gypsum Board | Polystyrene Insulation+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete |  | HNCC | Process Control Building |  | Emulsion Paint | THK9.5 Gypsum Board 2Ply | THK10 Air Space / THK135 Insulation ("가"등급) | External Exposed Smooth Reinforcen Conc. | NA
HNCC | 154KV Substation |  | EW13 | Gypsum Board Wall+Polystyrene Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint | 1-Layer Gypsum Board | Polystyrene Insulation+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete |  | HNCC | 154KV Substation |  | Emulsion Paint | THK9.5 Gypsum Board 2Ply | THK10 Air Space / THK135 Insulation ("가"등급) | THK200 Concrete Wall | Dryvit(Without Insulation)
Gypsum + Masonry |  |  | EW21 | Gypsum Board Wall+Mineral Wool Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board | Mineral Wool (Rock Wool)+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | Gypsum + Masonry
LECO | ARG MCC Building(RC) |  | EW23 | Gypsum Board Wall+Polystyrene Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board | Polystyrene Insulation+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | LECO | ARG MCC Building(RC) |  | Emulsion Paint | THK12.5 Gypsum Board 2Ply | THK10 Air Space / THK135 Insulation ("가"등급) | THK190 Concrete Block | Emulsion Paint on THK24 Cement Plaster
UTCC | Fuel Gas Electrical Building(RC) |  | EW24 | Gypsum Board Wall+Mineral Wool Insulation w/ Air Space+Concrete Brick Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board, Supporting Frame(Stud), Accessories | Mineral Wool (Rock Wool)+Air Space | Concrete Brick | Acrylic Emulsion Paint on Cement Plaster |  | UTCC | Fuel Gas Electrical Building(RC) |  | Emulsion Paint | Gypsum Board THK9.5mm 2 Plies | THK50 Fire Resistant Rigid Mineral Wool Insulation Board | THK380 Burnt Brick | Emulsion Paint on Cement Plastering
Masonry + Masonry |  |  | EW31 | Concrete Block Wall+Mineral Wool Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Mineral Wool (Rock Wool)+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | Masonry + Masonry
KLNG | Administration Building(RC) |  | EW32 | Concrete Block Wall+Glass Wool Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Glass Wool (Fiberglass)+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | KLNG | Administration Building(RC) |  | Acrylic Emulsion Paint on THK15 Cement Plaster | Concrete Block (390x90x190) | THK35 Air Gap / THK100 Fiberglass Insulation | Concrete Block (390x190x190) | Texture Paint on THK20 Cement Plaster
RAPO | CCB & Administration Building(RC) |  | EW33 | Concrete Block Wall+Polystyrene Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Polystyrene Insulation+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | RAPO | CCB & Administration Building(RC) |  | Emulsion Paint on THK15 Cement Plaster | THK200 Hollow Concrete Block | THK20 Air Gap / THK50 Insulation | THK100 Hollow Concrete Block | Emulsion Paint on THK20 Cement Mortar
RAPO | GIS Building(RC) |  | EW33 | Concrete Block Wall+Polystyrene Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Polystyrene Insulation+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | RAPO | GIS Building |  | THK15 Cement Render | THK200 Hollow Concrete Block | THK20 Air Gap / THK50 Insulation | THK100 Solid Block | THK20 Cement Render
TVEP | Administration Building(RC) |  | EW33 | Concrete Block Wall+Polystyrene Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Polystyrene Insulation+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | TVEP | Administration Building(RC) |  | Latex Paint on THK15 Cement Plaster | THK190 Concrete Block | THK20 Air Gap / THK50 Insulation (EXTRUDED-POLYSTYRENE BOARD-XPS) | THK100 Concrete Block | Latex Paint on THK15 Cement Plaster
TVEP | Warehouse(ST) |  | EW33 | Concrete Block Wall+Polystyrene Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Polystyrene Insulation+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster | Skirt Wall | TVEP | Warehouse(ST) | Insulated | Latex Paint on THK15 Cement Plaster | THK100 Concrete Block | THK20 Air Gap / THK50 Insulation (EXTRUDED-POLYSTYRENE BOARD-XPS) | THK190 Concrete Block | Latex Paint on THK15 Cement Plaster
RAPO | Gas Turbine Building(ST) |  | EW33 | Concrete Block Wall+Polystyrene Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Polystyrene Insulation+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster | Skirt Wall | RAPO | Gas Turbine Building(ST) | Insulated | Emulsion Paint on THK15 Cement Plaster | THK200 Hollow Concrete Block | THK20 Air Gap / THK50 Insulation | THK100 Hollow Concrete Block | Emulsion Paint on THK20 Cement Mortar
IBON | Administration Building(RC) |  | EW33 | Concrete Block Wall+Polystyrene Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Polystyrene Insulation+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | IBON | Administration Building(RC) | Insulated | Emulsion Paint on THK15 Cement Plaster | THK90 Hollow Concrete Block | THK20 Air Gap / THK50 Insulation(EPS, 25K) Expanded Polystyrene(EPS) - 비드법보온판 | THK190 Hollow Concrete Block | Acrylic Paint on THK15 Cement Plaster
OUMACHE-III | Central Control Building (RC) |  | EW33 | Concrete Block Wall+Polystyrene Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Polystyrene Insulation+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | OUMACHE-III | Central Control Building (RC) | Air Gap | Emulsion Paint on THK20 Cement Plaster | THK200 Hollow Concrete Block | THK100 Air Gap | THK100 Hollow Concrete Block | Emulsion Paint on THK20 Cement Mortar
OUMACHE-III | Demi Water Pump Building (RC) |  | EW33 | Concrete Block Wall+Polystyrene Insulation w/ Air Space+Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Polystyrene Insulation+Air Space | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | OUMACHE-III | Demi Water Pump Building (RC) | Air Gap | Emulsion Paint on THK15 Cement Plaster | THK200 Hollow Brick | THK.50 Air Gap | THK100 Hollow Brick | Emulsion Paint on THK.15 Cement Mortar
Masonry + Concrete |  |  | EW41 | Concrete Block Wall+Mineral Wool Insulation W/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Mineral Wool (Rock Wool)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete |  | Masonry + Concrete
UTCC | Main Building (ST) |  | EW44 | Concrete Brick Wall+Mineral Wool Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick | Mineral Wool (Rock Wool)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete | Skirt Wall | UTCC | Main Building (ST) |  | Emulsion Paint on THK15 Cement Mortar Plastering | THK120 Burnt Brick | THK15 Air Gap / THK50 Fire Resistant Rigid Mineral Wool Insulation Board (40kg/m3 Density) | THK150 Concrete Wall | Emulsion Paint on Fair Faced Concrete
IBON | CCB(RC) |  | EW42 | Concrete Block Wall+Glass Wool Insulation w/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Glass Wool (Fiberglass)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete |  | IBON | CCB(RC) | Insulated | Emulsion Paint on THK15 Cement Plaster | THK90 Hollow Concrete Block | THK50 Insulation(EPS, 25K) | THK300 Concrete Wall | Acrylic Paint on FF Conc.
SARB | Control Building(RC) |  | EW41 | Concrete Block Wall+Mineral Wool Insulation W/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Mineral Wool (Rock Wool)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete |  | SARB | Control Building(RC) | AAC | Acrylic Emulsion Paint on Cement Plaster | Thk.200 AAC Block Wall | Thk.50 Air Cap | Thk.250 Blast Resistant Conc. Wall | Texture Lartex Paint
SARB | Control Building(RC) |  | EW41 | Concrete Block Wall+Mineral Wool Insulation W/ Air Space+Concrete Wall+Acrylic Emulsion Paint on Fair Faced Concrete | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Mineral Wool (Rock Wool)+Air Space | Concrete Wall | Acrylic Emulsion Paint on Fair Faced Concrete |  | SARB | Control Building(RC) | AAC & Tile | Acrylic Emulsion Paint on Cement Plaster | Thk.200 AAC Block Wall | Thk.50 Air Cap | Thk.250 Blast Resistant Conc. Wall | Porcelain Tile w/Mechanical Fixing
Single Wall |  |  | EW52 | Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | 0 | 0 | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | Single Wall
IKAN | Main Control Building(RC) |  | EW51 | Concrete Wall+Fair Faced Concrete | 0 | 0 | 0 | Concrete Wall | Fair Faced Concrete |  | IKAN | Main Control Building(RC) |  | Vinyl Acetate Paint | Concrete Wall |  |  | Acrylic Emulsion Paint on Fair Faced Concrete Wall
VEQU | WT Building |  | EW52 | Concrete Block Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | 0 | 0 | Concrete Block | Acrylic Emulsion Paint on Cement Plaster |  | VEQU | WT Building |  | Emulsion Paint on THK15 Cement Plaster | THK200 Hollow Concrete Block |  |  | Emulsion Paint on THK18 Cement Plaster
IKAN | Substation (RC) |  | EW53 | Concrete Brick Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | 0 | 0 | Concrete Brick | Acrylic Emulsion Paint on Cement Plaster |  | IKAN | Substation (RC) |  | Emulsion Paint on THk.16 Cement Plaster | Thk.230 Brick Wall |  |  | Emulsion Paint on THk.16 Cement Plaster
BISKRA | Watch Tower (RC) |  | EW53 | Concrete Brick Wall+Acrylic Emulsion Paint on Cement Plaster | Acrylic Emulsion Paint on Cement Plaster | 0 | 0 | Concrete Brick | Acrylic Emulsion Paint on Cement Plaster |  | BISKRA | Watch Tower (RC) |  | Emulsion Paint on THk.15 Cement Plaster | Thk.230 Brick Wall |  |  | Emulsion Paint on THk.15 Cement Plaster
SARB | Jetty Harbor Master Building (RC) |  | EW55 | AAC (Autoclaved Aerated Concrete) Block Wall | N.A | 0 | 0 | AAC (Autoclaved Aerated Concrete) Block | N.A |  | SARB | Jetty Harbor Master Building (RC) | AAC | Acrylic Latex Paint on Cement Plaster | Thk.250 AAC Block |  |  | Acrylic Latex Paint on Cement Plaster
Project | Building | Description | Style Number | Style Name (Key Name) | Interior Finish (참고) |  | Cladding Sheet Material | Cladding Insulation | Exterior Finish | Remark | Project | Building | Description | Interior Finish (참고) |  | Cladding Sheet Material | Cladding Insulation | Exterior Finish | Remark
Cladding |  |  | EW51 | Concrete Wall+Fair Faced Concrete | 0 | 0 | 0 | Concrete Wall | Fair Faced Concrete |  | Cladding
LECO | Extruder Building(ST) |  | EW61 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | LECO | Extruder Building(ST) |  |  |  | THK100 Glasswool Panel w/ 불연강판
RAPO | Gas Turbine Building(ST) |  | EW65 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | RAPO | Gas Turbine Building(ST) |  |  |  | THK50 Thermal Insulated Trapezoidal AL. Cladding
HNCC | Warehouse |  | EW62 | Steel Single Sheet Wall | 0 | 0 | Corrugated Galvanized Steel Sheet-Single | 0 | 0 |  | HNCC | Warehouse |  |  |  | THK75 Glasswool Wall Panel /불연강판 |  |  | 불연재로 적용
Barbados | Power House(ST) | DG 발전소 소음 차단 : 흡음판+Cladding | EW69 | Perforated Steel Sandwich Panel (Mineral Wool Insulation) | 0 | Perforated Steel Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool) | 0 |  | Barbados | Power House(ST) | DG 발전소 소음 차단 : 흡음판+Cladding |  | Sound Absorbing Panel THK100 (perforated Steel Sheet) | THK50 Thermal Insulated Trapezoidal Cladding |  |  | Sound absornig panel t= .75 outer sheet, 100mm mineral wool, t=.75 perforated inner sheet
Cladding + Gypsum/ Masonry/Concrete |  |  | EW92 | Steel Sandwich Panel (Mineral Wool Insulation)+Concrete Block | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool) | 0 |  | Cladding + Gypsum/ Masonry/Concrete
UKAN | Eating Building |  | EW91 | Steel Sandwich Panel (Mineral Wool Insulation)+Gypsum Board Wall | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool) | 0 |  | UKAN | Eating Building |  | Emulsion Paint | Gypsum Board 12.5mm 2 Plies | THK100 Wall Sandwich Panel
VEQU | CCB(ST) |  | EW91 | Steel Sandwich Panel (Mineral Wool Insulation)+Gypsum Board Wall | Acrylic Emulsion Paint on Gypsum Board | 1-Layer Gypsum Board | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool) | 0 |  | VEQU | CCB(ST) |  | Emulsion Paint | Gypsum Board 12.5mm 1 Plies |  | THK50 Wall Sandwich Panel(Mineral Wool)
VEQU | CCB(ST) | 배터리실 | EW92 | Steel Sandwich Panel (Mineral Wool Insulation)+Concrete Block | ACID Resistant Ceramic Tile on Cement Plaster | Concrete Block | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool) | 0 |  | VEQU | CCB(ST) | 배터리실 | Acid Resistant Tile | THK200 Hollow Concrete Block |  | THK50 Wall Sandwich Panel(Mineral Wool)
VEQU | CCB(ST) | 화장실 | EW92 | Steel Sandwich Panel (Mineral Wool Insulation)+Concrete Block | Glazed Ceramic Tile on Cement Plaster | Concrete Block | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool) | 0 |  | VEQU | CCB(ST) | 화장실 | Ceramic Tile | THK200 Hollow Concrete Block |  | THK50 Wall Sandwich Panel(Mineral Wool)
VEQU | CCB(ST) | FM200 Room | EW92 | Steel Sandwich Panel (Mineral Wool Insulation)+Concrete Block | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool) | 0 |  | VEQU | CCB(ST) | FM200 Room | Emulsion Paint on THK15 Cement Plaster | THK200 Hollow Concrete Block |  | THK50 Wall Sandwich Panel(Mineral Wool)
BISKRA | Water Treatment Building (ST) |  | EW93 | Steel Sandwich Panel (Mineral Wool Insulation)+Concrete Brick | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool) | 0 |  | BISKRA | Water Treatment Building (ST) |  | Emulsion Paint on THK15 Cement Plaster | THK200 Hollow Brick | Air Cap | THK100 Wall Sandwich Panel
MISC | [10 empty] | MISC
[11 empty] | 안동 (남부발전) | 유지창고(RC) |  | THK18 시멘트몰탕 위 수성페인트 | 1.0B 시멘트 벽돌 |  | THK50 메탈판넬
[11 empty] | HNCC | Waste Material Warehouse |  |  |  |  | THK0.6 Metal Color Sheet
[11 empty] | AFEC (FEED) | Admin. and Control building |  | Emeulsion Paint | 2Ply Gypsumboard w/Metal stud | Thermal Insulation (min.R19) | Metal Panel w/6" Metal stud
[11 empty] | AFEC (FEED) | Raw Water Treatment Bldg |  |  |  | Thk2" PIR Insulatied Wall Panel (R16) |  |  | *WM : PIR 없음
Interial Wall | [10 empty] | Interial Wall
Project | Building | Description | Style Number | Style Name (Key Name) | One Side Finish (참고) | Base Material | Base Material Insulation | Fire Rating | Other Side Finish (참고) | Remark | Project | Building | Description | One Side Finish (참고) | Base Material | Base Material Insulation | Fire Rating | Other Side Finish (참고) | Remark
Gypsum |  |  | IW14 | 2-Layer Gypsum Board to Both Sides_Mineral Wool Insulation | Acrylic Emulsion Paint on Gypsum Board | 2-Layer Gypsum Board to Both Sides | Mineral Wool (Rock Wool) | 0 | Acrylic Emulsion Paint on Gypsum Board |  | Gypsum
UKAN | Main Admin Building | Cold Storage | IW16 | 2-Layer Gypsum Board to Both Sides_w/o Insulation | Steel Sandwich Panel (Mineral Wool Insulation) | 2-Layer Gypsum Board to Both Sides | w/o Insulation | 0 | Acrylic Emulsion Paint on Gypsum Board | Insulation 적용 확인 | UKAN | Main Admin Building | Cold Storage | Thk.150 Wall Sandwich Panel | Gypsum Board 12.5mm 2 Plies w/Thk.50 Metal Stud |  |  | Emulsion Paint
UKAN | Laboratory Building | Lab | IW11 | 1-Layer Gypsum Board to Both Sides_Mineral Wool Insulation | Chemical Resistant Paint on Gypsum Board | 1-Layer Gypsum Board to Both Sides | Mineral Wool (Rock Wool) | 0 | Acrylic Emulsion Paint on Gypsum Board | Insulation 적용 확인 Gypsum Layer 확인 | UKAN | Laboratory Building | Lab | Chemical Reistant Paint | Thk. 150 Gypsum Wall
Masonry |  |  | IW21 | Block Wall | Acrylic Emulsion Paint on Cement Plaster | Concrete Block | 0 | 0 | Acrylic Emulsion Paint on Cement Plaster |  | Masonry
IKAN | Substation (RC) | Battery Room | IW22 | Brick Wall | Acid Resistant Paint on Cement Plaster | Concrete Brick | 0 | 0 | Acrylic Emulsion Paint on Cement Plaster |  | IKAN | Substation (RC) | Battery Room | Acid Resistant Paint on Thk.16 Cement Plaster | Thk.230 Brick Wall
IKAN | Main Control Building(RC) | Central Control Room | IW22 | Brick Wall | Acrylic Emulsion Paint on Cement Plaster | Concrete Brick | 0 | 0 | Acrylic Emulsion Paint on Cement Plaster |  | IKAN | Main Control Building(RC) | Central Control Room | Vinyl Acetate Paint on Thk.16 Cement Plaster | Thk.230 Brick Wall
SARB | Control Building(RC) | Toilet | IW21 | Block Wall | Porcelain Tile | Concrete Block | 0 | 0 | Acrylic Emulsion Paint on Cement Plaster |  | SARB | Control Building(RC) | Toilet | Porcelain Tile | Thk.200 Conc. Block
Concrete |  |  | IW31 | Concrete Wall | Acrylic Emulsion Paint on Cement Plaster | Concrete Wall | 0 | 0 | Acrylic Emulsion Paint on Cement Plaster |  | Concrete
|  |  | IW31 | Concrete Wall | Acrylic Emulsion Paint on Cement Plaster | Concrete Wall | 0 | 0 | Acrylic Emulsion Paint on Cement Plaster
Masonry+Gypsum | [10 empty] | Concrete
IKAN | Main Control Building(RC) | HVAC Room | IW47 | 2-Layer Gypsum Board to One Side_Mineral Wool Insulation_Concrete Brick | Acrylic Emulsion Paint on Gypsum Board | 2-Layer Gypsum Board to One Side | Mineral Wool (Rock Wool) | Concrete Brick | Acrylic Emulsion Paint on Cement Plaster |  | IKAN | Main Control Building(RC) | HVAC Room | Thk.12 2 Layer Gypsum Board w/Acrylic Emulsion Paint | Thk.230 Brick Wall | Thk.50 Sound Control Insulation

## Roof Style
# B칼럼에는 노란색 행을 제외하면 콜론( : ) 이 들어가서는 안됨
팀 표준 Style Name & Numbering - Roof
* 동일 Finish Material 의 두께, Size, 높이가 다른 경우 => 별도 구분 않함.
※ Roof Style Schedule - |  | (기본 입력된 정보) | Style No (Key Name) | Style Name | 표준Size(Ref.) | Wall Finish-In | Wall Base Material-1~3 | Wall Finish-Ex
※ Roof Schedule - |  | (설계자의 설계 추가 입력 정보) | Wall Detail : 실제 적용 두께, Size | Fire_Rating : Fire Rating
Concrete Roof: | [9 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Roof Style No | Roof Style Name | Roof Ref. | Roof_Base Material | Roof_Finish-1 | Roof_Finish-2 | Roof_Finish-3 | Roof_Finish-4 | Roof_Finish-5 | Roof_Style Remark
Slope < Insulation < Waterproofing |  |  |  | Floor Family-1 | Roof Family-1
| RF11 | Lightweight Concrete(Slope)+Insulation+Waterproofing |  | Concrete Slab | Light-Weight Concrete Screed (Slope 1%) |  | Rigid Extruded Polystyrene Foam Insulation(XPS) | Waterproofing Membrane-EPDM(or Equivalent)
| RF12 | Mortar Screed Concrete(Slope)+Insulation+Waterproofing |  | Concrete Slab | Mortar Screed (Slope 1%) | PE Sheet (Vapor Barrier) | Rigid Extruded Polystyrene Foam Insulation(XPS) | Waterproofing Membrane-EPDM(or Equivalent)
| RF13 | Lightweight Concrete(Slope)+Insulation+Waterproofing+Gravel |  | Concrete Slab | Light-Weight Concrete Screed (Slope 1%) |  | Rigid Extruded Polystyrene Foam Insulation(XPS) | Waterproofing Membrane-EPDM(or Equivalent) | Gravel for Roof
Slope < Waterproofing < Insulation < Protection |  |  |  | Floor Family-1 | Roof Family-1
| RF21 | Concrete Slab(Slope)+Waterproofing+Insulation+Protection Concrete |  | Concrete Slab (Slope 1%) |  | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Protective Concrete w/ Steel Trowel Finish
| RF22 | Concrete Slab(Slope)+Waterproofing+Insulation+Concrete Roof Tile |  | Concrete Slab (Slope 1%) |  | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Concrete Roof Tile
| RF23 | Lightweight Concrete(Slope)+Waterproofing+Insulation+Gravel |  | Concrete Slab | Light-Weight Concrete Screed (Slope 1%) | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | Geotextile | Gravel for Roof
| RF24 | Lightweight Concrete(Slope)+Waterproofing+Insulation+Roof Tile |  | Concrete Slab | Light-Weight Concrete Screed (Slope 1%) | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | Geotextile | Concrete Roof Tile
| RF25 | Mortar Screed Concrete(Slope)+Waterproofing+Insulation+Roof Tile |  | Concrete Slab | Mortar Screed (Slope 1%) | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Concrete Roof Tile
| RF26 | Lightweight Concrete(Slope)+Waterproofing+Insulation+Protection Concrete |  | Concrete Slab | Light-Weight Concrete Screed (Slope 1%) | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Protective Concrete w/ Steel Trowel Finish
Waterproofing < Insulation < Protection & Slope |  |  |  | Floor Family-1 | Roof Family-1
| RF31 | Waterproofing+Insulation+Protection Concrete(Slope) |  | Concrete Slab |  | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Protective Concrete w/ Steel Trowel Finish (Slope 1%)
| RF32 | Waterproofing+Insulation+Lightweight Concrete(Slope) |  | Concrete Slab |  | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Light-Weight Concrete Screed (Slope 1%)
Insulation < Protection < Waterproofing | RF41 | Concrete Slab(Slope)+Insulation+Protection Concrete+Waterproofing |  | Concrete Slab | Liquid Waterproofing | Rigid Extruded Polystyrene Foam Insulation(XPS) | Welded Wire Fabric | Protective Concrete w/ Steel Trowel Finish | 스카이패널 건식복합방수 | * 스카이패널 건식복합방수 : WM 없음
| N.A | N.A
기준 | Screed 적용 기준 |  |  | 구배가 필요한 바닥마감에만 적용
| Hardener위 Epoxy 기준 |  |  | Hardener위 Epoxy 작업 어려움
| Epoxy Paint / Epoxy Based Sealer / Epoxy Lining 기준 |  |  | 두께 : Epoxy Paint < Epoxy Coating < Self-Leveling Epoxy
| Tile on Screed 적용 기준 |  |  | Screed : 구배용 WM 별도 구분, Tile 자체 Work Master에 Mortar Bond Coat or Adhesive 포함
Cladding Roof: | [9 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Roof Style No | Roof Style Name | Ref. Size, Thickness | Roof_Base Material | Roof_Finish-1 | Roof_Finish-2 | Roof_Finish-3 | Roof_Finish-4 | Roof_Finish-5 | Roof_Style Remark
[5 empty] | Cladding Sheet Material | Cladding Sheet Insulation
Sandwich Panel Roof |  |  |  |  | Roof Family-1
| RF61 | Steel Sandwich Panel (Mineral Wool Insulation) |  | Steel Structure | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool) |  |  |  | WM : Corrugated Galvanized Steel Sheet Sandwich Panel (THK=50~70, 70~100, 100~150, 150 이상 mm ) (Fire Rating : N.A, 1Hr, 2Hr)
| RF62 | Steel Sandwich Panel (Glass Wool Insulation) |  | Steel Structure | Corrugated Galvanized Steel Sheet Sandwich Panel | Glass Wool (Fiberglass)
| RF63 | Aluminum Sandwich Panel (Mineral Wool Insulation) |  | Steel Structure | Corrugated Aluminum Sheet Sandwich Panel | Mineral Wool (Rock Wool) |  |  |  | WM : Corrugated Aluminum Sheet Sandwich Panel (THK=50~70, 70~100, 100~150, 150 이상 mm ) (Fire Rating : N.A, 1Hr, 2Hr)
| RF64 | Aluminum Sandwich Panel (Glass Wool Insulation) |  | Steel Structure | Corrugated Aluminum Sheet Sandwich Panel | Glass Wool (Fiberglass)
Single Metal Sheet Roof | RF71 | Corrugated Galvanized Steel Single Sheet |  | Steel Structure | Corrugated Galvanized Steel Single Sheet
| RF72 | Corrugated Aluminum Single Sheet |  | Steel Structure | Corrugated Aluminum Single Sheet
| N.A | N.A
기준 | WM : Mineral, Glass Wool 두 종류만 있음. PIR등 신소재 반영 검토

## Roof 사례
팀 기준 사양 : Roof | [11 empty] | 프로젝트 적용 현황
* 동일 Finish Material 의 두께, Size, 높이가 다른 경우 => 별도 구분 않함.
Concrete Roof | [11 empty] | Concrete Roof
Project | Building | Description | Style No | Style Name (Key Name) | Base Material Roof | Roof Finish 1 | Roof Finish 2 | Roof Finish 3 | Roof Finish 4 | Roof Finish 5 | Remark | Project | Building | Description | Base Material Roof | Roof Finish 1 | Roof Finish 2 | Roof Finish 3 | Roof Finish 4 | Roof Finish 5 | Remark
Slope < Insulation < Waterproofing |  |  | RF12 | Mortar Screed Concrete(Slope)+Insulation+Waterproofing | Concrete Slab | Mortar Screed (Slope 1%) | PE Sheet (Vapor Barrier) | Rigid Extruded Polystyrene Foam Insulation(XPS) | Waterproofing Membrane-EPDM(or Equivalent) | 0 |  | Slope < Insulation < Waterproofing
SACE |  |  | RF11 | Lightweight Concrete(Slope)+Insulation+Waterproofing | Concrete Slab | Light-Weight Concrete Screed (Slope 1%) | 0 | Rigid Extruded Polystyrene Foam Insulation(XPS) | Waterproofing Membrane-EPDM(or Equivalent) | 0 |  | SACE |  |  | Concrete Slab | Min. THK50 Lightweight Screed w / WWF (150x150-MW9xMW9) *Slope : 2% |  | Nominally THK120 Rigid Insulation (R-30, Fully Adhered) | THK1.52 Single Ply EPDM Membrane (Fully Bonded)
IKAN |  |  | RF12 | Mortar Screed Concrete(Slope)+Insulation+Waterproofing | Concrete Slab | Mortar Screed (Slope 1%) | PE Sheet (Vapor Barrier) | Rigid Extruded Polystyrene Foam Insulation(XPS) | Waterproofing Membrane-EPDM(or Equivalent) | 0 |  | IKAN |  |  | Concrete Slab | Min. THK50 Cement Screed *Slope : 1% | THK.0.15mm P.E FILM | THK110mm Rigid Extruded Polystyrene Insulation | Fully Bonded THK1.5 Single Ply EPDM Sheet
SARB |  |  | RF13 | Lightweight Concrete(Slope)+Insulation+Waterproofing+Gravel | Concrete Slab | Light-Weight Concrete Screed (Slope 1%) | 0 | Rigid Extruded Polystyrene Foam Insulation(XPS) | Waterproofing Membrane-EPDM(or Equivalent) | Gravel for Roof |  | SARB |  |  | Concrete Slab | Min. Thk.30 Light Weight Conc. W/Slope of 1:75 | Min. Thk.75 Rigid Insulation Board | Base Sheet on Sheating Paper | 4 Pilies Asphaly Sheet | Granule Surfaced Cap Sheet (SR1>=78)
AFEC | Admin. and Control Bldg | [10 empty] | AFEC | Admin. and Control Bldg |  | Deck Slab | Tapered Rigid Insulation for Slope | Rigid Insulation (R30) | TPO Membrane system w/Protection board
Slope < Waterproofing < Insulation < Protection |  |  | RF21 | Concrete Slab(Slope)+Waterproofing+Insulation+Protection Concrete | Concrete Slab (Slope 1%) | 0 | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Protective Concrete w/ Steel Trowel Finish |  | Slope < Waterproofing < Insulation < Protection
UTCC |  |  | RF21 | Concrete Slab(Slope)+Waterproofing+Insulation+Protection Concrete | Concrete Slab (Slope 1%) | 0 | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Protective Concrete w/ Steel Trowel Finish |  | UTCC |  |  | Concrete Slab / Steel Trowel Finish *Slope |  | Bituminous Water Proof Membrane (THK.4mm) | THK.100 Polystyrene Rigid Insulation (Compressive Strength Min.40 kPa) | THK.0.1 P.E Film (2 Plys) | THK.60 Protection Concrete (w/ #8-150x150 W.W.F)
TIPO |  |  | RF22 | Concrete Slab(Slope)+Waterproofing+Insulation+Concrete Roof Tile | Concrete Slab (Slope 1%) | 0 | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Concrete Roof Tile |  | TIPO |  |  | Concrete Slab / Steel Trowel Finish *Slope |  | Asphalt Primer / 2 Layers of Asphalt-Impregnated Roofing Felt | THK.50 Rigid Insulation | 2 Layers of P.E Film (THK.0.1mm) | Min. 15mm Cement Mortar / Concrete Roof Tile (300x300x30)
RAPO |  |  | RF22 | Concrete Slab(Slope)+Waterproofing+Insulation+Concrete Roof Tile | Concrete Slab (Slope 1%) | 0 | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Concrete Roof Tile |  | RAPO |  |  | Concrete Slab / Steel Trowel Finish *Slope 1% (W.W.F #8 150x150) |  | THK.4 Waterproofing Membrane w/ Cold Worked Prime Coat | THK.75mm Rigid Insulation (Polystyrene) | THK.0.1mm P.E Film 2 Ply | Min. 20mm Bed Mortar / Precast Concrete Roof Tile (400x400x40)
GULF |  |  | RF24 | Lightweight Concrete(Slope)+Waterproofing+Insulation+Roof Tile | Concrete Slab | Light-Weight Concrete Screed (Slope 1%) | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | Geotextile | Concrete Roof Tile |  | GULF |  |  | Concrete Slab / Steel Trowel Finish | Light Weight Celular Leveling Concrete (500~550 kg/m3) *Min. Slope 1.5% | Asphalt Primer / Double Layer Modified Bitumen Membrane Waterproofing Thk.3mm | THK.50mm Thermal Insulation Extruded Polystyrene Board (Density 32~35 kg/m3) |  | Filter Fabric / Gravel 50mm or Cement Paver (400x400x40 w/ Plastic Support) | 터키업체 설계
RAPO (GIS) |  |  | RF24 | Lightweight Concrete(Slope)+Waterproofing+Insulation+Roof Tile | Concrete Slab | Light-Weight Concrete Screed (Slope 1%) | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | Geotextile | Concrete Roof Tile |  | RAPO (GIS) |  |  | Concrete Slab / Steel Trowel Finish | Min.50 Thk. Lightweight Form Concrete, Laid to Fall *slope 1:80 (1.25%) | Bituminous primer - 2 Coats / Bituminous Membrane - 4mm Thick | THK.75mm Extruded Polystyrene Insulation Board |  | Geo-Textile Water Filtering Membrane - Terram / Precast Concrete Roof Tile (400x400x50) | 카타르 현지설계
Jebel-L |  |  | RF25 | Mortar Screed Concrete(Slope)+Waterproofing+Insulation+Roof Tile | Concrete Slab | Mortar Screed (Slope 1%) | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Concrete Roof Tile |  | Jebel-L |  |  | Concrete Slab | Min. THK.40 Slope Screed | THK.4 Waterproofing Membrane | 2 Layers of THK.50 Roofmate Sheet | 2 Layers of THK.0.1 Non-woven Polypropylene | THK.20 Sand / Building Paper / Concrete Roof Tile (400x400x40) w/ THK.20 Mortar Bedding
KLNG |  |  | RF26 | Lightweight Concrete(Slope)+Waterproofing+Insulation+Protection Concrete | Concrete Slab | Light-Weight Concrete Screed (Slope 1%) | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Protective Concrete w/ Steel Trowel Finish |  | KLNG |  |  | Concrete Slab | Min. THK50 Lightweight Concrete (Cement Screed on Lightweight Concrete for Surface Treatment) | Bituminous Coating / 4mm Bituminous Waterproofing Membrane | THK.50mm Extruded Polystyrene Rigid Board | THK.0.15mm Polyethylene Sheet | 50mm Concrete Topping with Welded Wire Fabric
Waterproofing < Insulation < Protection & Slope |  |  | RF31 | Waterproofing+Insulation+Protection Concrete(Slope) | Concrete Slab | 0 | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Protective Concrete w/ Steel Trowel Finish (Slope 1%) |  | Waterproofing < Insulation < Protection & Slope
TVEP |  |  | RF31 | Waterproofing+Insulation+Protection Concrete(Slope) | Concrete Slab | 0 | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Protective Concrete w/ Steel Trowel Finish (Slope 1%) |  | TVEP |  |  | Concrete Slab / Steel Trowel Finish |  | Prime Coat / Built-up Water Proofing Membrane | THK.50 Rigid Insulation | THK.0.1 P.E Film (2 Plys) | Min.60 Protection Concrete (Slope 2/100) W/ #8-150x150 Wire Mesh *Slope 2%
VEQU |  |  | RF31 | Waterproofing+Insulation+Protection Concrete(Slope) | Concrete Slab | 0 | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Protective Concrete w/ Steel Trowel Finish (Slope 1%) |  | VEQU |  |  | Concrete Slab / Steel Trowel Finish |  | Prime Coat / Built-up Water Proofing Membrane | THK.50 Rigid Insulation | THK.0.1 P.E Film (2 Plys) | Min.60 Protection Concrete (Slope 1/100) W/ #8-150x150 Wire Mesh *Slope 1% | 지붕구체로 Slope을 줄경우, Protection Concrete의 Slope은 없음
LECO |  |  | RF31 | Waterproofing+Insulation+Protection Concrete(Slope) | Concrete Slab | 0 | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Protective Concrete w/ Steel Trowel Finish (Slope 1%) |  | LECO |  |  | Concrete Slab |  | THK3 복합방수시트 | THK.220 Roof Rigid Insulation ("가"등급) | THK.0.2 P.E Film | THK50(min) Plain Concrete *Slope : 1%
안동 (남부발전) |  |  | RF31 | Waterproofing+Insulation+Protection Concrete(Slope) | Concrete Slab | 0 | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Protective Concrete w/ Steel Trowel Finish (Slope 1%) |  | 안동 (남부발전) |  |  | Concrete Slab / Steel Trowel Finish |  | 일체형 복합방수 | THK.110mm Insulation(압출보온판 "가"급) | THK.0.1mm P.E Film 2 Ply | THK.60(min) 무근콘크리트(25-24-12) w/ #8-150x150 W.W.F. *Slope 1%
평택탈황 (서부발전) |  |  | RF32 | Waterproofing+Insulation+Lightweight Concrete(Slope) | Concrete Slab | 0 | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Light-Weight Concrete Screed (Slope 1%) |  | 평택탈황 (서부발전) |  |  | Concrete Slab |  | THK.3 Sheet 방수 | THK.50mm Insulation | THK.0.1mm P.E Film 2 Ply | THK.60 Lightweight Concrete w/ Wiremesh #8-150x150
UKAN |  |  | RF31 | Waterproofing+Insulation+Protection Concrete(Slope) | Concrete Slab | 0 | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Protective Concrete w/ Steel Trowel Finish (Slope 1%) |  | UKAN |  |  | Concrete Slab with Steel Trowel Finish | Thk.6 Waterproofing Membrane 3 Layers of 2mm Polymer Modified Bitumen | Thk.0.05 PE Film | Thk.75 Rigid Insulation, Extruded Foam Polystyrene, Min 60Kpa, Heat Treanmission Coefficient <=0.5W/m2c | Thk.0.05 PE Film | Min. Thk.100 Protection Conc.(B10) w/Welded Wire Fabric Dia. 4x150x150 for slope w/Control Hoint @1500x1500
Insulation < Protection < Waterproofing |  |  | RF31 | Waterproofing+Insulation+Protection Concrete(Slope) | Concrete Slab | 0 | Waterproofing Membrane-EPDM(or Equivalent) | Rigid Extruded Polystyrene Foam Insulation(XPS) | PE Sheet (Vapor Barrier) 2Plies | Protective Concrete w/ Steel Trowel Finish (Slope 1%) |  | Insulation < Protection < Waterproofing
HNCC |  |  | RF41 | Concrete Slab(Slope)+Insulation+Protection Concrete+Waterproofing | Concrete Slab | Liquid Waterproofing | Rigid Extruded Polystyrene Foam Insulation(XPS) | Welded Wire Fabric | Protective Concrete w/ Steel Trowel Finish | 스카이패널 건식복합방수 |  | HNCC |  |  | Thk150 Conc. Slab (Slope=2/100) | Liquid Water Proofing | Thk220 Insulation('가'등급) | Thk70 Plain Concrete w/#8-150x150 Wire Mesh | Skypanel Roofing System
HNCC | [11 empty] | HNCC |  |  | Thk150 Conc. Slab (Slope=1/100) | Liquid Water Proofing | Thk280 Roof Rigid Insulation('가'등급) | Thk70 Plain Concrete w/#8-150x150 Wire Mesh | Skypanel Roofing System
Cladding Roof | [11 empty] | Cladding Roof
Project | Building | Description |  |  |  | Cladding Sheet Material | Cladding Sheet Insulation |  |  |  | Remark | Project | Building | Description | Base Material Roof | Roof Finish 1 | Roof Finish 2 | Roof Finish 3 | Roof Finish 4 |  | Remark
|  |  | EW61 | #N/A |  | #N/A | #N/A
IBON | Turbine House(ST) |  | RF61 | Steel Sandwich Panel (Mineral Wool Insulation) |  | Corrugated Galvanized Steel Sheet Sandwich Panel | Mineral Wool (Rock Wool) |  |  |  |  | IBON | Turbine House(ST) |  |  | THK50 Insulated Metal Cladding (Rockl Wool)
LECO | Extruder Building(ST) |  | RF62 | Steel Sandwich Panel (Glass Wool Insulation) |  | Corrugated Galvanized Steel Sheet Sandwich Panel | Glass Wool (Fiberglass) |  |  |  |  | LECO | Extruder Building(ST) |  |  | THK150 Glasswool Panel w/ 불연강판
LECO | Process Building(ST) |  | RF62 | Steel Sandwich Panel (Glass Wool Insulation) |  | Corrugated Galvanized Steel Sheet Sandwich Panel | Glass Wool (Fiberglass) |  |  |  |  | LECO | Process Building(ST) |  |  | THK150 내화 Glasswool Panel (0.5HR) w/ 불연강판
IBON | Steam Turbine Building(ST) |  | RF62 | Steel Sandwich Panel (Glass Wool Insulation) |  | Corrugated Galvanized Steel Sheet Sandwich Panel | Glass Wool (Fiberglass) |  |  |  |  | IBON | Steam Turbine Building(ST) |  |  | THK50 Insulated Metal Cladding (Glass Wool)
HNCC | Warehouse |  | RF62 | Steel Sandwich Panel (Glass Wool Insulation) |  | Corrugated Galvanized Steel Sheet Sandwich Panel | Glass Wool (Fiberglass) |  |  |  |  | HNCC | Warehouse |  |  | THK100 Glasswool Roof Panel
HNCC | Polymer Catalyst Warehouse |  | RF62 | Steel Sandwich Panel (Glass Wool Insulation) |  | Corrugated Galvanized Steel Sheet Sandwich Panel | Glass Wool (Fiberglass) |  |  |  |  | HNCC | Polymer Catalyst Warehouse |  |  | THK50 Glasswool Roof Panel w/불연강판
RAPO | Gas Turbine Building(ST) |  | RF63 | Aluminum Sandwich Panel (Mineral Wool Insulation) |  | Corrugated Aluminum Sheet Sandwich Panel | Mineral Wool (Rock Wool) |  |  |  |  | RAPO | Gas Turbine Building(ST) |  |  | THK75 Thermal Insulated Trapezoidal AL. Cladding
[12 empty] | UKAN | Eating Building |  |  | THK 200 Roof Sandwich Panel
[12 empty] | HNCC | Waste Material Warehouse |  |  | THK0.6 Metal Color Sheet
[12 empty] | AFEC | Raw Water Treatment Bldg |  |  | THK2.5" PIR Insulated Roof Panel (R21)
SACE
HNCC

## Door Style
# B칼럼에는 노란색 행을 제외하면 콜론( : ) 이 들어가서는 안됨
팀 표준 Style Name & Numbering - Door
* Door Size, Fire Rating이 다른 경우 => 별도 구분 않함.
※ Door Style Schedule - |  | 기본 입력된 정보 | Style Name(Key Name) | Style No. | 표준Size(Ref.) | Door 재질 | Frame 재질 | Vision/Panic
※ Door Schedule - |  | 설계자의 설계 추가 입력 정보 | Int. or Ext 입력 | Exit 입력 | Fire Rating 입력 | Hardware
Single Door: | [8 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Door Style No | Door Style Name | Ref. Door Size | Door_Leaf | Door_Frame | Door_Vision | Door_Panic | Door_Fire Rating | Door_Style Remark
Single Door | SD11 | Steel Door_Single | W1000 x H2100 | Steel | Steel | N.A | N.A | NA/0.5/1.0 /1.5/2.0 | Steel Door w/ Steel Frame
| SD12 | Steel Door_Single_Vision | W1000 x H2100 | Steel | Steel | Vision | N.A | NA/0.5/1.0 /1.5/2.0
| SD13 | Steel Door_Single_Panic Bar | W1000 x H2100 | Steel | Steel | N.A | Panic | NA/0.5/1.0 /1.5/2.0
| SD14 | Steel Door_Single_Vision_Panic Bar | W1000 x H2100 | Steel | Steel | Vision | Panic | NA/0.5/1.0 /1.5/2.0
| SD15 | Steel Door_Single for Shaft | W600 x H900 HVAC Duct Shaft | Steel | Steel | N.A | N.A | NA/0.5/1.0 /1.5/2.0
| SD21 | Blast Resistant Door_Single | W1000 x H2100 | Steel | Steel | N.A | N.A | NA/0.5/1.0 /1.5/2.0 | Blast Resistant Door w/ Steel Frame
| SD22 | Blast Resistant Door_Single_Panic Bar | W1000 x H2100 | Steel | Steel | N.A | Panic | NA/0.5/1.0 /1.5/2.0
| SD31 | Aluminum Door_Single | W1000 x H2100 | Aluminum | Aluminum | N.A | N.A | NA/0.5/1.0/1.5 | Aluminum Door w/ Aluminum Frame
| SD32 | Aluminum Door_Single_Vision | W1000 x H2100 | Aluminum | Aluminum | Vision | N.A | NA/0.5/1.0/1.5
| SD33 | Aluminum Door_Single_Panic Bar | W1000 x H2100 | Aluminum | Aluminum | N.A | Panic | NA/0.5/1.0/1.5
| SD34 | Aluminum Door_Single_Vision_Panic Bar | W1000 x H2100 | Aluminum | Aluminum | Vision | Panic | NA/0.5/1.0/1.5
| SD41 | Glass Door_Single | W1000 x H2100 | Glass Door | SST Frame | N.A | N.A | N.A
| SD51 | SST Door_Single | W1000 x H2100 | Stainless Steel Door | SST Frame | N.A | N.A | N.A
| SD61 | Wood Door_Single | W1000 x H2100 | Wood | Wood | N.A | N.A | N.A
| SD62 | Wood Door_Single_Vision | W1000 x H2100 | Wood | Wood | Vision | N.A | N.A
| SD71 | uPVC Door | W1000 x H2100 | uPVC | uPVC | N.A | N.A | N.A
| N.A | N.A
기준
Double Door: | [8 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Door Style No | Door Style Name | Ref. Size, Thickness | Door_Leaf | Door_Frame | Door_Vision | Door_Panic | Door_Fire Rating | Door_Style Remark
Double Door | DD11 | Steel Door_Double | W2000 x H2100 | Steel | Steel | N.A | N.A | NA/0.5/1.0 /1.5/2.0
| DD12 | Steel Door_Double_Vision | W2000 x H2100 | Steel | Steel | Vision | N.A | NA/0.5/1.0 /1.5/2.0
| DD13 | Steel Door_Double_Panic | W2000 x H2100 | Steel | Steel | N.A | Panic | NA/0.5/1.0 /1.5/2.0
| DD14 | Steel Door_Double_Vision_Panic Bar | W2000 x H2100 | Steel | Steel | Vision | Panic | NA/0.5/1.0 /1.5/2.0
| DD21 | Blast Resistant Door_Double | W2000 x H2100 | Steel | Steel | N.A | N.A | NA/0.5/1.0 /1.5/2.0
| DD22 | Blast Resistant Door_Double_Panic Bar | W2000 x H2100 | Steel | Steel | N.A | Panic | NA/0.5/1.0 /1.5/2.0
| DD31 | Aluminum Door_Double | W2000 x H2100 | Aluminum | Aluminum | N.A | N.A | NA/0.5/1.0/1.5
| DD32 | Aluminum Door_Double_Vision | W2000 x H2100 | Aluminum | Aluminum | Vision | N.A | NA/0.5/1.0/1.5
| DD33 | Aluminum Door_Double_Panic | W2000 x H2100 | Aluminum | Aluminum | N.A | Panic | NA/0.5/1.0/1.5
| DD34 | Aluminum Door_Double_Vision_Panic Bar | W2000 x H2100 | Aluminum | Aluminum | Vision | Panic | NA/0.5/1.0/1.5
| DD41 | Glass Door_Double | W2000 x H2100 | Glass Door | SST Frame | N.A | N.A | N.A
| DD51 | SST Door_Double | W2000 x H2100 | Stainless Steel Door | SST Frame | N.A | N.A | N.A
| DD61 | Wood Door_Double | W2000 x H2100 | Wood | Wood | N.A | N.A | N.A
| DD62 | Wood Door_Double_Vision | W2000 x H2100 | Wood | Wood | Vision | N.A | N.A
| N.A | N.A
기준
Double Door + Transsom: | [8 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Door Style No | Door Style Name | Ref. Size, Thickness | Door_Leaf | Door_Frame | Door_Vision | Door_Panic | Door_Fire Rating | Door_Style Remark
Double Door + Transsom | DDT11 | Steel Door_Double_Transsom | W2000xH2100 + W2000xH1000 | Steel | Steel | N.A | N.A | NA/0.5/1.0 /1.5/2.0
| DDT12 | Steel Door_Double_Vision_Transsom | W2000xH2100 + W2000xH1000 | Steel | Steel | Vision | N.A | NA/0.5/1.0 /1.5/2.0
| DDT13 | Steel Door_Double_Panic_Transsom | W2000xH2100 + W2000xH1000 | Steel | Steel | N.A | Panic | NA/0.5/1.0 /1.5/2.0
| DDT14 | Steel Door_Double_Vision_Panic Bar_Transsom | W2000xH2100 + W2000xH1000 | Steel | Steel | Vision | Panic | NA/0.5/1.0 /1.5/2.0
| DDT21 | Blast Resistant Door_Double | W2000xH2100 + W2000xH1000 | Steel | Steel | N.A | N.A | NA/0.5/1.0 /1.5/2.0
| DDT22 | Blast Resistant Door_Double_Panic Bar | W2000xH2100 + W2000xH1000 | Steel | Steel | N.A | Panic | NA/0.5/1.0 /1.5/2.0
| N.A | N.A
기준
Shutter / Sliding / Hanger / Swing / Revolving / Folding: | [8 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Door Style No | Door Style Name | Ref. Size, Thickness | Door_Leaf | Door_Frame | Door_Vision | Door_Panic | Door_Fire Rating | Door_Style Remark
Shutter | BD11 | Steel Roll Up Door_Manual |  | Steel | Steel | Manual |  | NA/0.5/1.0 /1.5/2.0
| BD12 | Steel Roll Up Door_Motor |  | Steel | Steel | Motor |  | NA/0.5/1.0 /1.5/2.0
| BD13 | Blast Resistant Roll Up Door_Manual |  | Steel | Steel | Manual |  | NA/1.0/2.0
| BD14 | Blast Resistant Roll Up Door_Motor |  | Steel | Steel | Motor |  | NA/1.0/2.0
| BD15 | Aluminum Roll Up Door_Manual |  | Aluminum | Aluminum | Manual |  | N.A
| BD16 | Aluminum Roll Up Door_Motor |  | Aluminum | Aluminum | Motor |  | N.A
Sliding | BD21 | Steel Sliding Door_Manual |  | Steel | Steel | Manual |  | NA/0.5/1.0 /1.5/2.0
| BD22 | Steel Sliding Door_Motor |  | Steel | Steel | Motor |  | NA/0.5/1.0 /1.5/2.0
| BD23 | Aluminum Sliding Door_Manual |  | Aluminum | Aluminum | Manual |  | N.A
| BD24 | Aluminum Sliding Door_Motor |  | Aluminum | Aluminum | Motor |  | N.A
| BD25 | Glass Sliding Door_Motor |  | Glass Door | SST Frame | Manual |  | N.A | WM 항목 없음
| BD26 | Glass Sliding Door_Motor |  | Glass Door | SST Frame | Motor |  | N.A | WM 항목 없음
Hanger | BD31 | Steel Hanger Door |  | Steel | Steel | N.A |  | N.A
Swing | BD41 | Steel Swing Door |  | Steel | Steel | N.A |  | N.A
| BD42 | Aluminum Swing Door |  | Aluminum | Aluminum | N.A |  | N.A
Revolving | BD51 | Revolving Door_Manual |  | Glass Door | SST Frame | Manual |  | N.A
| BD52 | Revolving Door_Auto |  | Glass Door | SST Frame | Auto |  | N.A
Folding | BD61 | Steel Folding(Accordion) Door_Manual |  | Steel | Steel | Manual |  | N.A
| BD62 | Steel Folding(Accordion) Door_Motor |  | Steel | Steel | Motor |  | N.A
| BD63 | Aluminum Folding(Accordion) Door_Manual |  | Aluminum | Aluminum | Manual |  | N.A
| BD64 | Aluminum Folding(Accordion) Door_Motor |  | Aluminum | Aluminum | Motor |  | N.A
| BD65 | PVC Folding(Accordion) Door_Manual |  | PVC | PVC | Manual |  | N.A
| BD66 | Glass Folding(Accordion) Door_Manual |  | Glass Door | SST Frame | Motor |  | N.A | WM 항목 없음
| N.A | N.A
기준

## Door 사례
팀 기준 사양 : Door (inc. Shutter) | [13 empty] | 프로젝트 적용 현황
Project | Building | Description | Style Number | Style Name (Key Name) | Door Type | Door Size (Opening) | Door | Frame | Vision | Panic | Fire Rating | Hardware | Remark | Project | Building | Description | Door Type | Door Size (Opening) | Door | Frame | Vision | Panic | Fire Rating | Hardware | Remark
Single Door | [13 empty] | Single Door
HNCC | 154Kv Substation |  | SD11 | Steel Door_Single |  | W1000 x H2100 | Steel | Steel | N.A | N.A |  |  |  | HNCC | 154Kv Substation | Fire Rated Steel Door |  | W1160xH2290 | Steel Door Leaf Thk45mm | Galvanized Steel and Paint Thick.1.3mm | N.A | N.A | 1.0 H | -Hinge : Pivot Hinge(Top & Floor) - Vertical Flush Bolt - Cylinder lock - Door stop - Door closers | Internal
IBON | CCB(RC) |  | SD12 | Steel Door_Single_Vision |  | W1000 x H2100 | Steel | Steel | Vision | N.A |  |  |  | IBON | CCB(RC) | Steel Door |  | W1000 x H2100 | Galvanized Steel w/Paint | Galvanized Steel w/Paint | Clear Wired Glass (Thk.7mm) |  |  | -Door Lever -Cylinder Lockset -Door Closer -Door Stopper -Pivot Hinge
SACE1 | Central Control Building(RC) Store |  | SD12 | Steel Door_Single_Vision |  | W1000 x H2100 | Steel | Steel | Vision | N.A |  |  |  | SACE1 | Central Control Building(RC) Store | Steel Door | Type-A | 1000x2150 (1020x2160) | Min. THK 45 Galvanized Steel w/Paint | Galvanized Steel w/Paint | Fire Rated Glazing (200x600) | N.A | 0.33 H | -Lever Handle -Mortise Lock -Master Key System -Door Stopper(Floor Type) -Butt Hinge -Door Closer | Internal
TVEP | Control Building(RC) |  | SD14 | Steel Door_Single_Vision_Panic Bar |  | W1000 x H2100 | Steel | Steel | Vision | Panic |  |  |  | TVEP | Control Building(RC) | Steel Door | Type-A | W1000 x H2100 | Steel Door | Steel | Clear Wired Glass (Thk.6mm) | Panic Bar | 1.5H | -Hinge : Full Mortise Butt -Panic Bar with Lever Handle on other side -Lockset -Overhead Door Closer (Parallel Arm Mounting) | Exit
TVEP | Control Building(RC) HVAC Duct Shaft |  | SD15 | Steel Door_Single for Shaft |  | W600 x H900 HVAC Duct Shaft | Steel | Steel | N.A | N.A |  |  |  | TVEP | Control Building(RC) HVAC Duct Shaft | Steel Door |  | W600 x H900 | Steel | Steel | N.A | N.A | 1.5 H | -Hinge : Full Mortise Butt - Cup Handle Type Door Lock | Internal
SACE1 | Central Control Building(RC) Blast Chamber |  | SD22 | Blast Resistant Door_Single_Panic Bar |  | W1000 x H2100 | Steel | Steel | N.A | Panic |  |  |  | SACE1 | Central Control Building(RC) Blast Chamber | Blast Resistant Door | Type-A | 1000x2150 (1020x2160) | Min. THK 45 Galvanized Steel w/Paint *Blast -Overpressure : 0.81 PSI -Impulse 471.25 PSI-MS -Response Range : L -Performance Category : I | Galvanized Steel w/Paint | N.A | Push Panic Bar (Inside) | 1.5 H | -Lever Handle -Mortise Lock -Master Key System -Door Stopper(Floor Type) -Butt Hinge -Gas Tight Seal(Heacy-Duty PVC Seal) -Door Closer -Door Bottom w/Rain Drip -Securuty Door Locck | External
HNCC | Process Control Building |  | SD41 | Glass Door_Single |  | W1000 x H2100 | Glass Door | SST Frame | N.A | N.A |  |  |  | HNCC | Process Control Building | Stainless Steel Door |  | 1000x2200 | SSD w/Tempered Glass |  |  |  |  | -Hinge : Floor Hinge
HNCC | Process Control Building |  | SD12 | Steel Door_Single_Vision |  | W1000 x H2100 | Steel | Steel | Vision | N.A |  |  |  | HNCC | Process Control Building | Steel Glass Door |  | 1000x3010 | Steel w/Tempered Glass Door Leaf Thk45mm | Galvanized Steel and Paint Thick.1.3mm |  |  |  | -Hinge : Butt Hinge - Knob - Cylinder lock - Door stop - Door closers
Double Door | [13 empty] | Double Door
SACE1 | Central Control Building(RC) Rack Room |  | DD11 | Steel Door_Double |  | W2000 x H2100 | Steel | Steel | N.A | N.A |  |  |  | SACE1 | Central Control Building(RC) Rack Room | Steel Door | Type-B | 1800x2150 (1820x2160) | Min. THK 45 Galvanized Steel w/Paint | Galvanized Steel w/Paint | N.A | N.A | 1.5 H | -Lever Handle -Mortise Lock -Vert Flush Bolt(T&B, For Fixed Leaf) -Master Key System -Door Stopper(Floor Type) -Butt Hinge -Door Closer | Internal
HNCC | 154kV Substation |  | DD11 | Steel Door_Double |  | W2000 x H2100 | Steel | Steel | N.A | N.A |  |  |  | HNCC | 154kV Substation | Fire Rated Steel Door |  | 2160x2100 3160x3090 2660x3000 등 장비실에 따라 사이즈 다양함 | Steel Door Leaf Thk45mm | Galvanized Steel and Paint Thick.1.3mm |  |  | 1.0 H | -Hinge : Pivot Hinge(Top & Floor) - Knob - Vertical Flush Bolt - Cylinder lock - Door stop - Door closers
IBON | CCB(RC) |  | DD12 | Steel Door_Double_Vision |  | W2000 x H2100 | Steel | Steel | Vision | N.A |  |  |  | IBON | CCB(RC) | Steel Door |  | 2000x2100 등 장비실에 따라 사이즈 다양함 | Galvanized Steel w/Paint | Galvanized Steel w/Paint | Clear Wired Glass (Thk.7mm) |  |  | -Door Lever -Cylinder Lockset -Door Closer -Door Stopper -Pivot Hinge -Flush Bolt
HNCC | Process Control Building |  | DD21 | Blast Resistant Door_Double |  | W2000 x H2100 | Steel | Steel | N.A | N.A |  |  |  | HNCC | Process Control Building | Blast Door ww/Wicket door |  | 2160x2290 | Blast Resistant Steel Door | Galvanized Steel and Paint |  |  |  | -Hinge : Blast heavy dutty - Knob - Vertical Flush Bolt - Cylinder lock - Door stop - Door closers
SACE1 | Central Control Building(RC) Air Lock |  | DD22 | Blast Resistant Door_Double_Panic Bar |  | W2000 x H2100 | Steel | Steel | N.A | Panic |  |  |  | SACE1 | Central Control Building(RC) Air Lock | Blast Resistant Door | Type-B | 1800x2150 (1820x2160) | Min. THK 45 Galvanized Steel w/Paint *Blast -Overpressure : 0.81 PSI -Impulse 471.25 PSI-MS -Response Range : L -Performance Category : I | Galvanized Steel w/Paint | N.A | Push Panic Bar (Inside) | 1.5 H | -Lever Handle -Mortise Lock -Master Key System -Door Stopper(Floor Type) -Butt Hinge -Gas Tight Seal(Heacy-Duty PVC Seal) -Door Closer -Door Bottom w/Rain Drip -Securuty Door Locck | External
HNCC | Process Control Building |  | DD41 | Glass Door_Double |  | W2000 x H2100 | Glass Door | SST Frame | N.A | N.A |  |  |  | HNCC | Process Control Building | Stainless Steel Door |  | 2000x3010 | SSD w/Tempered Glass | Stainless Steel |  |  |  | -Hinge : Floor Hinge
HNCC | Subcontractor Building |  | DD41 | Glass Door_Double |  | W2000 x H2100 | Glass Door | SST Frame | N.A | N.A |  |  |  | HNCC | Subcontractor Building | Stainless Steel Door |  | 2200x2700 | SSD w/Tempered Glass | Stainless Steel |  |  |  | -Hinge : Floor Hinge
HNCC | Subcontractor Building |  | DD41 | Glass Door_Double |  | W2000 x H2100 | Glass Door | SST Frame | N.A | N.A |  |  |  | HNCC | Subcontractor Building | Stainless Steel Door |  | 2160x2290 | Fire Glass Thk29mm | Stainless Steel |  |  |  | -Hinge : Floor Hinge
Double Door + Transsom | [13 empty] | Double Door + Transsom
SACE1 | Central Control Building(RC) OTS Training Room |  | DDT11 | Steel Door_Double_Transsom |  | W2000xH2100 + W2000xH1000 | Steel | Steel | N.A | N.A |  |  |  | SACE1 | Central Control Building(RC) OTS Training Room | Steel Door | Type-C | 1800x2700 (1820x2710) | Min. THK 45 Galvanized Steel w/Paint | Galvanized Steel w/Paint Removable Transsom | N.A | N.A | 1.5 H | -Lever Handle -Mortise Lock -Vert Flush Bolt(T&B, For Fixed Leaf) -Master Key System -Door Stopper(Floor Type) -Butt Hinge -Door Closer | Internal
HNCC | Laboratory Building |  | DDT11 | Steel Door_Double_Transsom |  | W2000xH2100 + W2000xH1000 | Steel | Steel | N.A | N.A |  |  |  | HNCC | Laboratory Building | Steel Door |  | 3320x3060 | Door Leaf Thk45mm Galvanized steel and Paint | Galvanized Steel and Paint Thick.1.3mm |  |  |  | -Hinge : Pivot Hinge(Top & Floor) - Knob - Vertical Flush Bolt - Cylinder lock - Door stop - Door closers
IBON | CCB(RC) |  | DDT12 | Steel Door_Double_Vision_Transsom |  | W2000xH2100 + W2000xH1000 | Steel | Steel | Vision | N.A |  |  |  | IBON | CCB(RC) | Steel Door |  | 2200x3000 등 장비실에 따라 사이즈 다양함 | Galvanized Steel w/Paint | Galvanized Steel w/Paint | Clear Wired Glass (Thk.7mm) |  |  | -Door Lever -Cylinder Lockset -Door Closer -Door Stopper -Pivot Hinge -Flush Bolt
SACE1 | Central Control Building(RC) Battery Room |  | DDT22 | Blast Resistant Door_Double_Panic Bar |  | W2000xH2100 + W2000xH1000 | Steel | Steel | N.A | Panic |  |  |  | SACE1 | Central Control Building(RC) Battery Room | Blast Resistant Door | Type-C | 1800x2700 (1820x2710) | Min. THK 45 Galvanized Steel w/Paint *Blast -Overpressure : 0.81 PSI -Impulse 471.25 PSI-MS -Response Range : L -Performance Category : I | Galvanized Steel w/Paint Removable Transsom | N.A | Push Panic Bar (Inside) | 1.5 H | -Lever Handle -Mortise Lock -Master Key System -Door Stopper(Floor Type) -Butt Hinge -Gas Tight Seal(Heacy-Duty PVC Seal) -Door Closer -Door Bottom w/Rain Drip -Securuty Door Locck | External
Shutter / Sliding / Hanger / Swing / Revolving / Folding | [13 empty] | Shutter / Sliding / Hanger / Swing / Revolving / Folding
TVEP | Turbine Building(ST) |  | BD12 | Steel Roll Up Door_Motor |  | 0 | Steel | Steel | Motor |  |  |  |  | TVEP | Turbine Building(ST) |  |  | W7400 x H7000 | Sigle Skin Slat |  |  |  |  | Motor Operated | External Wind Resistance
HNCC | 154Kv Subtation |  | BD12 | Steel Roll Up Door_Motor |  | 0 | Steel | Steel | Motor |  |  |  |  | HNCC | 154Kv Subtation | GIS room에 설치 |  | 5000x4500 | [6 empty] | By Vendor
HNCC | Subcontractor Building |  | BD66 | Glass Folding(Accordion) Door_Manual |  | 0 | Glass Door | SST Frame | Motor |  |  |  |  | HNCC | Subcontractor Building | Folding door Mess Hall |  | 6500x2700 2640x2700 | Tempered Glass Thk9mm | Manufacturer's destails |  |  |  | Manufacturer's destails
HNCC | Process Control Building |  | BD26 | Glass Sliding Door_Motor |  | 0 | Glass Door | SST Frame | Motor |  |  |  |  | HNCC | Process Control Building | Sliding Door (Automatic Type w/Censor) |  | 1000x2200 | SSD w/Tempered Glass | Stainless Steel |  |  |  | Manufacturer Standard
HNCC | Process Control Building |  | BD26 | Glass Sliding Door_Motor |  | 0 | Glass Door | SST Frame | Motor |  |  |  |  | HNCC | Process Control Building | Sliding Door (Automatic Type w/Censor) |  | 2020x2510 | SSD w/Tempered Glass | Stainless Steel |  |  |  | Manufacturer Standard
HNCC | Subcontractor Building |  | BD26 | Glass Sliding Door_Motor |  | 0 | Glass Door | SST Frame | Motor |  |  |  |  | HNCC | Subcontractor Building | Sliding Door |  | 2000x2200 | SSD w/Tempered Glass | Stainless Steel |  |  |  | Manufacturer Standard

## Window Style
# B칼럼에는 노란색 행을 제외하면 콜론( : ) 이 들어가서는 안됨
팀 표준 Style Name & Numbering - Window
* Window Size, Fire Rating이 다른 경우 => 별도 구분 않함.
※ Window Style Schedule - |  | 기본 입력된 정보 | Style No.(Key Name) | Style Name | 표준Size(Ref.) | Glass 재질 | Frame 재질
※ Window Schedule - |  | 설계자의 설계 추가 입력 정보 | Int. or Ext 입력 | Fire Rating 입력
Sliding Type: | [7 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Window Style No | Window Style Name | Ref. Window Size | Window_Glass | Window_Frame | Window_Fire Rating |  | Window_Style Remark
Steel Window | WN11 | Steel Window_SG_Sliding |  | Single Glazing | Steel | NA/0.5/1.0 |  | WM : Single/Double Glazing 구분 없음, FR (NA/0.5H/1.0H) 구분
| WN12 | Steel Window_DG_Sliding |  | Double Glazing | Steel | NA/0.5/1.0
Aluminum Window | WN13 | Aluminum Window_SG_Sliding |  | Single Glazing | Aluminum | NA/0.5/1.0 |  | WM : Single/Double Glazing 구분 없음, FR (NA/0.5H/1.0H) 구분
| WN14 | Aluminum Window_DG_Sliding |  | Double Glazing | Aluminum | NA/0.5/1.0
uPVC Window | WN15 | uPVC Window_SG_Sliding |  | Single Glazing | uPVC |  |  | WM : Single/Double Glazing 구분 없음, FR 구분 없음
| WN16 | uPVC Window_DG_Sliding |  | Double Glazing | uPVC
Blast Resistant Window | WN17 | Blast Resistant Steel Window_Sliding | [5 empty] | WM : Blast Load: Overpressure ( )psi, Duration ( )ms
Bullet-Proof Steel Window | WN19 | Bullet-Proof Steel Window_Sliding
| N.A | N.A
기준 | WM : Window Type 추가 필요
WM : Glass Type 추가 필요
Awning Type: | [7 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Window Style No | Window Style Name | Ref. Window Size | Window_Glass | Window_Frame | Window_Fire Rating |  | Window_Style Remark
Steel Window | WN21 | Steel Window_SG_Awning |  | Single Glazing | Steel | NA/0.5/1.0 |  | WM : Single/Double Glazing 구분 없음, FR (NA/0.5H/1.0H) 구분
| WN22 | Steel Window_DG_Awning |  | Double Glazing | Steel | NA/0.5/1.0
Aluminum Window | WN23 | Aluminum Window_SG_Awning |  | Single Glazing | Aluminum | NA/0.5/1.0 |  | WM : Single/Double Glazing 구분 없음, FR (NA/0.5H/1.0H) 구분
| WN24 | Aluminum Window_DG_Awning |  | Double Glazing | Aluminum | NA/0.5/1.0
uPVC Window | WN25 | uPVC Window_SG_Awning |  | Single Glazing | uPVC |  |  | WM : Single/Double Glazing 구분 없음, FR 구분 없음
| WN26 | uPVC Window_DG_Awning |  | Double Glazing | uPVC
Blast Resistant Window | WN27 | Blast Resistant Steel Window_Awning | [5 empty] | WM : Blast Load: Overpressure ( )psi, Duration ( )ms
Bullet-Proof Steel Window | WN29 | Bullet-Proof Steel Window_Awning
| N.A | N.A
기준
Fix Type: | [7 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Window Style No | Window Style Name | Ref. Window Size | Window_Glass | Window_Frame | Window_Fire Rating |  | Window_Style Remark
Steel Window | WN31 | Steel Window_SG_Fix |  | Single Glazing | Steel | NA/0.5/1.0 |  | WM : Single/Double Glazing 구분 없음, FR (NA/0.5H/1.0H) 구분
| WN32 | Steel Window_DG_Fix |  | Double Glazing | Steel | NA/0.5/1.0
Aluminum Window | WN33 | Aluminum Window_SG_Fix |  | Single Glazing | Aluminum | NA/0.5/1.0 |  | WM : Single/Double Glazing 구분 없음, FR (NA/0.5H/1.0H) 구분
| WN34 | Aluminum Window_DG_Fix |  | Double Glazing | Aluminum | NA/0.5/1.0
| WN34A | Aluminum Window_DG_Low E_Fix |  | Double Glazing_Low E | Aluminum |  |  | WM 없음, Low E 사례 : 6mm Low E Glass (Out)+12mm(Argon)+6mm Clear Glass (In)
uPVC Window | WN35 | uPVC Window_SG_Fix |  | Single Glazing | uPVC |  |  | WM : Single/Double Glazing 구분 없음, FR 구분 없음
| WN36 | uPVC Window_DG_Fix |  | Double Glazing | uPVC
Blast Resistant Window | WN37 | Blast Resistant Steel Window_Fix | [5 empty] | WM : Blast Load: Overpressure ( )psi, Duration ( )ms
Bullet-Proof Steel Window | WN39 | Bullet-Proof Steel Window_Fix
| N.A | N.A
기준
Combination Type: | [7 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Window Style No | Window Style Name | Ref. Window Size | Window_Glass | Window_Frame | Window_Fire Rating |  | Window_Style Remark
Fix + Awning | WN41 | Steel Window_SG_Comb |  | Single Glazing | Steel | NA/0.5/1.0 |  | WM : Single/Double Glazing 구분 없음, FR (NA/0.5H/1.0H) 구분
| WN42 | Steel Window_DG_Comb |  | Double Glazing | Steel | NA/0.5/1.0
| WN43 | Aluminum Window_SG_Comb |  | Single Glazing | Aluminum | NA/0.5/1.0 |  | WM : Single/Double Glazing 구분 없음, FR (NA/0.5H/1.0H) 구분
| WN44 | Aluminum Window_DG_Comb |  | Double Glazing | Aluminum | NA/0.5/1.0
| WN44A | Aluminum Window_DG_Low E_Comb |  | Double Glazing_Low E | Aluminum |  |  | WM 없음, Low E 사례 : 6mm Low E Glass (Out)+12mm(Argon)+6mm Clear Glass (In)
| WN45 | uPVC Window_SG_Comb |  | Single Glazing | uPVC |  |  | WM : Single/Double Glazing 구분 없음, FR 구분 없음
| WN46 | uPVC Window_DG_Comb |  | Double Glazing | uPVC
| N.A | N.A
기준
Skylight: | [7 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Window Style No | Window Style Name | Ref. Window Size | Window_Glass | Window_Frame | Window_Fire Rating |  | Window_Style Remark
Skylight | WN71 | Skylight_FRP | [5 empty] | WM : FRP(Fiberglass Reinforced Plastics) Skylight
| WN72 | Skylight_Acrylic | [5 empty] | WM : Acrylic Skylight w/ Ventilation
| N.A | N.A
기준
MISC: | [7 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Window Style No | Window Style Name | Ref. Window Size | Window_Glass | Window_Frame | Window_Fire Rating |  | Window_Style Remark
| WN81 | Aluminum Window_DG_Casement
| WN91 | Aluminum Window_DG_Single Hung |  | Double Glazing | Aluminum
| WN91A | Aluminum Window_DG_Low E_Single Hung |  | Double Glazing_Low E | Aluminum
| WN95 | Aluminum Window_DG_Double Hung |  | Double Glazing | Aluminum
| WN101 | Aluminum Window_DG_Tilt
| WN111 | Aluminum Window_DG_Center Pivot
| N.A | N.A
기준
Louver: | [7 empty] | # 현재 시트에서 카테고리 구분의 기준이 되는 행 # 이름 변경 시 협의 필요(명칭 끝에 ':' 필요)
# | Window Style No | Window Style Name | Ref. Size | Window_Glass | Window_Frame | Window_Fire Rating |  | Window_Style Remark
Louver | LV11 | Louver_Aluminum |  | Aluminum | Aluminum
| LV12 | Louver_Steel |  | Steel | Steel
| N.A | N.A
기준

## Window 사례
팀 기준 사양 : Window | [11 empty] | 프로젝트 적용 현황
* 동일 Finish Material 의 두께, Size, 높이가 다른 경우 => 별도 구분 않함.
Project | Building | Description | Style Number | Style Name (Key Name) | Window Type | Size | Glass | Frame | Hardware | Fire Rating | Remark | Project | Building | Description | Window Type | Window Size (Opening) | Glass | Frame | Hardware | Fire Rating | Remark
Sliding Type | [11 empty] | Sliding Type
TVEP | Control Building(RC) |  | WN14 | Aluminum Window_DG_Sliding |  | 0 | Double Glazing | Aluminum |  |  |  | TVEP | Control Building(RC) |  | Type-1 | W1200 x H1200 | Double Glazing of Tempered Safety Glass (Thk.6mm Double w/ Thk.12mm Air Space) | Aluminum | Insect Screen | N.A | External
VEQU | CCB(ST) |  | WN14 | Aluminum Window_DG_Sliding |  | 0 | Double Glazing | Aluminum |  |  |  | VEQU | CCB(ST) | Aluminum Window |  | W2000 x H1000 | Double Glazing (Thk.6mm Double w/ Thk.6mm Air Space) | Aluminum | Insect Screen | N.A | External
Awning Type | [11 empty] | Awning Type
TVEP | Control Building(RC) |  | WN24 | Aluminum Window_DG_Awning |  | 0 | Double Glazing | Aluminum |  |  |  | TVEP | Control Building(RC) | Aluminum Window |  | W1200 x H600 | Double Glazing of Tempered Safety Glass (Thk.6mm Double w/ Thk.12mm Air Space) | Aluminum | Insect Screen | N.A | External
Fix Type | [11 empty] | Fix Type
SACE1 | Central Control Building(RC) Meeting Room |  | WN32 | Steel Window_DG_Fix |  | 0 | Double Glazing | Steel |  |  |  | SACE1 | Central Control Building(RC) Meeting Room | Steel Window | Type-B | W2000 x H1400 W : EQ=1000 x 2 (2020 x 1420) | Fire Rated Glazing | Galvanized Steel w/Paint |  | 0.75 H | Internal
SACE1 | Central Control Building(RC) Main Control Room |  | WN32 | Steel Window_DG_Fix |  | 0 | Double Glazing | Steel |  |  |  | SACE1 | Central Control Building(RC) Main Control Room | Steel Window | Type-D | W3280 x H1700 (3300 x 1720) | Fire Rated Glazing | Galvanized Steel w/Paint |  | 2.0 H | Internal
TVEP | Control Building(RC) |  | WN33 | Aluminum Window_SG_Fix |  | 0 | Single Glazing | Aluminum |  |  |  | TVEP | Control Building(RC) | Aluminum Window |  | W2400 x H750 | Clear Single Glass THK 6mm | Aluminum |  | N.A | External
HNCC | 154Kv Substation |  | WN32 | Steel Window_DG_Fix |  | 0 | Double Glazing | Steel |  |  |  | HNCC | 154Kv Substation | Steel Window |  | 1200x1200 | Double Glazed Insulated Glass | Steel Galvanized and Paint |  |  | External
HNCC | Laboratory Building |  | WN34A | Aluminum Window_DG_Low E_Fix |  | 0 | Double Glazing_Low E | Aluminum |  |  |  | HNCC | Laboratory Building | Aluminum Window |  | 1500x1900 | Double Glazed Insulated Glass (Low-E glass) Thick.24mm | Aluminum PVDF Coating |  |  | 국내법에 따른 소방관 진입창 용도임
Combination Type | [11 empty] | Combination Type
TVEP | Control Building(RC) |  | WN44 | Aluminum Window_DG_Comb |  | 0 | Double Glazing | Aluminum |  |  |  | TVEP | Control Building(RC) | Aluminum Window Awning + Fix |  | W1200 x H1200 | Double Glazing of Tempered Safety Glass (Thk.6mm Double w/ Thk.12mm Air Space) | Aluminum | Insect Screen | N.A | External
HNCC | Laboratory Building |  | WN44A | Aluminum Window_DG_Low E_Comb |  | 0 | Double Glazing_Low E | Aluminum |  |  |  | HNCC | Laboratory Building | Aluminum Window |  | 1500x1900 | Double Glazed Insulated Glass (Low-E glass) Thick.24mm | Aluminum PVDF Coating |  |  | 국내법에 따른 소방관 진입창 용도임
Skylight | [11 empty] | Skylight
|  |  | WN71 | Skylight_FRP |  | 0 | 0 | 0
MISC | [11 empty] | MISC
|  |  | WN81 | Aluminum Window_DG_Casement |  | 0 | 0 | 0
|  |  | WN91 | Aluminum Window_DG_Single Hung |  | 0 | Double Glazing | Aluminum
HNCC | Laboratory Building |  | WN91A | Aluminum Window_DG_Low E_Single Hung |  | 0 | Double Glazing_Low E | Aluminum |  |  |  | HNCC | Laboratory Building | Aluminum Window |  | 1500x1800 | Double Glazed Insulated Glass (Low-E glass) Thick.24mm | Aluminum PVDF Coating |  |  | 국내법에 따른 소방관 진입창 용도임
|  |  | WN101 | Aluminum Window_DG_Tilt |  | 0 | 0 | 0
|  |  | WN111 | Aluminum Window_DG_Center Pivot |  | 0 | 0 | 0
Louver | [11 empty] | Louver
|  |  | LV11 | Louver_Aluminum |  | 0 | Aluminum | Aluminum