## BOQ
7.4.3 BOQ
B. BOQ (Construction)
[P-NFFF] UAE 핵연료공장 건설사업_20220824 [ Rev. No : 01 ]
Discipline : Architecture | [17 empty] | August 24, 2022
NO. | Full Code | Gauge Code | WBS Name | Brief Spec. | Reference to | Unit | Total (Q'ty)
[8 empty] | Main Building | Administration Building | Workshop & Warehouse | Fire Brigade Building | Water Treatment Building | Main Gate House | Gas Storage Building | Fire Water Pump Building | Raw Water Pump Building | Covered Car Parking Shelter #1 | Covered Car Parking Shelter #2
1 | PACBB |  | EARTH WORKS
1) | PACBBA000010 |  | EXCAVATION | FROM GROUND TO 2M DEPTH | B-01 | M3 | 7048.52 | 6865.79 | [8 empty] | 134.13 | 48.6
2) | PACBBA000020 |  | EXCAVATION | BELOW 2M DEPTH | B-01 | M3 | 16927.33 | 11636.43 | 1461.14 | 652.74 | 1140.54 | 697.2 | 325.08 | 520.13 | 364.04 | 130.03
3) | PACBBB000010 | A | BACKFILL (GENERAL FILL) | SELECTED EXCAVATED SOIL | B-02 | M3 | 10699.76 | 7219.29 | 849.87 | 455.87 | 656.91 | 479.82 | 242.52 | 374.51 | 242.94 | 97.01 | 61.44 | 19.58
4) | PACBBD000010 |  | DISPOSAL |  | B-04 | M3 | 13276.1 | 11282.89 | 611.27 | 196.89 | 483.64 | 217.38 | 82.56 | 145.61 | 121.1 | 33.02 | 72.72 | 29.02
5) | PACBBG000010 |  | PE SHEET (VAPOR BARRIER) | THK. 0.1 mm, 2 LAYERS | B-06 | M2 | 12175.49 | 9980.74 | 576.64 | 246.88 | 453.55 | 267.56 | 114 | 194.56 | 140.44 | 45.6 | 116.64 | 38.88
6) | PACBBI000040 | A | BORED PILE (CFA, D600) | INCLUDING PRE-BORING | B-07 | M | 7452 |  | 1656 | 846 | 1314 | 792 | 540 | 792 | 432 | 216 | 648 | 216
7) | PACBBI000040 | C | BORED PILE (CFA, D1000) | INCLUDING PRE-BORING | B-09 | M | 11232 | 11232
8) | PACBBI00AAAA | A | PILE HEAD TREATMENT FOR BORED PILE (CFA, DIA.600mm) |  | B-10 | EA | 414 |  | 92 | 47 | 73 | 44 | 30 | 44 | 24 | 12 | 36 | 12
9) | PACBBI00AAAA | C | PILE HEAD TREATMENT FOR BORED PILE (CFA, DIA.1000mm) |  | B-12 | EA | 624 | 624
2 | PACBC |  | CONCRETE WORKS
1) | PACBCA000010 | B | CONCRETE (LEAN) | [UG] F'C = 18 MPA, W/CONSTRUCTION JOINT | C-01 | M3 | 1217.42 | 997.93 | 57.67 | 24.69 | 45.35 | 26.76 | 11.4 | 19.45 | 14.05 | 4.56 | 11.67 | 3.89
2) | PACBCA000020 | A | CONCRETE (STRUCTURAL) | [AG] F'C = 28 MPA, W/CONSTRUCTION JOINT | C-02 | M3 | 18575.87 | 15423.71 | 946.23 | 475.18 | 550 | 466.52 | 155.34 | 242.27 | 249.79 | 53.27 | 8.16 | 5.4
3) | PACBCA000020 | B | CONCRETE (STRUCTURAL) | [UG] F'C = 28 MPA, W/CONSTRUCTION JOINT | C-03 | M3 | 8504.22 | 6925.91 | 452.08 | 172.2 | 350.81 | 189.86 | 71.16 | 126.15 | 101.41 | 28.46 | 61.05 | 25.13
4) | PACBCB000010 |  | FORM WORKS | 1 TIMES, FAIR FACE FOR ABOVE GROUND | C-06 | M2 | 109267.1 | 85122.42 | 7144.44 | 3593 | 4217.36 | 3698 | 1218.43 | 1816.81 | 1926 | 443.34 | 59.4 | 27.9
5) | PACBCB000020 |  | FORM WORKS | 3 TIMES, GENERAL FOR UNDERGROUND | C-07 | M2 | 6519.88 | 3577.92 | 780.4 | 359.2 | 621.3 | 398.96 | 144.6 | 189.44 | 225.04 | 57.84 | 117 | 48.18
6) | PACBCC000010 | A | REINFORCEMENT | ASTM A615 GRADE 60 | C-05 | TON | 4162.13 | 3478.34 | 203.77 | 94.56 | 130.65 | 95.43 | 30.66 | 53.48 | 51.38 | 11.89 | 8.31 | 3.66
7) | PACBCE000030 | B | EXPANSION JOINT (EXPOSED TYPE) | FOR EXTERNAL WALL | C-12A | M | 87 | 87
8) | PACBCE000030 | C | EXPANSION JOINT (W/ STAINLESS STEEL COVER) | FOR INTERNAL FLOOR | C-12B | M | 549 | 549
9) | PACBCE000030 | D | EXPANSION JOINT (W/ STAINLESS STEEL COVER) | FOR CEILING & WALL | C-12C | M | 2243 | 2243
10) | PACBCE000030 | E | EXPANSION JOINT (W/ GALVANIZED STEEL COVER) | FOR PARAPET | C-12D | M | 183 | 183
11) | PACBCE000070 | B | CONTROL JOINT (FOR WALL) |  | C-14 | M | 1281.2 | 704 | 124.8 | 100.8 | 134.4 | 98.4 | 15.6 | 24 | 72 | 7.2
12) | PACBCG000010 |  | PROTECTION BOARD | FOR EXTERNAL WATERPROOFING AREA | C-10 | M2 | 7083.25 | 2684.44 | 1029.46 | 565.33 | 828.75 | 622.76 | 239.4 | 358.24 | 341.62 | 95.76 | 232.17 | 85.32
13) | PACBCH000010 |  | WATER STOP | PVC WATERSTOP | C-08 | M | 575.9 | 496.6 | 42 |  | 29.3 |  |  |  | 8
14) | PACBCI000010 |  | BITUTHENE MEMBRANES | FOR EXTERNAL WATERPROOFING [SHEET TYPE] | C-09 | M2 | 18366.46 | 12267.3 | 1491.26 | 796.69 | 1030.58 | 863.16 | 336.6 | 531.04 | 468.1 | 134.64 | 329.37 | 117.72
3 | PACBD |  | BLOCK WORKS
1) | PACBDB000010 |  | HOLLOW CONCRETE BLOCK(4") | W/LINTEL FOR OPENING | D-04 | M2 | 4422.94 |  | 1295.36 | 748.8 | 383.88 | 707 | 283.5 | 337.2 | 432 | 235.2
2) | PACBDB000020 |  | HOLLOW CONCRETE BLOCK(8") | W/LINTEL FOR OPENING | D-03 | M2 | 12399.3 | 6102 | 1490.4 | 1130.4 | 1024.8 | 630 | 526.5 | 762 | 498 | 235.2
3) | PACBDG000010 |  | INSULATION | ONLY FOR BLOCK WALL INSULATION | D-01 | M2 | 4085.74 |  | 1295.36 | 748.8 | 383.88 | 707 | 283.5 |  | 432 | 235.2
4) | PACBDK000010 | B | DAMP-PROOF COURSE | FOR EXTERNAL MASONRY WALL | D-02 | M | 462.25 |  | 64.8 | 48 | 59.75 | 28 | 66 | 84.5 | 72 | 39.2
4 | PACBE |  | PAINTING WORKS
1) | PACBEB000020 | A | EPOXY PAINT | INTERNAL WALL | E-09 | M2 | 9614.7 | 9614.7
2) | PACBEB000020 | B | EPOXY PAINT NUCLEAR (EPN) | INTERNAL WALL | E-05 | M2 | 15889.14 | 15889.14
3) | PACBEB000030 | A | EPOXY PAINT | CEILING | E-09 | M2 | 5828.5 | 5314 |  |  |  | 514.5
4) | PACBEB000030 | B | EPOXY PAINT NUCLEAR (EPN) | CEILING | E-05 | M2 | 5708 | 5708
5) | PACBEB000040 | A | EPOXY PAINT | FLOOR | E-10 | M2 | 8020.34 | 5838.2 | 75.52 | 340.8 | 424.45 | 550.25 |  | 443.12 | 275 | 73
6) | PACBEB000040 | B | EPOXY PAINT NUCLEAR (EPN) | FLOOR | E-06 | M2 | 6917.6 | 6917.6
7) | PACBEB00ZZZZ | A | EPOXY PAINT | SKIRT, H=100MM | E-11 | M | 789.4 |  | 67.2 | 176.8 | 155 | 70 |  | 187.2 | 94 | 39.2
8) | PACBEB00ZZZZ | B | EPOXY PAINT NUCLEAR (EPN) | SKIRT, H=100MM | E-07 | M | 88 | 88
9) | PACBEC000020 |  | ACID RESISTANT PAINT | FLOOR | E-13 | M2 | 70.4 | 56 | 14.4
10) | PACBEC000030 |  | ACID RESISTANT PAINT | INTERNAL WALL | E-14 | M2 | 234.92 | 165 | 69.92
11) | PACBEC000040 |  | ACID RESISTANT PAINT | CEILING | E-14 | M2 | 70.4 | 56 | 14.4
12) | PACBEC000050 |  | ACID RESISTANT PAINT | SKIRT, H=100MM | E-15 | M | 45.2 | 30 | 15.2
13) | PACBED000010 |  | WATER EMULSION PAINT | EXTERNAL WALL | E-16 | M2 | 7762.06 | 834.48 | 1633.28 | 998.4 | 1267.92 | 949.4 | 434.7 | 709.8 | 604.8 | 329.28
14) | PACBED000020 |  | WATER EMULSION PAINT | INTERNAL WALL | E-17 | M2 | 15302.04 | 6051.1 | 2987.96 | 1879.44 | 1547.6 | 427 | 486.54 | 1123.2 | 564 | 235.2
15) | PACBED000030 |  | WATER EMULSION PAINT | CEILING | E-17 | M2 | 2296.24 | 455 | 455.52 | 340.8 | 450.77 | 74.25 |  | 171.9 | 275 | 73
16) | PACBEE000010 |  | ANTI-DUST EPOXY PAINT | UNDER RAISED FLOOR | E-12 | M2 | 461.5 | 434 |  |  |  | 27.5
17) | PACBEL000020 |  | CHEMICAL RESISTANT EPOXY PAINT | INTERNAL WALL | E-19 | M2 | 1003 | 198 |  |  |  | 805
18) | PACBEL000040 |  | CHEMICAL RESISTANT EPOXY PAINT | FLOOR | E-18 | M2 | 766.5 | 252 |  |  |  | 514.5
5 | PACBF |  | TILE WORKS
1) | PACBFB000020 |  | GLAZED CERAMIC TILE | WALL W/ BEDDING, WIREMESH IF NECESSARY | F-11 | M2 | 2546.24 | 394.2 | 1513.28 | 109.08 | 289.98 | 120.9 | 118.8
2) | PACBFC000010 |  | UNGLAZED NON-SLIP CERAMIC TILE | FLOOR W/ BEDDING, WIREMESH IF NECESSARY | F-10 | M2 | 1421.94 | 617 | 518.2 | 49.2 | 141.94 | 55 | 40.6
3) | PACBFC000020 |  | UNGLAZED NON-SLIP CERAMIC TILE | SKIRTS, H=100MM. W/ BEDDING, WIREMESH IF NECESSARY | F-10 | M | 238.2 | 197 | 41.2
4) | PACBFD000010 |  | P.V.C TILE | FLOOR W/ BEDDING, WIREMESH IF NECESSARY | F-14 | M2 | 3176.38 | 2214 | 471.28 | 158.4 | 248.2 |  | 84.5
5) | PACBFD000020 |  | P.V.C TILE | SKIRTS W/ BEDDING, WIREMESH IF NECESSARY | F-16 | M | 2465.2 | 1487 | 487.2 | 142 | 202.8 | 46 | 100.2
6) | PACBFJ000010 |  | MARBLE TILE | FLOOR W/ BEDDING, WIREMESH IF NECESSARY | F-04 | M2 | 833 | 172 | 503.2 |  |  |  | 157.8
7) | PACBFJ000020 |  | MARBLE TILE | SKIRTS, H=100MM. W/ BEDDING, WIREMESH IF NECESSARY | F-05 | M | 495.2 | 50 | 365.2 |  |  |  | 80
6 | PACBG |  | WATERPROOFING WORKS
1) | PACBGA000010 |  | LIQUID WATERPROOFING | LIQUID+URETHANE, FOR INTERNAL FLOOR AREA | G-02 | M2 | 969.36 | 315 | 430.6 | 49.2 | 78.96 | 55 | 40.6
2) | PACBGA000020 |  | LIQUID WATERPROOFING | LIQUID+URETHANE, FOR INTERNAL WALL AREA | G-02 | M2 | 3070.92 | 1042 | 1513.28 | 109.08 | 166.86 | 120.9 | 118.8
3) | PACBGB000010 | B | Fire Sealing Compound (Fire Rating 3Hr) |  | L-22 | M3 | 7 | 7
4) | PACBGB000010 | C | Fire Sealing Compound (Fire Rating 1.5Hr) |  | L-23 | M3 | 14 | 14
7 | PACBH |  | ROOF WORKS
1) | PACBHA000010 | B | SLOPE MORTAR | W/ TROWELING, WITHOUT WIREMESH | H-09 | M3 | 1354.38 | 1113.12 | 72.35 | 38.02 | 37.17 | 48.83 | 15.82 | 9.45 | 16.04 | 3.58
2) | PACBHC000010 |  | WATERPROOFING MEMBRANE | FOR ROOF AREA ONLY | H-03 | M2 | 12442.99 | 8446.23 | 1080.16 | 638.4 | 681.72 | 690.6 | 284.3 | 205.62 | 318.2 | 97.76
3) | PACBHD000010 |  | RIGID INSULATION FOR ROOF (THK. 150mm) |  | H-01 | M2 | 11539.81 | 7988.25 | 995.68 | 576 | 582.48 | 630 | 246.5 | 171.9 | 275 | 74
4) | PACBHE000010 |  | PE SHEET (FOR ROOF) |  | H-04 | M2 | 11465.81 | 7988.25 | 995.68 | 576 | 582.48 | 630 | 246.5 | 171.9 | 275
5) | PACBHG000010 | A | CONCRETE TILE | WITH MORTAR BEDDING (20MM) | H-07 | M2 | 11465.81 | 7988.25 | 995.68 | 576 | 582.48 | 630 | 246.5 | 171.9 | 275
8 | PACBI |  | DOOR & WINDOW WORKS
1) | PACBIA000010 |  | STEEL DOOR (1000x2100) | SINGLE DOOR W/HARDWARE | I-03 | EA | 48 | 18 | 8 | 3 | 7 | 2 | 6 | 2 | 2
2) | PACBIA000020 | A | STEEL DOOR (2000x2100) | DOUBLE DOOR W/HARDWARE | I-03 | EA | 3 | 3
3) | PACBIA000020 | B | STEEL DOOR (2500x3000) | DOUBLE DOOR W/HARDWARE | I-03 | EA | 28 | 4 | 7 | 6 | 2 | 3 | 1 | 3 |  | 2
4) | PACBIA000020 | C | STEEL DOOR (2000x2100)_AIR TIGHT | DOUBLE DOOR W/HARDWARE | I-03A | EA | 1 | 1
5) | PACBIA000020 | D | STEEL DOOR (2500x3000)_AIR TIGHT | DOUBLE DOOR W/HARDWARE | I-03A | EA | 1 | 1
6) | PACBIE000010 |  | STAINLESS STEEL DOOR (1000x2100) | SINGLE DOOR W/HARDWARE | I-07 | EA | 6 | 6
7) | PACBIE000020 |  | STAINLESS STEEL DOOR (2500x3000) | DOUBLE DOOR W/HARDWARE | I-07 | EA | 10 | 10
8) | PACBIH000070 | A | STEEL DOOR W/90 MIN (1000x2100) | SINGLE DOOR W/HARDWARE | I-01 | EA | 49 | 15 | 9 | 6 | 11 | 3 | 2 | 3
9) | PACBIH000070 | B | STEEL DOOR W/90 MIN (1000x2100)_AIR TIGHT | SINGLE DOOR W/HARDWARE | I-01A | EA | 2 | 2
10) | PACBIH000070 | C | STEEL DOOR W/45 MIN (1000x2100) | SINGLE DOOR W/HARDWARE | I-01B | EA | 82 | 31 | 40 | 5 | 1 |  | 5
11) | PACBIH000070 | D | STEEL DOOR W/45 MIN (1000x2100)_AIR TIGHT | SINGLE DOOR W/HARDWARE | I-01C | EA | 4 | 4 | [10 empty] | Rev.1에서 추가됨
12) | PACBIH000080 | A | STEEL DOOR W/90 MIN (2000x2100) | DOUBLE DOOR W/HARDWARE | I-01 | EA | 10 | 10
13) | PACBIH000080 | B | STEEL DOOR W/90 MIN (2500x3000) | DOUBLE DOOR W/HARDWARE | I-01 | EA | 7 | 5 |  |  | 1 | 1
14) | PACBIH000080 | C | STEEL DOOR W/90 MIN (2000x2100)_AIR TIGHT | DOUBLE DOOR W/HARDWARE | I-01A | EA | 2 | 2
15) | PACBIH000080 | D | STEEL DOOR W/90 MIN (2500x3000)_AIR TIGHT | DOUBLE DOOR W/HARDWARE | I-01A | EA | 4 | 4
16) | PACBIH000080 | E | STEEL DOOR W/45 MIN (2000x2100) | DOUBLE DOOR W/HARDWARE | I-01B | EA | 6 | 5 | 1
17) | PACBIH000080 | F | STEEL DOOR W/45 MIN (2500x3000) | DOUBLE DOOR W/HARDWARE | I-01B | EA | 10 | 1 | 5 | 2 |  | 1 | 1
18) | PACBIH000130 | B | STEEL DOOR W/180 MIN (1000x2100)_AIR TIGHT | SINGLE DOOR W/HARDWARE | I-02A | EA | 36 | 36
19) | PACBIH000140 | C | STEEL DOOR W/180 MIN (2000x2100)_AIR TIGHT | DOUBLE DOOR W/HARDWARE | I-02A | EA | 15 | 15
20) | PACBIH000140 | D | STEEL DOOR W/180 MIN (2500x3000)_AIR TIGHT | DOUBLE DOOR W/HARDWARE | I-02A | EA | 15 | 15
21) | PACBIO000010 | A | SHUTTER (6000x6000) | W/HARDWARE | I-04 | EA | 7 | 1 |  |  | 6
22) | PACBIO000010 | B | SHUTTER (5000x5000) | W/HARDWARE | I-04 | EA | 6 | 4 |  | 2
23) | PACBIO000010 | C | SHUTTER (4000x4000) | W/HARDWARE | I-04 | EA | 10 | 7 |  |  |  | 1 |  |  | 2
24) | PACBIO000010 | D | SHUTTER (3000x3000) | W/HARDWARE | I-04A | EA | 2 | 2
25) | PACBIP000010 | C | ALUMINUM WINDOW (1200x1500) | DOUBLE GLASS W/HARDWARE | I-12 | EA | 11 |  | 1 | 2 | 5 | 1 | 2
26) | PACBIP000010 | D | ALUMINUM WINDOW (3000x1500) | SINGLE GLASS W/HARDWARE | I-13 | EA | 10 | 10
27) | PACBIP000010 | E | ALUMINUM WINDOW (1800x1500) | SINGLE GLASS W/HARDWARE | I-13 | EA | 10 | 10
28) | PACBIP000010 | F | ALUMINUM WINDOW (1200x1500) | SINGLE GLASS W/HARDWARE | I-13 | EA | 10 | 10
29) | PACBIP000010 | G | ALUMINUM WINDOW (500x1200) | SINGLE GLASS W/HARDWARE | I-13 | EA | 10 | 10
30) | PACBIP000010 | H | ALUMINUM WINDOW (2400x1500) | DOUBLE GLASS W/HARDWARE | I-12 | EA | 47 | 13 |  | 6 | 6 | 4 | 4 | 4 | 6 | 4
31) | PACBIP000010 | I | ALUMINUM WINDOW (1200x1500) (FIX + SLIDE) | DOUBLE GLASS W/HARDWARE | I-12 | EA | 39 | 12 | 11 | 2 | 7 | 4 | 3
32) | PACBIP000010 | J | ALUMINUM WINDOW (2400x1500) (FIX + SLIDE) | DOUBLE GLASS W/HARDWARE | I-12 | EA | 23 | 4 | 16 |  | 2 |  | 1
33) | PACBIP000010 | K | ALUMINUM WINDOW (3000x1500) (FIX + SLIDE) | DOUBLE GLASS W/HARDWARE | I-12 | EA | 42 | 35 | 5 |  | 2
34) | PACBIP000010 | L | ALUMINUM WINDOW (2400x1500)_RADIATION | DOUBLE GLASS W/HARDWARE | I-12A | EA | 10 | 10
35) | PACBIQ000010 |  | ALUMINUM LOUVER |  | I-14 | M2 | 0.45 |  |  |  |  | 0.45
36) | PACBIQ000030 | B | LOUVER (GALVANIZED STEEL) |  | I-16 | M2 | 9.29 |  |  | 5.4 | 2.76 | 0.81 | 0.32
37) | PACBIT000010 |  | MASTER KEY SYSTEM |  | I-11 | SET | 1 | 1
9 | PACBJ |  | EXTERIOR/INTERIOR FINISH WORKS
1) | PACBJA000020 |  | CARPET TILE | HIGH TRAFFIC CARPET TILE | F-09 | M2 | 272.4 | 186 | 86.4
2) | PACBJB000010 |  | GYPSUM BOARD | WALL | J-08 | M2 | 478.44 |  | 358.8 |  | 70.14 |  | 49.5
3) | PACBJB000020 |  | GYPSUM BOARD | WALL, 1.5HR FIRE-RATING. | J-09 | M2 | 1143.8 |  | 782 | 244.8 |  |  | 117
4) | PACBJC000040 |  | ACOUSTIC MINERAL BOARD CEILING |  | J-04 | M2 | 6639.29 | 4823.2 | 1060.88 | 158.4 | 301.31 | 66 | 229.5
5) | PACBJC000050 |  | PVC STRIP CEILING |  | J-05 | M2 | 505.01 | 198 | 138.2 | 49.2 | 62.51 | 16.5 | 40.6
6) | PACBJD000010 |  | EXTERNAL PLASTER | FOR EXTERNAL MASONRY WALL | J-01 | M2 | 2877.5 |  | 598 | 345.6 | 501.9 | 196 | 297 | 507 | 432
7) | PACBJD000020 |  | INTERNAL PLASTER | FOR INTERNAL MASONRY WALL | J-02 | M2 | 21445.62 | 12204 | 2380.96 | 1920.96 | 1543.5 | 1064 | 754.2 | 1014 | 564
8) | PACBJE000010 |  | RAISED FLOOR W/ VINYL TILE | H=600MM | J-14 | M2 | 461.5 | 434 |  |  |  | 27.5
9) | PACBJG000040 |  | GALVANIZED STEEL SHEET W/FLASHING IF NECESSORY | ROOF | J-12A | M2 | 1035 | 306 | [8 empty] | 477 | 252
10) | PACBJH000010 |  | SANDWICH PANEL W/FLASHING IF NECESSORY | WALL | J-13 | M2 | 7740.93 | 7674.33 | [5 empty] | 66.6
11) | PACBJH000020 |  | SANDWICH PANEL W/FLASHING IF NECESSORY | ROOF | J-12 | M2 | 271.22 | [6 empty] | 271.22
12) | PACBJI000010 |  | GUTTER | EAVE GUTTER. | J-15 | M | 19.1 | [6 empty] | 19.1
13) | PACBJJ000010 |  | CUBICLE PARTITION | FOR TOILET | J-11 | M2 | 290.26 | 163.76 | 64.4 | 16.1 | 16.1 | 13.8 | 16.1
14) | PACBJJ000020 |  | URINAL SCREEN |  | L-15 | EA | 35 | 17 | 6 | 3 | 3 | 3 | 3
15) | PACBJM000010 |  | STEEL TROWEL FINISH | FOR CONCRETE SURFACE | J-03 | M2 | 14666.34 | 12431.3 | 89.92 | 340.8 | 424.45 | 588.75 |  | 443.12 | 275 | 73
10 | PACBK |  | STEEL WORKS
1) | PACBKA000010 | A | STRUCTURAL STEEL (INDOOR STEEL) | ASTM A36 | K-01 | TON | 11.85 | 11.85
2) | PACBKA000010 | B | STRUCTURAL STEEL (INDOOR STEEL) | ASTM A992 | K-02 | TON | 134.97 | 121.67 | [5 empty] | 13.3
3) | PACBKA000010 | C | STRUCTURAL STEEL (OUTDOOR STEEL) | ASTM A36 | K-15 | TON | 106.43 | 66.49 | [8 empty] | 25.64 | 14.3
4) | PACBKA000010 | E | STRUCTURAL STEEL (FOR PURLIN & GIRTH) | ASTM A36 | K-01 | TON | 9.55 | [6 empty] | 2.5 |  |  | 4.7 | 2.35
5) | PACBKA000010 | F | STRUCTURAL STEEL (FOR CLADDING SUPPORT) | ASTM A36 | K-01A | TON | 61.31 | 61.31
6) | PACBKE000030 |  | ANCHOR BOLT | DIA 24MM, L=900 | K-03 | EA | 436 | 324 | [5 empty] | 40 |  |  | 72
7) | PACBKE000050 |  | ANCHOR BOLT | DIA 30MM, L=1200 | K-03 | EA | 24 | [10 empty] | 24
8) | PACBKF000010 |  | STEEL HANDRAIL | W/ PAINT (OR) HOT DIP GALVANIZED. | K-12 | M | 446.38 | 378 | 54.08 |  | 14.3
9) | PACBKG000010 | A | STEEL PAINTING (INDOOR STEEL) | FOR NON FIRE-PROOFED SURFACE, SECOND & FINAL COAT | K-05 | M2 | 2739.55 | 2166 | [5 empty] | 573.55
10) | PACBKG000010 | B | STEEL PAINTING (OUTDOOR STEEL) | FOR NON FIRE-PROOFED SURFACE, SECOND & FINAL COAT | K-05 | M2 | 1752.71 | [9 empty] | 1172.67 | 580.04
11) | PACBKG00AAAA | B | STEEL PAINTING (FIRE-PROOFED) | FOR-FIRE-PROOFED, PAINT TYPE (3.0HR) | K-07 | M2 | 3338.24 | 3338.24
12) | PACBKH000010 |  | CAGED LADDER (2.5m < H ≤ 10m) | HOT DIP GALVANIZED. | K-13 | M | 196.6 | 99.5 | 10 | 18.4 | 20.2 | 18 | 6.5 | 8 | 8 | 8
13) | PACBKI000020 |  | GRATING | THK.>=32MM, GALVANIZED | K-09 | M2 | 288 | 288
14) | PACBKK000010 |  | CHECKERED PLATE | GALVANIZED, | K-10 | M2 | 429.4 | 429.4
15) | PACBKL000010 |  | DECK PLATE | GALVANIZED. | K-08 | M2 | 1570 | 1570
16) | PACBKM000010 |  | GROUTING | NON-SHRINK CEMENT BASED GROUT. | K-04 | M3 | 0.35 | [6 empty] | 0.09 |  |  | 0.15 | 0.11
11 | PACBL |  | MISC. WORKS
1) | PACBLA000010 | A | ROOF DRAIN (DIA=100mm) | FOR BUILDING, CAST IRON | L-01 | EA | 82 |  | 16 | 14 | 10 | 10 | 8 | 8 | 10 | 6
2) | PACBLA000010 | B | ROOF DRAIN (DIA=150mm) | FOR BUILDING, CAST IRON | L-02 | EA | 38 | 38
3) | PACBLB000010 | A | DOWNSPOUT (DIA=100mm) | FOR BUILDING, GALV. STEEL. | L-05 | M | 568 |  | 147.2 | 100.8 | 70 | 70 | 36 | 48 | 60 | 36
4) | PACBLB000010 | B | DOWNSPOUT (DIA=150mm) | FOR BUILDING, GALV. STEEL. | L-06 | M | 879 | 879
5) | PACBLB000040 |  | DOWN SPOUT HEAD | GALVANIZED | L-09 | EA | 120 | 38 | 16 | 14 | 10 | 10 | 8 | 8 | 10 | 6
6) | PACBLC000010 |  | CONCRETE SPLASH BLOCK | CONCRETE BLOCK TYPE. | L-11 | EA | 120 | 38 | 16 | 14 | 10 | 10 | 8 | 8 | 10 | 6
7) | PACBLD000010 |  | STEEL FENCE |  | L-24 | M | 568.5 | 521 | [5 empty] | 47.5
8) | PACBLD000040 |  | FENCE DOOR |  | L-25 | EA | 2 | [6 empty] | 2
9) | PACBLE000020 |  | STEEL BOLLARD (REMOVABLE TYPE) |  | L-13 | EA | 38 | 10 | 4 | 4 | 12 | 2 | 2 |  | 4
10) | PACBLF000020 |  | ROOM SIGNAGE |  | L-14 | SET | 199 | 86 | 54 | 14 | 18 | 8 | 12 | 4 | 2 | 1
11) | PACBLI000020 |  | MIRROR / W GLASS SHELF |  | L-18 | EA | 26 | 15 | 5 | 2 | 1 | 1 | 2
12) | PACBLI000030 |  | SOAP DISPENSERS |  | L-20 | EA | 32 | 15 | 5 | 4 | 2 | 2 | 4
13) | PACBLI000050 |  | TOWEL BAR |  | L-19 | EA | 27 | 10 | 5 | 4 | 2 | 2 | 4
14) | PACBLI000090 |  | PAPER HOLDER |  | L-21 | EA | 39 | 22 | 5 | 4 | 2 | 2 | 4
15) | PACBLI00AAAA | D | VANITY TOP | 1 BOWL | L-17 | EA | 10 | 5 | 1 | 1 | 1 | 1 | 1
16) | PACBLI00AAAA | E | VANITY TOP | 2 BOWL | L-17 | EA | 20 | 10 | 2 | 2 | 2 | 2 | 2
17) | PACBLJ000010 |  | MISC STEEL | GALVANIZED. | L-12 | TON | 10 | 10

## Description
7.4.3 BOQ
C. MATERIAL BRIEF SPECIFICATION
[P-NFFF] UAE 핵연료공장 건설사업_20220824 [ Rev. No : 01 ]
Discipline : Architecture |  | August 24, 2022
B-01 | EXCAVATION - FOR GENERAL SOIL - GENERAL SOIL, BY HAND DIGGING OR BY MACHINERY EQUIPMENT WITHOUT USING JACK HAMMERS, DRILLS OR BLASTING EQUIPMENT - INCLUDING COMPACTION AT EXCAVATED LEVEL - INCLUDING PROTECTION MEASURE TO EXITING UTILITIES WHICH MAY BE ENCOUNTERED DURING THE WORK - INCLUDING DEWATERING WORK WITH A PROVISION OF SUMP AND PUMP, IF REQUIRED - INCLUDING SLOPE SHORING AND COVERING, IF REQUIRED - INCLUDING TRANSPORTATION TO THE TEMPORARY STOCK AREA INSIDE OF SITE DESIGNATED BY CONTRACTOR.
B-02 | BACK FILLING - SELECTED EXCAVATED SOIL - INCLUDING NECESSARY TEST AS PER SPEC. AND/OR LOCAL REGULATIONS - INCLUDING COMPACTION UP TO 95% OF MAXIMUM DRY DENSITY ACCORDING TO AASHTO T 180-METHOD D. - EACH LAYER SHALL NOT EXCEED 200mm AT LOOSE CONDITION - INCLUDING SCREENING FOR PROPER GRADATION. . MAX. PARTICLE SIZE : 10mm . FINE CONTENTS (LESS THAN 0.02mm) < 20% . PLASTICITY INDEX < 6% . LIQUID LIMIT < 25% - INCLUDING TRANSPORTATION FROM TEMPORARY STOCK AREA INSIDE OF SITE DESIGNED BY CONTRACTOR TO BACKFILLING AREA
B-03 | BACK FILLING - IMPORTED SOIL - INCLUDING NECESSARY TEST AS PER SPEC. AND/OR LOCAL REGULATIONS - INCLUDING COMPACTION UP TO 95% OF MAXIMUM DRY DENSITY ACCORDING TO AASHTO T 180-METHOD D. - EACH LAYER SHALL NOT EXCEED 200mm AT LOOSE CONDITION - IMPORTED MATERIAL TO BE SUPPLIED SHALL SATISFY WITH THE CRITERIA BELOW. . MAX. PARTICLE SIZE : 10mm . FINE CONTENTS (LESS THAN 0.02mm) < 20% . PLASTICITY INDEX < 6% . LIQUID LIMIT < 25% - INCLUDING TRANSPORTATION FROM THE SOIL MATERIAL SOURCE(AN APPROVED BORROW PIT) TO PROJECT SITE AND TRANSPORTATION FROM TEMPORARY STOCK AREA INSIDE OF SITE DESIGNATED BY CONTRACTOR TO BACKFILLING AREA
B-04 | DISPOSAL - OUTSIDE SITE - INCLUDING TRANSPORTATION OF SURPLUS/UNSUITABLE SOIL, WHICH WILL NOT BE USED FOR BACKFILLING AND/OR BANKING, FROM THE TEMPORARY STOCK AREA TO THE DISPOSAL AREA OUTSIDE THE PROJECT SITE - THE LICENSE FOR DISPOSAL SHALL BE OBTAINED BY SUBCONTRACTOR AND ROYALTY/FEE FOR DISPOSAL SHALL BE PAID BY SUBCONTRACTOR, AT ITS OWN EXPENSE. - INCLUDING SPREADING AND GRADING THE SOIL IN THAT DISPOSAL AREA. - LOCATION OF DISPOSAL AREA : IT SHALL BE VERIFIED AND CONFIRMED BY SUBCONTRACTOR.
B-05 | CRUSHED STONE - IMPORTED - INCLUDING TRANSPORTATION, LAYING, LEVELING AND COMPACTION OF CRUSHED STONE - Φ20~40mm
B-06 | VAPOUR BARRIER - THK. 0.15mm, P.E FILM 2 PLIES - FOR BELOW GROUND SLAB
B-07 | BORED PILE (CFA, D600) - CFA(CONTINUOUS FLIGHT AUGER) TYPE - CAST IN SITU CONCRETE FOR PILES : f’c = MIN. 35 MPa (AT 28 DAYS, CYLINDRICAL STRENGTH) - CEMENT TYPE : TYPE V CONFORMING TO ASTM C 150 - PILE DIAMETER : 600mm - PILE LENGTH : 18.0m (AVERAGE.) - INCLUDE REINFORCING BAR : MINIMUM 10% (TONS OF REBAR FOR CUBIC METER OF CONCRETE VOLUMES) - INCLUDING DEWATERING(IF REQUIRED) AND SITE CLEARANCE WORK. - ANY REQUIRED SHIFTING, ASSEMBLY AND DISMANTLING OF EQUIPMENT FOR CFA PILING DURING WORK SHALL BE INCLUDED IN UNIT PRICE OF CFA PILING. - CONSTRUCTION DEBRIS INCLUDING SOIL AND MUD WHICH ARE OCCURRED DURING PILING WORK SHALL BE DISPOSED IN ACCORDANCE WITH LOCAL REGULATIONS - INCLUDING ALL MATERIALS(CONCRETE, REBAR, AND ETC.), EQUIPMENT AND LABOR. - INCLUDING LEADING, LIFTING, AND INSTALLATION OF PILE - INCLUDING ALL DOCUMENT WORKS INCLUDING METHOD STATEMENT, ITP, AS-BUILT SURVEY REPORT AND OTHERS - INCLUDING ALL ACCESSORIES FOR PILING WORK - SONIC LOGGING TUBES : FOUR (4) STEEL PIPES OF INTERNAL DIA. NOT LESS THAN 50MM FOR ENTIRE LENGTH OF PILE TO BE INSTALLED IN ALL PILES | Rev.B_s1에서 추가됨
B-08 | BORED PILE (CFA, D800) - CFA(CONTINUOUS FLIGHT AUGER) TYPE - CAST IN SITU CONCRETE FOR PILES : f’c = MIN. 35 MPa (AT 28 DAYS, CYLINDRICAL STRENGTH) - CEMENT TYPE : TYPE V CONFORMING TO ASTM C 150 - PILE DIAMETER : 800mm - PILE LENGTH : 18.0m (AVERAGE.) - INCLUDE REINFORCING BAR : MINIMUM 10% (TONS OF REBAR FOR CUBIC METER OF CONCRETE VOLUMES) - INCLUDING DEWATERING(IF REQUIRED) AND SITE CLEARANCE WORK. - ANY REQUIRED SHIFTING, ASSEMBLY AND DISMANTLING OF EQUIPMENT FOR CFA PILING DURING WORK SHALL BE INCLUDED IN UNIT PRICE OF CFA PILING. - CONSTRUCTION DEBRIS INCLUDING SOIL AND MUD WHICH ARE OCCURRED DURING PILING WORK SHALL BE DISPOSED IN ACCORDANCE WITH LOCAL REGULATIONS - INCLUDING ALL MATERIALS(CONCRETE, REBAR, AND ETC.), EQUIPMENT AND LABOR. - INCLUDING LEADING, LIFTING, AND INSTALLATION OF PILE - INCLUDING ALL DOCUMENT WORKS INCLUDING METHOD STATEMENT, ITP, AS-BUILT SURVEY REPORT AND OTHERS - INCLUDING ALL ACCESSORIES FOR PILING WORK - SONIC LOGGING TUBES : FOUR (4) STEEL PIPES OF INTERNAL DIA. NOT LESS THAN 50MM FOR ENTIRE LENGTH OF PILE TO BE INSTALLED IN ALL PILES | Rev.B_s1에서 추가됨
B-09 | BORED PILE (CFA, D1000) - CFA(CONTINUOUS FLIGHT AUGER) TYPE - CAST IN SITU CONCRETE FOR PILES : f’c = MIN. 35 MPa (AT 28 DAYS, CYLINDRICAL STRENGTH) - CEMENT TYPE : TYPE V CONFORMING TO ASTM C 150 - PILE DIAMETER : 1000mm - PILE LENGTH : 18.0m (AVERAGE.) - INCLUDE REINFORCING BAR : MINIMUM 10% (TONS OF REBAR FOR CUBIC METER OF CONCRETE VOLUMES) - INCLUDING DEWATERING(IF REQUIRED) AND SITE CLEARANCE WORK. - ANY REQUIRED SHIFTING, ASSEMBLY AND DISMANTLING OF EQUIPMENT FOR CFA PILING DURING WORK SHALL BE INCLUDED IN UNIT PRICE OF CFA PILING. - CONSTRUCTION DEBRIS INCLUDING SOIL AND MUD WHICH ARE OCCURRED DURING PILING WORK SHALL BE DISPOSED IN ACCORDANCE WITH LOCAL REGULATIONS - INCLUDING ALL MATERIALS(CONCRETE, REBAR, AND ETC.), EQUIPMENT AND LABOR. - INCLUDING LEADING, LIFTING, AND INSTALLATION OF PILE - INCLUDING ALL DOCUMENT WORKS INCLUDING METHOD STATEMENT, ITP, AS-BUILT SURVEY REPORT AND OTHERS - INCLUDING ALL ACCESSORIES FOR PILING WORK - SONIC LOGGING TUBES : FOUR (4) STEEL PIPES OF INTERNAL DIA. NOT LESS THAN 50MM FOR ENTIRE LENGTH OF PILE TO BE INSTALLED IN ALL PILES | Rev.B_s1에서 추가됨
B-10 | BORED PILE (CFA, D600) - THIS WORK IS APPLIED TO PILE HEAD TREATMENT FOR READY TO START PILE CAP AND FURTHER FOOTING CONCRETE WORKS. - FURNISHING ALL EQUIPMENT AND MATERIALS REQUIRED TREATING THE PILE HEAD. - THE WORK COVERS EXCAVATION, CHIPPING OF PILE HEAD, BENDING, CUTTING AND/OR SPLICING REINFORCING BAR OF PILES IN ACCORDANCE WITH SPECIFIED DRAWINGS AND SPECIFICATION. - DISPOSAL OF THE CONSTRUCTION DEBRIS RELATED TO PILE HEAD TREATMENT WORK TO THE DISPOSAL AREA AND CLEANING OF THE WORK SITE. - INCLUDING PILE CUTTING AND PILE HEAD TREATMENT
B-11 | BORED PILE (CFA, D800) - THIS WORK IS APPLIED TO PILE HEAD TREATMENT FOR READY TO START PILE CAP AND FURTHER FOOTING CONCRETE WORKS. - FURNISHING ALL EQUIPMENT AND MATERIALS REQUIRED TREATING THE PILE HEAD. - THE WORK COVERS EXCAVATION, CHIPPING OF PILE HEAD, BENDING, CUTTING AND/OR SPLICING REINFORCING BAR OF PILES IN ACCORDANCE WITH SPECIFIED DRAWINGS AND SPECIFICATION. - DISPOSAL OF THE CONSTRUCTION DEBRIS RELATED TO PILE HEAD TREATMENT WORK TO THE DISPOSAL AREA AND CLEANING OF THE WORK SITE. - INCLUDING PILE CUTTING AND PILE HEAD TREATMENT
B-12 | BORED PILE (CFA, D1000) - THIS WORK IS APPLIED TO PILE HEAD TREATMENT FOR READY TO START PILE CAP AND FURTHER FOOTING CONCRETE WORKS. - FURNISHING ALL EQUIPMENT AND MATERIALS REQUIRED TREATING THE PILE HEAD. - THE WORK COVERS EXCAVATION, CHIPPING OF PILE HEAD, BENDING, CUTTING AND/OR SPLICING REINFORCING BAR OF PILES IN ACCORDANCE WITH SPECIFIED DRAWINGS AND SPECIFICATION. - DISPOSAL OF THE CONSTRUCTION DEBRIS RELATED TO PILE HEAD TREATMENT WORK TO THE DISPOSAL AREA AND CLEANING OF THE WORK SITE. - INCLUDING PILE CUTTING AND PILE HEAD TREATMENT
C-01 | LEAN CONCRETE - f'c=18MPa (CYLINDRICAL STRENGTH) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE V - FOR LEAN CONC, BLINDING, SCREED, BACKFILL - INCLUDING MARKING, LEVELING, SCAFFOLDING, STAGING, CURING & TESTING - INCLUDING POURING & VIBRATING WORK - INCLUDING SMOOTH CONCRETE FINISHING - INCLUDING ALL CONSTRUCTION AND JOINTS WORK - INCLUDING LABOR & EQUIPMENT FOR ERECTION - INCLUDING CRACKED REPAIR & REQUIRED DAMAGED SURFACE - INCLUDING EMBEDDING MATERIALS IN CONCRETE AND TEMPLATE - INCLUDING TESTING, SUPERVISION, INSPECTION AT SITE - INCLUDING CONVEY OF CONCRETE FROM BATCH PLANT TO THE PLACE OF FINAL DEPOSIT - INCLUDING STORAGE/MAINTENANCE/PRESERVATION OF ALL CONCRETE MATERIALS AT SUBCONTRACTOR'S WAREHOUSE OR STORAGE AREA
C-02 | REINF. CONCRETE (ABOVE) - f'c=28MPa (CYLINDRICAL STRENGTH) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE V - ABOVE GROUND STRUCTURES - INCLUDING MARKING, LEVELING, SCAFFOLDING, STAGING, CURING & TESTING - INCLUDING POURING & VIBRATING WORK - INCLUDING SMOOTH CONCRETE FINISHING - INCLUDING ALL CONSTRUCTION AND JOINTS WORK - INCLUDING LABOR & EQUIPMENT FOR ERECTION - INCLUDING CRACKED REPAIR & REQUIRED DAMAGED SURFACE - INCLUDING EMBEDDING MATERIALS IN CONCRETE AND TEMPLATE - INCLUDING TESTING, SUPERVISION, INSPECTION AT SITE - INCLUDING CONVEY OF CONCRETE FROM BATCH PLANT TO THE PLACE OF FINAL DEPOSIT - INCLUDING STORAGE/MAINTENANCE/PRESERVATION OF ALL CONCRETE MATERIALS AT SUBCONTRACTOR'S WAREHOUSE OR STORAGE AREA
C-03 | REINF. CONCRETE (UNDER) - f'c=28MPa (CYLINDRICAL STRENGTH) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE V - BELOW GROUND STRUCTURES - STRUCTURES CONTACTED WITH SOIL - INCLUDING MARKING, LEVELING, SCAFFOLDING, STAGING, CURING & TESTING - INCLUDING POURING & VIBRATING WORK - INCLUDING SMOOTH CONCRETE FINISHING - INCLUDING ALL CONSTRUCTION AND JOINTS WORK - INCLUDING LABOR & EQUIPMENT FOR ERECTION - INCLUDING CRACKED REPAIR & REQUIRED DAMAGED SURFACE - INCLUDING EMBEDDING MATERIALS IN CONCRETE AND TEMPLATE - INCLUDING TESTING, SUPERVISION, INSPECTION AT SITE - INCLUDING CONVEY OF CONCRETE FROM BATCH PLANT TO THE PLACE OF FINAL DEPOSIT - INCLUDING STORAGE/MAINTENANCE/PRESERVATION OF ALL CONCRETE MATERIALS AT SUBCONTRACTOR'S WAREHOUSE OR STORAGE AREA
C-04 | HIGH YIELD DEFORMED BAR (EPOXY COATED) - ASTM A615 GRADE 60 (Fy=420MPa) OR EQUIVALENT - FUSION BONDED EPOXY COATED REINFORCING BAR(ASTM A775) - INCLUDING PRESSURE WELDED JOINT WORK WHERE NECESSARY & STRENGTH TEST - INCLUDING BAR SUPPORTS, TIE WIRES, SPACER, FABRICATED BAR MESH - INCLUDING RE-BAR SHOP DRAWING & BAR BENDING SCHEDULE - INCLUDING BAR BENDING & CUTTING - INCLUDING SLIP ROUND BAR AT SEPARATION JOINT - INCLUDING LABOR & EQUIPMENT - INCLUDING SITE INSPECTION
C-05 | HIGH YIELD DEFORMED BAR (BLACK DEFORMED BARS) - ASTM A615 GRADE 60 (Fy=420MPa) OR EQUIVALENT - INCLUDING PRESSURE WELDED JOINT WORK WHERE NECESSARY & STRENGTH TEST - INCLUDING BAR SUPPORTS, TIE WIRES, SPACER, FABRICATED BAR MESH - INCLUDING RE-BAR SHOP DRAWING & BAR BENDING SCHEDULE - INCLUDING BAR BENDING & CUTTING - INCLUDING SLIP ROUND BAR AT SEPARATION JOINT - INCLUDING LABOR & EQUIPMENT - INCLUDING SITE INSPECTION
C-06 | FAIR FACED FORM - FOR EXPOSED SUPERSTRUCTURE FORM FACE / PAINTED CONCRETE FORM FACE - FOR EQUIPMENT PLINTH AND FLOOR OPENING - COATED PLYWOOD THK. 18MM, 3 USE - INCLUDING, FORM TIE, ALL ACCESSORIES, SEALING OF FORM TIE HOLE, SEPARATOR & ANCHOR BOX OUT. - INCLUDING CHAMFER FOR EXPOSED EDGE - INCLUDING FLOOR AND WALL OPENING WORK & SLEEVE - INCLUDING BOXOUT FOR EQUIPMENT ANCHOR BOLT - INCLUDING LABOR & EQUIPMENT - INCLUDING FABRICATION / FORM INSTALL & REMOVAL - INCLUDING SHORING, SCAFFORDING AND SAFETY MEASURES
C-07 | NORMAL FACED FORM - FOR UNDERGROUND CONCRETE - FOR HIDDEN SURFACE & APPLIED FINISHING CONCRETE FORM FACE (EXCLUDE PAINTED CONCRETE FORM FACE) - NORMAL PLYWOOD THK. 18MM, 6 USE - INCLUDING, FORM TIE, ALL ACCESSORIES, SEALING OF FORM TIE HOLE, SEPARATOR & ANCHOR BOX OUT. - INCLUDING CHAMFER FOR EXPOSED EDGE - INCLUDING FLOOR AND WALL OPENING WORK & SLEEVE - INCLUDING BOXOUT FOR EQUIPMENT ANCHOR BOLT - INCLUDING LABOR & EQUIPMENT - INCLUDING FABRICATION / FORM INSTALL & REMOVAL - INCLUDING SHORING, SCAFFORDING AND SAFETY MEASURE
C-08 | PVC WATERSTOP - W = 150, THK 9mm FOR FLAT DUMBBELL - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING HEAVY DUTY FLEXIBLE P.V.C. WITH A CENTRAL EXPANSION BULB
C-09 | UNDERGROUND BITUMEN MEMBRANE - FLEXIBLE MULTY LAYERED COMPOSITE SHEET - FELT MEMBRANE BONDED TO BITUMEN/POLYMER ADHESIVE - FOR ALL UNDERGROUND CONCRETE SURFACE - INCLUDING SEALING JOINT WORK ; RAKING OUT OF WALL & FILLING W/ BITUMEN SEALING COMPOUND - FOR WRAPPING ALL UNDERGROUND FOUNDATION / CONC. STRUCTURE - INCLUDING AEROFOIL OR SIMILAR - INCLUDE'G ALUMINUM FLASHING ACCORDING TO SPEC. - REFER TO TECHNICAL SPEC.
C-10 | PROTECTION BOARD - BITUMEN IMPREGNATED FIBRE BOARD - THK. 6mm - FOR SIDE & TOP SIDE - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK
C-11 | SEPARATION JOINT - FOR AROUND GRADE SLAB - THK. 12 x 12 / SEALANT W/ BACKING ROD FORM - AS PER BS 6093 - INCLUDING PREMOULDED FILLER
C-12 | EXPANSION JOINT - FOR EXTERNAL/INTERNAL FLOOR - THK. 25mm x 25mm OIL RESISTANT SEALANT W/ BACKING ROD FORM - AS PER BS 6093 - INCLUDING PREMOULDED FILLER
C-12A | EXPANSION JOINT (EXPOSED TYPE) - FOR EXTERNAL WALL - THK. 50MM - INCLUDING FLEXIBLE JOINT FILLER, SEALANT, BACK-UP ROD
C-12B | EXPANSION JOINT (W/ STAINLESS STEEL COVER) - FOR INTERNAL FLOOR - THK. 50MM - INCLUDING FLEXIBLE JOINT FILLER, SEALANT, BACK-UP ROD, SST FLASHING COVER W/ FIXING ACCESSORIES, CORNER ANGLE/ANCHOR
C-12C | EXPANSION JOINT (W/ STAINLESS STEEL COVER) - FOR CEILING & WALL - THK. 50MM - INCLUDING FLEXIBLE JOINT FILLER, SEALANT, BACK-UP ROD, SST FLASHING COVER W/ FIXING ACCESSORIES, CORNER ANGLE/ANCHOR
C-12D | EXPANSION JOINT (W/ GALVANIZED STEEL COVER) - FOR PARAPET - THK. 50MM - INCLUDING FLEXIBLE JOINT FILLER, SEALANT, BACK-UP ROD, GALVANIZED STEEL FLASHING COVER W/ FIXING ACCESSORIES
C-13 | CONTROL JOINT (FOR FLOOR) - FOR FLOOR OF HEAVY DUTY TRAFFIC - THK. 6mm x 6mm OIL RESISTANT SEALANT W/ BACKING ROD FORM - INCLUDING SAW CUTTING OF CONC.
C-14 | CONTROL JOINT (FOR WALL) - FOR VERTICAL & HOR. WALL JOINT - THK. 10mm x 10mm 2-PART POLYSULPHIDE BASED SEALANT W/ BACKING ROD FORM - INCLUDING SAW CUTTING OF CONC.
C-15 | UNDERGROUND BITUMEN EMULSION PAINT - FOR UNDERGROUND CONCRETE PROTECTION - MASTER SEAL 420 OR EQUIVALENT - 2 COATS - NORMAL DRY CONDITION - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK
D-01 | INSULATION FOR CAVITY WALL - THK.100mm GLASSWOOL (MIN. 64kg/m3 DENSITY) - CLASS A (FLAME SPREAD INDEX 0~25, SMOKE DEVELOPED INDEX 0~450), IN ACCORDANCE WITH NFPA 255 - INCLUDING FIXING ACCESSORIES - INCLUDING SCAFFOLDING
D-02 | DAMP-PROOF COURSE - ALUMINUM CORED BITUMENISED HESSIAN COVERED SHEET : BS 743, W=350mm - HORIZONTAL: BOTTOM OF ALL BLOCKWORK INCLUDING 12MM THICK CEMENT MORTAR - VERTICAL: ALL DOOR & WINDOW REVEALS - THE DAMP PROOF MEMBRANE SHALL BE LAPPED AND BE FULLY BONDED TO A DAMP PROOF COURSE IN THE PLINTH WALL
D-03 | HOLLOW CONC. BLOCK (8") - TYPE I AS PER ASTM C90 - MORTAR : Min. COMPRESSIVE STRENGTH OF 175kg/m2 at 28 DAYS, ASTM C270 - PORTLAND CEMENT : ASTM C150, TYPE l - AGGREGATES : ASTM C144 - WALL TIE : GALVANIZED STEEL, ASTM A153 CLASS B2 OR EQUIVALANT : FISHTAILED TYPE (150 mm x 75mm) : Max. @450mm (VERTICAL) : Max. @900mm (HORIZONTAL) - WALL LUG : BUTTERFLY TYPE : Max. @450mm (VERTICAL) - INCLUDING GALV. ANCHOR, TIES, LUGS - INCLUDING METAL LATH (Min.300mm Wide) - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING VERTICAL JOINTS POINTED FLUSH AND HORIZONTAL JOINTS POINTED STRUCK FOR FAIR FACED CONC. BLOCK ONLY - INCLUDING GALV. ANCHOR STRIP TO BE WELDED TO STEEL - INCLUDING SOLID CONC. BLOCK FOR END BLOCKS - INCLUDING HEADER, STIFF COLUMN, LINTEL, CONC. FRAME FOR LARGE OPENING - INCLUDING SEISMIC REINFORCEMENT BAR (VERTICAL, HORIZONTAL)
D-04 | HOLLOW CONC. BLOCK (4") - TYPE I AS PER ASTM C90 - MORTAR : Min. COMPRESSIVE STRENGTH OF 175kg/m2 at 28 DAYS, ASTM C270 - PORTLAND CEMENT : ASTM C150, TYPE l - AGGREGATES : ASTM C144 - WALL TIE : GALVANIZED STEEL, ASTM A153 CLASS B2 OR EQUIVALANT : FISHTAILED TYPE (150 mm x 75mm) : Max. @450mm (VERTICAL) : Max. @900mm (HORIZONTAL) - WALL LUG : BUTTERFLY TYPE : Max. @450mm (VERTICAL) - INCLUDING GALV. ANCHOR, TIES, LUGS - INCLUDING METAL LATH (Min.300mm Wide) - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING VERTICAL JOINTS POINTED FLUSH AND HORIZONTAL JOINTS POINTED STRUCK FOR FAIR FACED CONC. BLOCK ONLY - INCLUDING GALV. ANCHOR STRIP TO BE WELDED TO STEEL - INCLUDING SOLID CONC. BLOCK FOR END BLOCKS - INCLUDING HEADER, STIFF COLUMN, LINTEL, CONC. FRAME FOR LARGE OPENING - INCLUDING SEISMIC REINFORCEMENT BAR (VERTICAL, HORIZONTAL)
E-01 | ACRYLIC PAINT (EXT.) - FOR EXT. WALL - 1 COAT PRIMER - 2 COATS ACRYLIC PAINT - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-02 | ACRYLIC PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT PRIMER - 2 COATS ACRYLIC PAINT - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-03 | ACRYLIC PAINT (BASE) - FOR BASE PAINT H=100mm - 1 COAT PRIMER - 2 COATS ACRYLIC PAINT - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-04 | EPOXY PAINT NUCLEAR (EXT.) - FOR EXT. WALL - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-05 | EPOXY PAINT NUCLEAR (INT.) - FOR INT. WALL & CEILING - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-06 | EPOXY PAINT NUCLEAR (FLOOR) - FOR INT. FLOOR - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION- TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-07 | EPOXY PAINT NUCLEAR (BASE) - FOR BASE PAINT H=100mm - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-08 | EPOXY PAINT (EXT.) - FOR EXT. WALL - 1 COAT PRIMER - 2 COATS EPOXY POLYAMIDE - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-09 | EPOXY PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT PRIMER - 2 COATS EPOXY POLYAMIDE - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-10 | EPOXY PAINT (FLOOR) - FOR INTERIOR FLOOR - 1 COAT PRIMER - 2 COATS EPOXY POLYAMIDE - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION- TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-11 | EPOXY PAINT (BASE) - FOR BASE PAINT H=100mm - 1 COAT PRIMER - 2 COATS EPOXY POLYAMIDE - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-12 | EPOXY PAINT (DUST PROOF) - FOR BENEATH OF FALSE FLOOR - 1 COAT PRIMER - 1 COATS EPOXY POLYAMIDE - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-13 | ACID RESISTANT PAINT (FLOOR) - FOR INTERIOR FLOOR - 1 COAT CHLORINATED RUBBER PRIMER - 2 COATS CHLORINATED RUBBER HIGH BUILD - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-14 | ACID RESISTANT PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT CHLORINATED RUBBER PRIMER - 2 COATS CHLORINATED RUBBER HIGH BUILD - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-15 | ACID RESISTANT PAINT (BASE.) - FOR BASE PAINT H=100mm - 1 COAT CHLORINATED RUBBER PRIMER - 2 COATS CHLORINATED RUBBER HIGH BUILD - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-16 | EMULSION PAINT (EXT.) - FOR EXT. WALL - 1 COAT PRIMER - 2 COATS EMULSION PAINT - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-17 | EMULSION PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT PRIMER - 2 COATS EMULSION PAINT - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-18 | CHEMICAL RESISTANT EPOXY PAINT (FLOOR) - FOR INTERIOR FLOOR - 1 COAT EPOXY PRIMER / SEALER - 2 COATS PHENOLIC EPOXY - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-19 | CHEMICAL RESISTANT EPOXY PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT EPOXY PRIMER / SEALER - 2 COATS PHENOLIC EPOXY - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
E-20 | SURFACE HARDENER - FOR INTERIOR FLOOR - HEAVY DUTY FLOOR CHEMICAL SURFACE HARDENER ANTI-DUST FINISH - GRANOLITE® NON-METALLIC FLOOR HARDENER - INCLUDING STEEL TROWEL FINISHING AND/OR MECHANICAL PLACING & FINISHING - INCLUDING JOINT GROUTING - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION - USAGE RATE 5 KG/M2. - INCLUDING ONE COAT OF SEALBOND GR’ CURING COMPOUND.
F-01 | GRANITE TILE - FOR FLOOR - THK. 30mm - INCLUDING BEDDING & JOINT GROUTING - INCLUDING GRINDING WORK & POLISHING - INCLUDING ADHESIVE
F-02 | GRANITE TILE - FOR WALL - THK. 20mm - INCLUDING 3mm THICK REAL CEMENT PASTE OR ADHESIVE & JOINT GROUTING - INCLUDING STEEL ANCHORING & ACCESSARIES & SEALANT - INCLUDING ADHESIVE & JOINT GROUTING - INCLUDING SCAFFOLDING - INCLUDING GRANITE SKIRTING (H=100)
F-03 | GRANITE STAIR TREAD & RISER - THK. 20mm - INCLUDING ANTI-SLIP GROOVE ON TREAD - INCLUDING BEDDING MORTAR & JOINT GROUTING - INCLUDING ADHESIVE - INCLUDING POLISHING
F-04 | MARBLE TILE - FOR FLOOR - THK. 30mm - INCLUDING BEDDING & JOINT GROUTING - INCLUDING GRINDING WORK & POLISHING - INCLUDING ADHESIVE
F-05 | MARBLE TILE - FOR WALL & BASE - THK. 20mm - INCLUDING 3mm THICK REAL CEMENT PASTE OR ADHESIVE & JOINT GROUTING - INCLUDING STEEL ANCHORING & ACCESSARIES & SEALANT - INCLUDING ADHESIVE & JOINT GROUTING - INCLUDING SCAFFOLDING - INCLUDING GRANITE SKIRTING (H=100)
F-06 | MARBLE STAIR TREAD & RISER - THK. 20mm - INCLUDING ANTI-SLIP GROOVE ON TREAD - INCLUDING BEDDING MORTAR & JOINT GROUTING - INCLUDING ADHESIVE - INCLUDING POLISHING
F-07 | GRANITE / MARBLE SILL - THK. 30mm - FOR WINDOW SILL OR DIVIDING STRIP - INCLUDING BEDDING & JOINT GROUTING - INCLUDING ADHESIVE
F-08 | ANTI-STATIC VINYL TILE - ANTI-STATIC PVC FLOOR TILES (400mmx400mm, THK. 3mm) - INCLUDING ADHESIVE, WELDING - INCLUDING POLISHING WORK
F-09 | CARPET TILE - FOR FLOOR (THK. 7mm) - ANTISTATIC - POLYPROPYLENE YARN IN LOOP-PILE (1/10") - INCLUDING ADHESIVE & SURFACE TREATMENT
F-10 | UNGLAZED NON-SLIP CERAMIC TILE - FOR FLOOR - THK. 7mm / NON-SLIP TYPE - INCLUDING NON-SLIP NOSING - INCLUDING BEDDING MORTAR & JOINT GROUTING & SEALANT - INCLUDING ADHESIVE & POLISHING
F-11 | GLAZED CERAMIC TILE - FOR WALL - THK. 6mm - INCLUDING BEDDING MORTAR & JOINT GROUTING - INCLUDING 3mm THICK REAL CEMENT PASTE OR ADHESIVE & JOINT GROUTING & SEALANT - INCLUDING SCAFFOLDING - INCLUDING ADHESIVE & POLISHING
F-12 | ACID RESISTANT TILE - FOR FLOOR - THK. 300 x 300 x 16mm - INCLUDING ACID PROOF MEMBRANE, BEDDING, EPOXY BASED ADHESIVE & JOINT GROUTING - INCLUDING POLISHING
F-13 | ACID RESISTANT TILE - FOR WALL - THK. 300 x 300 x 16mm - INCLUDING ACID PROOF MEMBRANE, EPOXY BASED ADHESIVE & JOINT GROUTING - INCLUDING SCAFFOLDING - INCLUDING POLISHING
F-14 | P.V.C TILE - PVC FLOOR TILES (400mm X 400mm ,THK. 3mm) - INCLUDING ADHESIVE - INCLUDING POLISHING
F-15 | P.V.C STAIR TREAD & RISER - H100mm x THK. 3mm - INCLUDING METAL EDGE STRIPS - INCLUDING NON-SLIP NOSING - INCLUDING ADHESIVE - INCLUDING POLISHING
F-16 | P.V.C SKIRTING - H100mm x THK. 2mm - INCLUDING ADHESIVE
F-17 | TERRAZZO TILE - FOR FLOOR - THK. 30mm - INCLUDING BEDDING & JOINT GROUTING - INCLUDING POLISHING - INCLUDING ADHESIVE - INCLUDING GRINDING WORK
F-18 | TERRAZZO STAIR TREAD & RISER - THK. 30mm - INCLUDING ANTI-SLIP GROOVE ON TREAD - INCLUDING BEDDING & JOINT GROUTING - INCLUDING ADHESIVE - INCLUDING POLISHING
F-19 | TERRAZZO SKIRTING - H100 x 20 mm - INCLUDING BEDDING & JOINT GROUTING - INCLUDING GRINDING WORK - INCLUDING ADHESIVE
G-01 | MEMBRANE SHEET (FLOOR) - FOR TOILET, SHOWER ROOM, THK. 2MM - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK
G-02 | CEMENTITIOUS WATERPROOFING - FOR FLOOR AND WALL OF WET ROOM - URETHANE PROOFING ON 2 COAT CEMENTITIOUS LIQUID WATERPROOFING - ACRYLIC-POLYMER EMULSION MIXED WITH CEMENT MORTARS - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK - INCLUDING WATER LEAK TEST
H-01 | RIGID INSULATION FOR ROOF (THK. 50mm) - FOR ROOF SLAB - THK. 150mm RIGID EXTRUDED POLYSTYRENE BOARD (Density : Min. 25kg/m3, Compressive Strength : Min. 250kPa, Thermal Conductivity : Max. 0.029 W/mK) - Class A (Flame Spread Index 0~25, Smoke Developed Index 0~450), in accordance with NFPA 255 - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK - INCLUDING JOINT TAPE
H-02 | RIGID INSULATION FOR ROOF (THK.100mm) - FOR ROOF SLAB - THK. 100mm RIGID EXTRUDED POLYSTYRENE BOARD (DENSITY : MIN. 25KG/M3, COMPRESSIVE STRENGTH : MIN. 250KPA, THERMAL CONDUCTIVITY : MAX. 0.029 W/MK) - CLASS A (FLAME SPREAD INDEX 0~25, SMOKE DEVELOPED INDEX 0~450), IN ACCORDANCE WITH NFPA 255 - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK - INCLUDING JOINT TAPE
H-03 | MEMBRANE WATERPROOFING - BUILT-UP ROOFING - FOR ROOF SLAB & PARAPET WALL - INCLUDING COLD WORKED PRIME COAT & 4mm THK. BITUMINUOUS ROOFING FELT - INCLUDING GALV. STEEL FLASHING TO SEAL/COVER THE END OF WATERPROOFING AT PARAPET/UPSTAND - INCLUDING BITUMEN SEALANT AT GROOVE TO END WATERPROOFING MEMBRANE AT UPSTAND - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK
H-04 | P.E FILM - THK. 0.1mm, 2 LAYERS FOR ROOF - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK
H-05 | LIGHT WEIGHT CONCRETE (ROOF) - LIGHTWEIGHT CELLULAR CONCRETE FILL PORTLAND CEMENT AND FOAMING AGENT - MIN. THK. 60 mm, 1/150 SLOPE - INCLUDING ALL MATERIALS FOR CONTROL JOINT : @1.5m x 1.5m - INCLUDING WIRE MESH FOR CRACK CONTROL - INCLUDING LABOR & EQUIPMENT - INCLUDING STEEL TROWEL FINISHING AND/ OR MECHANICAL PLACING & FINISHING
H-06 | CEMENT SCREED FOR WATER PROOFING (ROOF) - THK. 60mm / PROTECTION FOR WATER PROOFING - FOR ROOF - INCLUDING CONTROL JOINT WORK WITH ALL RELATED MATERIAL - INCLUDING STEEL TROWEL FINISHING AND/ OR MECHANICAL PLACING & FINISHING - INCLUDING WIRE MESH FOR CRACK CONTROL
H-07 | CON'C ROOF TILE - PRECASTE CONC. TILE SIZE : 400x400xT40mm - INCLUDING SEPARATION JOINT OF 15mm FILLED W/ APPROVED SEALANT - INCLUDING CRACK CONTROL JOINT : 8mmx12~15mm(H) @1.25x 1.25M FILLED W/APPROVED SEALANT - INCLUDING SEMI-DRY TYPE CEMENT MORTAR - INCLUDING CONTROL JOINT WORK WITH ALL RELATED MATERIAL - INCLUDING STEEL TROWEL FINISHING AND/ OR MECHANICAL PLACING & FINISHING
H-08 | PROTECTION CONCRETE (ROOF) - MIN.THK. 60 mm, - INCLUDING ALL MATERIALS(JOINT FILLER, SEALANT, BACK-UP ROD AND ETC.) FOR CONTROL JOINT : @1.5m x 1.5m - INCLUDING WIRE MESH(#8-150x150 W.W.F) FOR CRACK CONTROL - INCLUDING LABOR & EQUIPMENT
H-09 | SLOPE MORTAR - MIN. THK. 40 mm, 1/150 SLOPE - INCLUDING CONTROL JOINT WORK WITH ALL RELATED MATERIAL - INCLUDING STEEL TROWEL FINISHING AND/ OR MECHANICAL PLACING & FINISHING - INCLUDING ADHESIVE AND APPROPRIATE SLOPE
I-01 | FIRE RESIST. STEEL DOOR - 1.5 HOUR FIRE DOOR - INCLUDING UL CERTIFICATION (NFPA 80) - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT. - INCLUDING SIGN PLATE OF ANODIZED ALUMINIUM OR STAINLESS STEEL - HYDRAULIC DOOR CLOSERS SHALL BE FITTED TO ALL DOORS IN AIR- CONDITIONED AREA - DUST PROOF(FOR EXT.DOOR)
I-01A | FIRE RESIST. STEEL DOOR - 1.5 HOUR FIRE DOOR FOR RADIOACTIVE ROOM - EN 12207 AIR PERMEABILITY CLASSIFICATION - CLASS 4 - INCLUDING UL CERTIFICATION (NFPA 80) - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT. - INCLUDING SIGN PLATE OF ANODIZED ALUMINIUM OR STAINLESS STEEL - HYDRAULIC DOOR CLOSERS SHALL BE FITTED TO ALL DOORS IN AIR- CONDITIONED AREA - DUST PROOF(FOR EXT.DOOR)
I-01B | FIRE RESIST. STEEL DOOR - 0.75 HOUR FIRE DOOR - INCLUDING UL CERTIFICATION (NFPA 80) - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT. - INCLUDING SIGN PLATE OF ANODIZED ALUMINIUM OR STAINLESS STEEL - HYDRAULIC DOOR CLOSERS SHALL BE FITTED TO ALL DOORS IN AIR- CONDITIONED AREA - DUST PROOF(FOR EXT.DOOR) | Rev.B_s1에서 추가됨
I-01C | FIRE RESIST. STEEL DOOR - 0.75 HOUR FIRE DOOR FOR RADIOACTIVE ROOM - EN 12207 AIR PERMEABILITY CLASSIFICATION - CLASS 4 - INCLUDING UL CERTIFICATION (NFPA 80) - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT. - INCLUDING SIGN PLATE OF ANODIZED ALUMINIUM OR STAINLESS STEEL - HYDRAULIC DOOR CLOSERS SHALL BE FITTED TO ALL DOORS IN AIR- CONDITIONED AREA - DUST PROOF(FOR EXT.DOOR) | Rev.1에서 추가됨
I-02 | FIRE RESIST. STEEL DOOR - 3.0 HOUR FIRE DOOR - INCLUDING UL CERTIFICATION (NFPA 80) - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT.
I-02A | FIRE RESIST. STEEL DOOR - 3.0 HOUR FIRE DOOR FOR RADIOACTIVE ROOM - EN 12207 AIR PERMEABILITY CLASSIFICATION - CLASS 4 - INCLUDING UL CERTIFICATION (NFPA 80) - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT.
I-03 | NORMAL STEEL DOOR - DOOR FRAME : 1.6mm THK GALVANOZED STEEL PLATER - DOOR : 1.2mm THK GALVANIZED STEEL PLATE - INSULATION : 50mm THK GALSS WOOL - COATING : EPOXY PRIMER 75μm + POLYURETHANE PAINT 50 μm - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT. - INCLUDING SIGN PLATE OF ANODIZED ALUMINIUM OR STAINLESS STEEL - HYDRAULIC DOOR CLOSERS SHALL BE FITTED TO ALL DOORS IN AIR- CONDITIONED AREA - DUST PROOF(FOR EXT.DOOR)
I-03A | NORMAL STEEL DOOR - FOR RADIOACTIVE ROOM - EN 12207 AIR PERMEABILITY CLASSIFICATION - CLASS 4 - DOOR FRAME : 1.6mm THK GALVANOZED STEEL PLATER - DOOR : 1.2mm THK GALVANIZED STEEL PLATE - INSULATION : 50mm THK GALSS WOOL - COATING : EPOXY PRIMER 75μm + POLYURETHANE PAINT 50 μm - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT. - INCLUDING SIGN PLATE OF ANODIZED ALUMINIUM OR STAINLESS STEEL - HYDRAULIC DOOR CLOSERS SHALL BE FITTED TO ALL DOORS IN AIR- CONDITIONED AREA - DUST PROOF(FOR EXT.DOOR)
I-04 | ROLL-UP SHUTTER DOOR - ELECTRICALLY OPERATED TYPE W/MANUAL OPERATION - WITHSTAND THE WIND VELOCITY - MIN.1.8MM INSULATED ALUMINUM SLAT 6063 T5 WITH POWDER COATING FINISHING AAMA 2603 - RAILS SHALL BE ALUMINUM BOX 6063 T6 WITH POWDER COATING FINISHING AAMA 2603 - INCLUDING ALL HARDWARE - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING SIDE GUIDE RAIL AND BOTTOM RAIL AND OTHER ACCESSARIES INCLUDING ESCAPE DOOR AND WIND LOCK IF REQUIRED - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING SHUTTER BOX
I-04A | ROLL-UP SHUTTER DOOR - 3.0 HOUR FIRE RATING FOR RADIOACTIVE ROOM - EN 12207 AIR PERMEABILITY CLASSIFICATION - CLASS 4 - ELECTRICALLY OPERATED TYPE W/MANUAL OPERATION - WITHSTAND THE WIND VELOCITY - 100mm GLASS WOOL INSULATED, MIN.1.8MM ALUMINUM SLAT 6063 T5 WITH POWDER COATING FINISHING AAMA 2603 - RAILS SHALL BE ALUMINUM BOX 6063 T6 WITH POWDER COATING FINISHING AAMA 2603 - INCLUDING ALL HARDWARE - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING SIDE GUIDE RAIL AND BOTTOM RAIL AND OTHER ACCESSARIES INCLUDING ESCAPE DOOR AND WIND LOCK IF REQUIRED - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING SHUTTER BOX
I-05 | FOLDING DOOR - TOP HUNG FOLDING HEAVY DUTY TYPE - THK. 1.5mm STEEL SHEET W/ INSULATED DOUBLE SKIN - THK. 60mm (MIN.) - GALAVINIZED - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT, PANIC LATCH. ETC.) - INCLUDING PEDESTRIAN DOOR INTERGRADED IN THE FOLDING DOOR
I-06 | AUTOMATIC SLIDING DOOR -THK. 10mm TEMPERED SAFETY GLASS - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT, PANIC LATCH. ETC.) - INCLUDING STAINLESS STEEL FRAME AT TOP & BOTTOM ONLY - INCLUDING AUTOMATIC SYSTEM
I-07 | STAINLESS STEEL DOOR (GLASS SWING DOOR) - DOOR : THK. 12mm TEMPERED SAFETY GLASS - FIXED GLASS : THK. 8mm TEMPERED SAFETY GLASS - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT, PANIC LATCH. ETC.) - INCLUDING STAINLESS STEEL FRAME - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME
I-08 | TIMBER FLUSH DOOR - THK. 42mm (9 PLIES) - FACE VENEER : 12 mm DRIED WOOD, 5 mm PLYWOOD - INSIDE VENEER : 3 PLY PANEL W/ EACH 1.4mm THK. - WOOD LEAF FRAME : 65x32mm, 25x45mm - DOOR FRAME : STEEL FRAME W/THK. 40mm W/ RUBBER SEALING - SOUND INSULATION : 35~40 Db - INCLUDING ALL HARDWARES AND ACCESSARIES REQUIRED ACCORDING to ITB OR PROJECT REQUIREMENT (SUCH as PANIC BAR, LOCKSET, HINGES, DOOR CLOSER, ETC.) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - ALL TIMBER SHALL BE OF EITHER GRADE ‘A’ OR GRADE ‘B’ TIMBER
I-09 | PLYWOOD DOOR - THK. 42mm (9 PLIES) - FACE VENEER : 12 mm DRIED WOOD, 5 mm PLYWOOD - INSIDE VENEER : 3 PLY PANEL W/ EACH 1.4mm THK. - WOOD LEAF FRAME : 65x32mm, 25x45mm - DOOR FRAME : STEEL FRAME W/THK. 40mm W/ RUBBER SEALING - SOUND INSULATION : 35~40 Db - INCLUDING ALL HARDWARES AND ACCESSARIES REQUIRED ACCORDING to ITB OR PROJECT REQUIREMENT (SUCH as PANIC BAR, LOCKSET, HINGES, DOOR CLOSER, ETC.) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME
I-10 | HANGER DOOR - ELECTRICALLY OPERATED TYPE W/MANUAL OPERATION - WITHSTAND THE WIND VELOCITY - GALVANIZED STEEL - INCLUDING ALL HARDWARES - INCLUDING RAIL
I-11 | MASTER- KEY SYSTEM - MASTER-KEY SYSTEM FOR WHOLE FACILITY - GRAND MASTER KEYS : 10 NOS - MASTER KEYS ; 10 NOS. PER EACH GROUP - SUB-MASTER KEYS : 5 NOS. PER EACH BLDG - SINGLE KEYS : 3 NOS. PER EACH DOOR - INCLUDING PROFILE CYLINDER - MASTER KEY SYSTEM SHALL BE SUBJECT TO CLIENT'S APPROVAL
I-12 | ALUMINIUM WINDOW (DOUBLE) - ANODIZED HEAVY DUTY COATING - DOUBLE GLASS (THK. 6mm) W/ 12mm AIR SPACE - INCLUDING ALUMINUM ACCORDION SHUTER FOR COVERING OF WINDOW - INCLUDING ALL HARDWARES STAINLESS STEEL (SUCH AS LOCKSET AND CRESENT) - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING MORTAR FILLING INTO WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY ) - INCLUDING AL.SUB-FRAME & NYLON COATED INSECT SCREEN AT OPEN AREA ONLY( EXT. WINDOW ONLY )
I-12A | ALUMINIUM WINDOW (DOUBLE) - FOR RADIOACTIVE ROOM - EN 12207 AIR PERMEABILITY CLASSIFICATION - CLASS 4 - ANODIZED HEAVY DUTY COATING - DOUBLE GLASS (THK. 6mm) W/ 12mm AIR SPACE - INCLUDING ALUMINUM ACCORDION SHUTER FOR COVERING OF WINDOW - INCLUDING ALL HARDWARES STAINLESS STEEL (SUCH AS LOCKSET AND CRESENT) - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING MORTAR FILLING INTO WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY ) - INCLUDING AL.SUB-FRAME & NYLON COATED INSECT SCREEN AT OPEN AREA ONLY( EXT. WINDOW ONLY )
I-13 | ALUMINUM WINDOW (SINGLE) - ANODIZED HEAVY DUTY COATING - SINGLE GLASS (THK. 6mm) - INCLUDING ALL HARDWARES STAINLESS STEEL (SUCH AS LOCKSET AND CRESENT) - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING MORTAR FILLING INTO WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY ) - INCLUDING AL.SUB-FRAME & NYLON COATED INSECT SCREEN AT OPEN AREA ONLY( EXT. WINDOW ONLY )
I-14 | ALUMINIUM LOUVER - ANODIZED HEAVY DUTY COATING - W/ ENCLOSING FRAME - STAINLESS STEEL FLY SCREENS - BIRD GUARD ON THE INSIDE - INCLUDING ALL HARDWARES - INCLUDING SEALANT AROUND LOUVER FRAME - INCLUDING MORTAR FILLING INTO LOUVER FRAME
I-15 | SAND TRAP LOUVER (GALVANIZED STEEL) - GALVANIZED STEEL FRAME, BLADE & ACCESORIES - W/ HOT DIP GALVANIZED INSECT SCREEN - W/ WEATHER HOOD - COLOR TO BE APPROVED - MATERIAL APPROVAL REQ'D | Rev.1에서 추가됨
I-16 | LOUVER (GALVANIZED STEEL) - GALVANIZED STEEL FRAME, BLADE & ACCESORIES - W/ HOT DIP GALVANIZED INSECT SCREEN - COLOR TO BE APPROVED - MATERIAL APPROVAL REQ'D | Rev.1에서 추가됨
J-01 | EXTERIOR CEMENT PLASTER FOR WALL - THK. 18mm / 2 COATS - INCLUDING SCAFFOLDING - INCLUDING VERTICAL/HORIZONTAL CONTROL JOINT WORK - INCLUDING GALV. CORNER & CASING BEAD & PLASTER STOP & LATH WORK - INCLUDING PREPARETION OF SURFACE & MOIST CURING
J-02 | INTERIOR CEMENT PLASTER FOR WALL - THK. 18mm / 2 COATS - INCLUDING SCAFFOLDING - INCLUDING VERTICAL/HORIZONTAL CONTROL JOINT WORK - INCLUDING GALV. CORNER & CASING BEAD & PLASTER STOP & LATH WORK - INCLUDING PREPARETION OF SURFACE & MOIST CURING
J-03 | STEEL TROWEL FINISH - FOR CONCRETE FLOOR FACE UNDER THE HARDENER FINISHING, PAINTING AND PVC TILE, CARPET TILE, ETC. - INCLUDING FLOOR SLOPE AT WET AREA - INCLUDING GRINDING WORK ON CONC. SLAB
J-04 | ACOUSTIC MINERAL BOARD CEILING - SIZE : 600x600mm OR 600x1200mm (THK. 15mm) - NON-COMBUSTIBLE CLASS B TO EN13501-1 - INCLUDING GRID, HANGER, EDGE ANGLE - INCLUDING SCAFFOLDING - INCLUDING CURTAIN BOX MADE OF COATED STEEL SHEET - INCLUDING ACCESS PANEL TO THE CEILING - INCLUDING LIGHT FIXTURE & OPENING REINFORCED WORK - INCLUDING SEISMIC BRACING SYSTEM FOR THE SUSPENSION SYSTEM, IF REQUIRED
J-05 | PVC STRIP CEILING - 100mm WIDE x 15mm DEEP WITH 25mm RECESSED - FOR TOILETS, SHOWERS CEILING - INCLUDING GRID, HANGER, EDGE ANGLE - INCLUDING SCAFFOLDING - INCLUDING CURTAIN BOX MADE OF COATED STEEL SHEET - INCLUDING ACCESS PANEL TO THE CEILING - INCLUDING LIGHT FIXTURE & OPENING REINFORCED WORK - INCLUDING SEISMIC BRACING SYSTEM FOR THE SUSPENSION SYSTEM, IF REQUIRED
J-06 | ALUMINIUM PANEL CEILING - SIZE : 600x600mm OR 600x1200mm (THK. 0.5mm) - NON DIRECTIONAL PERFORATED ALUMINIUM - ACOUSTIC BLANKET (25mm LOW-DENSITY BLANKET OF GLASS FIBRE INSULATION) - INCLUDING GRID SYSTEM : GALVANIZED STEEL (MOLDING, LOCKING CLIP ETC.) - INCLUDING SUSPENSION SYSTEM : HOT DIP GAL. MILD STEEL FLATS AND/OR RODS (ROD HANGER : GAL. STEEL OF 4mm DIA.) - INCLUDING SCAFFOLDING - INCLUDING CURTAIN BOX MADE OF COATED STEEL SHEET - INCLUDING ACCESS PANEL TO THE CEILING - INCLUDING LIGHT FIXTURE & OPENING REINFORCED WORK - INCLUDING SEISMIC BRACING SYSTEM FOR THE SUSPENSION SYSTEM, IF REQUIRED
J-07 | SMC PANEL CEILING - SIZE : 600 x 600 x 1.2mm - SMC(SHEET MOULDING COMPOUND) - INCLUDING GRID, HANGER, EDGE ANGLE - INCLUDING SCAFFOLDING - INCLUDING CURTAIN BOX MADE OF COATED STEEL SHEET - INCLUDING ACCESS PANEL TO THE CEILING - INCLUDING LIGHT FIXTURE & OPENING REINFORCED WORK - INCLUDING SEISMIC BRACING SYSTEM DETAIL SHALL BE APPLIED FOR THE SUSPENSION SYSTEM, IF REQUIRED- INCLUDING LIGHT FIXTURE & OPENING REINFORCED WORK - INCLUDING SEISMIC BRACING SYSTEM FOR THE SUSPENSION SYSTEM, IF REQUIRED
J-08 | GYPSUM PLASTER BOARD PARTITION WALL - BOTH SIDE : THK. 12.5mm x 2PLIES GYPSUM PLASTER BOARD - T50 MINERAL FIBRE INSULATION CORE W/ GALVANIZED METAL STUD FRAME - NON-COMBUSTIBLE & NON-INFLAMMABLE TYPE - INCLUDING ALL HARDWARES & CONNECTING/FIXING ACCESSORIES - INCLUDING SCAFFOLDING - INCLUDING JOINT TAPING, OPENING WORK & COMPOUND, SEALANT - INCLUDING SLEEVE, DOOR & WINDOW REINFORCING FRAME WORK - INCLUDING CERTIFICATE
J-09 | GYPSUM PLASTER BOARD PARTITION WALL - FIRE RESISTANCE RATING (1.5 HOUR) - BOTH SIDE : THK. 12.5mm x 2PLIES GYPSUM PLASTER BOARD - T50 MINERAL FIBRE INSULATION CORE W/ GALVANIZED METAL STUD FRAME - NON-COMBUSTIBLE & NON-INFLAMMABLE TYPE - INCLUDING ALL HARDWARES & CONNECTING/FIXING ACCESSORIES - INCLUDING SCAFFOLDING - INCLUDING JOINT TAPING, OPENING WORK & COMPOUND, SEALANT - INCLUDING SLEEVE, DOOR & WINDOW REINFORCING FRAME WORK - INCLUDING CERTIFICATE- INCLUDING DOOR (W 650mm)
J-10 | GYPSUM PLASTER BOARD PARTITION WALL - FIRE RESISTANCE RATING (3.0 HOUR) - BOTH SIDE : THK. 12.5mm x 2PLIES GYPSUM PLASTER BOARD - T50 MINERAL FIBRE INSULATION CORE W/ GALVANIZED METAL STUD FRAME - NON-COMBUSTIBLE & NON-INFLAMMABLE TYPE - INCLUDING ALL HARDWARES & CONNECTING/FIXING ACCESSORIES - INCLUDING SCAFFOLDING - INCLUDING JOINT TAPING, OPENING WORK & COMPOUND, SEALANT - INCLUDING SLEEVE, DOOR & WINDOW REINFORCING FRAME WORK - INCLUDING CERTIFICATE- INCLUDING DOOR (W 650mm)
J-11 | TOILET PARTITION - HEIGHT : 2300mm - PARTITION : 30mm HIGH DENSITY CHIP BOARD W/ PVC VENEER - FRONT PANEL : 34x15x2mm ANODIZED ALUMINIUM - UNDERPANEL CLEARANCE : 150mm - INCLUDING ALL HARDWARES & ACCESSORIES(LOCKING DEVICE SOWING OCCUPYING INDICATOR) - INCLUDING U-CHANNEL 32x36x2mm - INCLUDING DOOR (W 650mm)- INCLUDING DOOR (W 650mm)
J-12 | THERMAL INSULATED TRAPEZOIDAL CLADDING(FOR ROOF) - EXTERIOR SKIN: TRAPEZOIDAL PROFILE MIN. 0.6T P.V.D.F COATING(25㎛), GALVANIZED STEEL SHEET - CORE: NON-COMBUSTIBLE MATERIAL ACCORDING TO ASTM or EQUIVALENT, MIN 100mm.GLASS WOOL, MIN.DENSITY 64kg/m3 - INTERIOR SKIN: TRAPEZOIDAL PROFILE MIN. 0.6T P.V.D.F COATING(25㎛), GALVANIZED STEEL SHEET - INCLUDING ALL FLASHING (ROOF RIDGE FLASHING FOR TOP & SIDE, CORNER & JOINT FLASHING, DOOR & WINDOW FLASHING, OPENING FLASHING, PARAPET FLASHING AND ETC.) - INCLUDING ACCESSORIES (ANCHOR, PLATE, TOP CAPPING & ALL FLASHING), SEALANT, BACK UP & JOINT FILLING MATERIAL (AROUND OPENING AREA) - INCLUDING SCAFFOLDING - INCLUDING DOOR & WINDOW SUNSHADE - INCLUDING PROTECTION FILM ON SURFACE OF PRODUCTS TILL SITE. - 10 YEAR GUARANTEE - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION - QUANTITIES ARE PROJECTED AREA | Rev.B_s1에서 추가됨
J-12A | SINGLE TRAPEZOIDAL CLADDING(FOR ROOF) - TRAPEZOIDAL PROFILE MIN. 0.6T P.V.D.F COATING(25㎛), GALVANIZED STEEL SHEET - INCLUDING ALL FLASHING (ROOF RIDGE FLASHING FOR TOP & SIDE, CORNER & JOINT FLASHING, DOOR & WINDOW FLASHING, OPENING FLASHING, PARAPET FLASHING AND ETC.) - INCLUDING ACCESSORIES (ANCHOR, PLATE, TOP CAPPING & ALL FLASHING), SEALANT, BACK UP & JOINT FILLING MATERIAL (AROUND OPENING AREA) - INCLUDING SCAFFOLDING - INCLUDING DOOR & WINDOW SUNSHADE - INCLUDING PROTECTION FILM ON SURFACE OF PRODUCTS TILL SITE. - 10 YEAR GUARANTEE - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION - QUANTITIES ARE PROJECTED AREA | Rev.B_s1에서 추가됨
J-13 | THERMAL INSULATED TRAPEZOIDAL CLADDING(FOR WALL) - EXTERIOR SKIN: TRAPEZOIDAL PROFILE MIN. 0.6T P.V.D.F COATING(25㎛), GALVANIZED STEEL SHEET - CORE: NON-COMBUSTIBLE MATERIAL ACCORDING TO ASTM or EQUIVALENT, MIN 50mm.GLASS WOOL, MIN.DENSITY 64kg/m3 - INTERIOR SKIN: TRAPEZOIDAL PROFILE MIN. 0.6T P.V.D.F COATING(25㎛), GALVANIZED STEEL SHEET - INCLUDING ALL FLASHING (ROOF RIDGE FLASHING FOR TOP & SIDE, CORNER & JOINT FLASHING, DOOR & WINDOW FLASHING, OPENING FLASHING, PARAPET FLASHING AND ETC.) - INCLUDING ACCESSORIES (ANCHOR, PLATE, TOP CAPPING & ALL FLASHING), SEALANT, BACK UP & JOINT FILLING MATERIAL (AROUND OPENING AREA) - INCLUDING SCAFFOLDING - INCLUDING DOOR & WINDOW SUNSHADE - INCLUDING PROTECTION FILM ON SURFACE OF PRODUCTS TILL SITE. - 10 YEAR GUARANTEE - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION - QUANTITIES ARE PROJECTED AREA
J-14 | ACCESS FLOOR SYSTEM(H=600) - 600 x 600 H:600 - 600mm x 600mm x Min.35mm, ANTI-STATIC PVC TILE(3mm) - HIGH DENSITY CHIPBOARD CORE(675 kg/m3) WRAPPED W/ 0.9mm GALV. SHEET - INCLUDING STEPS, SUPPORTING MATERIAL & ACCESSORIES - INCLUDING LIFTING TOOL - INCLUDING ADHESIVE OR ANCHOR & POLISHING - INCLUDING SEISMIC BRACING SYSTEM FOR SUPPORT STRUCTURE, IF REQUIRE
J-15 | GUTTER FLASHING - THK. 1.2mm GALVANIZED STEEL SHEET - W300mm x H200mm - INCLUDING INSULATION, GUTTER HANGER, ANCHOR & SEALANT - INDLUDING FIXING & JOINTING - INCLUDING SCAFFOLDING
K-01 | STRUCTURAL STEEL (INDOOR STEEL) - ASTM A36 OR EQUIVALENT - INCLUDING COMMON BOLT, NUT, WASHER COMMON BOLT : ASTM A307 (HOT-DIP GALVANIZED) ASTM A563, ASTM F436 (HOT-DIP GALVANIZED) FABRICATION WORK INCLUDES FOLLOWINGS BUT NOT LIMITED TO : - SHOP DRAWINGS WITH MASTER MEMBER LIST. - SUPPLY OF RAW MATERIALS CONSISTING OF STEEL STRUCTURES LIKE MAIN MEMBER(ROLL OR BUILT-UP), PURLIN & GIRTH, STAIR, CANOPY, FASTENERS AND STUD SHEAR CONNECTOR(STUD BOLT). - SUPPLY OF PAINTS FOR TOUCH UP PAINTING AT THE SITE. - FABRICATION OF STEEL STRUCTURES INCLUDING PAINTING. - TRANSPORTAION OF THE MATERIAL TO CONSTRUCTION SITE(FOT). - SUBMISSIONS : CERTIFICATE OF RAW MATERIALS, FACTORY TEST REPORT. ERECTION WORK INCLUDES FOLLOWING BUT NOT LIMITED TO : - ERECTION, BOLTING, WELDING, TOUCH UP PAINTING AND GROUTING WORK FOR COLUMN BASE. - SUPPLY OF EQUIPMENT FOR MATERIAL HANDLING AND LIFTING, SCAFFOLDING, TOOLS AND CONSUMABLES. - SUBMISSIONS : TEST AND INSPECTION REPORT - THE QUANTITY DO NOT INCLUDE FASTENER (SUCH AS HIGH STRENGTH BOLT & COMMON BOLT) AND STUD BOLT, WHICH SHALL BE ADDITIONALLY CONSIDERED BY THE CONTRACTOR'S EXPERIENCE AND INCLUDED IN THE UNIT PRICE.
K-01A | STRUCTURAL STEEL (INDOOR STEEL) - □50x50x2.3, ASTM A36 OR EQUIVALENT - STEEL FRAME FOR FIXING EXTERIOR WALL PANEL - INCLUDING SET ANCHOR FOR FIXING STEEL FRAME ON CONCRETE WALL FABRICATION WORK INCLUDES FOLLOWINGS BUT NOT LIMITED TO : - SHOP DRAWINGS WITH MASTER MEMBER LIST. - SUPPLY OF RAW MATERIALS - SUPPLY OF PAINTS FOR TOUCH UP PAINTING AT THE SITE. - FABRICATION OF STEEL STRUCTURES INCLUDING PAINTING. - TRANSPORTAION OF THE MATERIAL TO CONSTRUCTION SITE(FOT). - SUBMISSIONS : CERTIFICATE OF RAW MATERIALS, FACTORY TEST REPORT. ERECTION WORK INCLUDES FOLLOWING BUT NOT LIMITED TO : - ERECTION, BOLTING, WELDING, TOUCH UP PAINTING AND GROUTING WORK FOR COLUMN BASE. - SUPPLY OF EQUIPMENT FOR MATERIAL HANDLING AND LIFTING, SCAFFOLDING, TOOLS AND CONSUMABLES. - SUBMISSIONS : TEST AND INSPECTION REPORT - THE QUANTITY DO NOT INCLUDE FASTENER (SUCH AS HIGH STRENGTH BOLT & COMMON BOLT) AND STUD BOLT, WHICH SHALL BE ADDITIONALLY CONSIDERED BY THE CONTRACTOR'S EXPERIENCE AND INCLUDED IN THE UNIT PRICE.
K-02 | STRUCTURAL STEEL (INDOOR STEEL) - ASTM A992 OR EQUIVALENT - INCLUDING HIGH STRENGTH BOLT, NUT, WASHER HIGH STRENGTH BOLT : ASTM A325, HOT-DIP GALVANIZED or ASTM A490, PLAIN “UNCOATED" ASTM A563, ASTM F436 (HOT-DIP GALVANIZED) FABRICATION WORK INCLUDES FOLLOWINGS BUT NOT LIMITED TO : - SHOP DRAWINGS WITH MASTER MEMBER LIST. - SUPPLY OF RAW MATERIALS CONSISTING OF STEEL STRUCTURES LIKE MAIN MEMBER(ROLL OR BUILT-UP), PURLIN & GIRTH, STAIR, CANOPY, FASTENERS AND STUD SHEAR CONNECTOR(STUD BOLT). - SUPPLY OF PAINTS FOR TOUCH UP PAINTING AT THE SITE. - FABRICATION OF STEEL STRUCTURES INCLUDING PAINTING. - TRANSPORTAION OF THE MATERIAL TO CONSTRUCTION SITE(FOT). - SUBMISSIONS : CERTIFICATE OF RAW MATERIALS, FACTORY TEST REPORT. ERECTION WORK INCLUDES FOLLOWING BUT NOT LIMITED TO : - ERECTION, BOLTING, WELDING, TOUCH UP PAINTING AND GROUTING WORK FOR COLUMN BASE. - SUPPLY OF EQUIPMENT FOR MATERIAL HANDLING AND LIFTING, SCAFFOLDING, TOOLS AND CONSUMABLES. - SUBMISSIONS : TEST AND INSPECTION REPORT - THE QUANTITY DO NOT INCLUDE FASTENER (SUCH AS HIGH STRENGTH BOLT & COMMON BOLT) AND STUD BOLT, WHICH SHALL BE ADDITIONALLY CONSIDERED BY THE CONTRACTOR'S EXPERIENCE AND INCLUDED IN THE UNIT PRICE.
K-03 | ANCHOR BOLT - ASTM F-1554 GRADE 36 - HOT DIP GALVANIZED STEEL - FOR STEEL COLUMN BASE
K-04 | NON-SHRINKAGE GROUT - Fcu= 50MPa AT 28 DAYS - CEMENTIOUS - FOR STEEL COLUMN BASE - INCLUDING FORM WORK
K-05 | STEEL PAINTING(FOR NON FIRE-PROOFED SURFACE, BASE, SECOND & FINAL COAT) INDOOR STEEL - SURFACE PREPARATION: SA 2½ (ISO 8501-1:1988)/SSPC-SP10 COAT 1: EPOXY ZINC PHOSPHATE PRIMER, DFT : MIN 75㎛ COAT 2: EPOXY POLY AMINE HIGH BUILD, DFT : MIN 125㎛ COAT 3: ACRYLIC (SOLVENT BASED), DFT : MIN 50㎛ TOTAL DFT: Min 250㎛ OUTDOOR STEEL - SURFACE PREPARATION: SA 2½ (ISO 8501-1:1988)/SSPC-SP10 COAT 1: EPOXY ZINC PHOSPHATE PRIMER, DFT : MIN 75㎛ COAT 2: EPOXY POLY AMINE HIGH BUILD, DFT : MIN 125㎛ COAT 3: ACRYLIC (SOLVENT BASED), DFT : MIN 150㎛ TOTAL DFT: Min 350㎛
K-06 | FIRE PROOFING COATING (1.5 HOUR) - INTUMESCENT FIREPROOF PAINT - FIRE PROOFING COATING AFTER ERECTION OF STEEL STRUCTURES IN PLACE - INCLUDING SCAFFOLDING WORK - INCLUDING PROTECTION FOR EQUIPMENT AND FACILITY - INCLUDING REACTIFICATION OF DAMAGED PARTS ON SITE - INCLUDING CERTIFICATION - INCLUDING INSTRUMENSCENT PAINT FOR FIREPROOFED STEEL STRUCTURAL PROFILE AND GUSSET PLATE, REPAIR WORK - INCLUDING BEARING COMPONENTS OF BUILDING(COLUMN, CRANE GIRDER, WIND GIRDER, HORIZONTAL BRACE FOR FLOOR, VERTICAL BRACE FOR WALL, BRAM ETC.), FLIGHTS AND LANDINGS OF STAIRWAY - UL263, BS476 OR EQUIVALENT
K-07 | FIRE PROOFING COATING (3.0 HOUR) - INTUMESCENT FIREPROOF PAINT - FIRE PROOFING COATING AFTER ERECTION OF STEEL STRUCTURES IN PLACE - INCLUDING SCAFFOLDING WORK - INCLUDING PROTECTION FOR EQUIPMENT AND FACILITY - INCLUDING REACTIFICATION OF DAMAGED PARTS ON SITE - INCLUDING CERTIFICATION - INCLUDING INSTRUMENSCENT PAINT FOR FIREPROOFED STEEL STRUCTURAL PROFILE AND GUSSET PLATE, REPAIR WORK - INCLUDING BEARING COMPONENTS OF BUILDING(COLUMN, CRANE GIRDER, WIND GIRDER, HORIZONTAL BRACE FOR FLOOR, VERTICAL BRACE FOR WALL, BRAM ETC.), FLIGHTS AND LANDINGS OF STAIRWAY - UL263, BS476 OR EQUIVALENT
K-08 | DECK PLATE - THK. 1.6mm GALVANIZED STEEL - HOT DIPPED GALVANIZED AS PER ASTM A653-01a ZINC WEIGHT OF NOT LESS THAN 0.275kg/m2 ON EACH SIDE OF SHEET - INCLUDING ALL SUBSIDIARY WORK SUCH AS OPENING ARRANGEMENT, INSTALLATION OF END PLATE & ENCLOSURE, CONC. STOPPER, WELDING, ETC. - AS PER TECH SPEC. - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION
K-09 | GALV. STEEL GRATING - FOR TRENCH COVER, PLATFORM, STAIR LANDING & TREAD ETC. - HOT DIP GALVANIZED (4 MILS, 100 MICRONS) - BEARING BAR : DEPTH 32 OR 40mm x 5mm AT 30 MM C/C - CROSS BAR : 6mm Square Bar AT 100 MM C/C
K-10 | CHECKERED PLATE - FOR TRENCH COVER, PLATFORM, ETC. - HOT DIP GALVANIZED (4 MILS, 100 MICRONS) - THK. 6mm - RAISED DIAMOND PATTERN
K-11 | STAINLESS STEEL HANDRAIL - AS PER ASTM A53/A53M-01 - SUS 316 - ROUND OR SQUARE : POST - DIA. 32mm / SQUARE 40, THK.4 mm : INTERMEDIATE RAIL-DIA. Φ32mm, SQUARE 30 - TOP RAIL HEIGHT : 900mm - 2 INTERMEDIATE HORIZONTAL RAILS - PIPE POST SPACING @ 1200 mm - INCLUDING FIXING AND ACCESSORIES - INCLUDING TOE PLATE OR CHANNEL - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
K-12 | STEEL PIPE HANDRAIL (STAND TYPE) - RAILING PIPE : INTERNAL DIA. 32mm, THK.4 mm - TOP RAIL HEIGHT : WALKWAY & PLATFORM - 1100 mm : STAIR - 900 mm - 2 INTEMEDIATE HORIZONTAL RAILS - PIPE POST SPACING @ 1200 mm - HOT DIP GALVANIZED AND INORGANIC ETHYL ZINC SILICATE(1COAT) - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING. - INCLUDING FIXING AND ACCESSORIES - INCLUDING TOE PLATE OR CHANNEL - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
K-13 | CAGE LADDER (2.5m < H ≤ 10m) - LADDER : WIDTH - 400 mm : SIDE RAIL - ANGLE L60/8 or L75/10 : RUNG - Φ25 RIBBED BAR @280 - CAGE : DIAMETER 700 mm : CAGES STARTING 2.5m ABOVE G.L OR F.L : HORIZONTAL HOOP - F.B 55x6 mm @1.5m : VERTICAL HOOP - 5 EQUALLY SPACED - HOT DIP GALVANIZED AND INORGANIC ETHYL ZINC SILICATE(1COAT) - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
K-14 | CAGE LADDER (10.0m < H) - LADDER : WIDTH - 400 mm : SIDE RAIL - ANGLE L60/8 or L75/10 : RUNG - Φ25 RIBBED BAR @280 - CAGE : DIAMETER 700 mm : CAGES STARTING 2.5m ABOVE G.L OR F.L : HORIZONTAL HOOP - F.B 55x6 mm @1.5m : VERTICAL HOOP - 5 EQUALLY SPACED - HOT DIP GALVANIZED AND INORGANIC ETHYL ZINC SILICATE(1COAT) - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
K-15 | STRUCTURAL STEEL (OUTDOOR STEEL) - ASTM A36 OR EQUIVALENT - INCLUDING COMMON BOLT, NUT, WASHER COMMON BOLT : ASTM A307 (HOT-DIP GALVANIZED) ASTM A563, ASTM F436 (HOT-DIP GALVANIZED) FABRICATION WORK INCLUDES FOLLOWINGS BUT NOT LIMITED TO : - SHOP DRAWINGS WITH MASTER MEMBER LIST. - SUPPLY OF RAW MATERIALS CONSISTING OF STEEL STRUCTURES LIKE MAIN MEMBER(ROLL OR BUILT-UP), PURLIN & GIRTH, STAIR, CANOPY, FASTENERS AND STUD SHEAR CONNECTOR(STUD BOLT). - SUPPLY OF PAINTS FOR TOUCH UP PAINTING AT THE SITE. - FABRICATION OF STEEL STRUCTURES INCLUDING PAINTING. - TRANSPORTAION OF THE MATERIAL TO CONSTRUCTION SITE(FOT). - SUBMISSIONS : CERTIFICATE OF RAW MATERIALS, FACTORY TEST REPORT. ERECTION WORK INCLUDES FOLLOWING BUT NOT LIMITED TO : - ERECTION, BOLTING, WELDING, TOUCH UP PAINTING AND GROUTING WORK FOR COLUMN BASE. - SUPPLY OF EQUIPMENT FOR MATERIAL HANDLING AND LIFTING, SCAFFOLDING, TOOLS AND CONSUMABLES. - SUBMISSIONS : TEST AND INSPECTION REPORT - THE QUANTITY DO NOT INCLUDE FASTENER (SUCH AS HIGH STRENGTH BOLT & COMMON BOLT) AND STUD BOLT, WHICH SHALL BE ADDITIONALLY CONSIDERED BY THE CONTRACTOR'S EXPERIENCE AND INCLUDED IN THE UNIT PRICE.
K-16 | STRUCTURAL STEEL (OUTDOOR STEEL) - ASTM A992 OR EQUIVALENT - INCLUDING HIGH STRENGTH BOLT, NUT, WASHER HIGH STRENGTH BOLT : ASTM A325, HOT-DIP GALVANIZED or ASTM A490, PLAIN “UNCOATED" ASTM A563, ASTM F436 (HOT-DIP GALVANIZED) FABRICATION WORK INCLUDES FOLLOWINGS BUT NOT LIMITED TO : - SHOP DRAWINGS WITH MASTER MEMBER LIST. - SUPPLY OF RAW MATERIALS CONSISTING OF STEEL STRUCTURES LIKE MAIN MEMBER(ROLL OR BUILT-UP), PURLIN & GIRTH, STAIR, CANOPY, FASTENERS AND STUD SHEAR CONNECTOR(STUD BOLT). - SUPPLY OF PAINTS FOR TOUCH UP PAINTING AT THE SITE. - FABRICATION OF STEEL STRUCTURES INCLUDING PAINTING. - TRANSPORTAION OF THE MATERIAL TO CONSTRUCTION SITE(FOT). - SUBMISSIONS : CERTIFICATE OF RAW MATERIALS, FACTORY TEST REPORT. ERECTION WORK INCLUDES FOLLOWING BUT NOT LIMITED TO : - ERECTION, BOLTING, WELDING, TOUCH UP PAINTING AND GROUTING WORK FOR COLUMN BASE. - SUPPLY OF EQUIPMENT FOR MATERIAL HANDLING AND LIFTING, SCAFFOLDING, TOOLS AND CONSUMABLES. - SUBMISSIONS : TEST AND INSPECTION REPORT - THE QUANTITY DO NOT INCLUDE FASTENER (SUCH AS HIGH STRENGTH BOLT & COMMON BOLT) AND STUD BOLT, WHICH SHALL BE ADDITIONALLY CONSIDERED BY THE CONTRACTOR'S EXPERIENCE AND INCLUDED IN THE UNIT PRICE.
L-01 | ROOF DRAIN - Φ100 / CAST IRON
L-02 | ROOF DRAIN - Φ150 / CAST IRON
L-03 | ROOF DRAIN - Φ100 / UPVC
L-04 | ROOF DRAIN - Φ150 / UPVC
L-05 | DOWN SPOUT - Φ100 / GALV. STL. W/ FACTORY COAT OR ALUMINIUM TYPE - □100 / ALUMINIUM x MIN. 0.75 mm - INCLUDING DOWN SPOUT HANGER & ANCHOR - INCLUDING EPOXY PAINT
L-06 | DOWN SPOUT - Φ150 / GALV. STL. W/ FACTORY COAT OR ALUMINIUM TYPE - □150 / ALUMINIUM x MIN. 0.75 mm - INCLUDING DOWN SPOUT HANGER & ANCHOR - INCLUDING EPOXY PAINT
L-07 | DOWN SPOUT - Φ100 / UPVC W/ FACTORY COAT OR ALUMINIUM TYPE - INCLUDING DOWN SPOUT HANGER & ANCHOR
L-08 | DOWN SPOUT - Φ150 / UPVC W/ FACTORY COAT OR ALUMINIUM TYPE - INCLUDING DOWN SPOUT HANGER & ANCHOR
L-09 | DOWN SPOUT HEAD - GALV. STL. FOR DOWN SPOUT OR ALUMINIUM TYPE
L-10 | DOWN SPOUT HEAD - UPVC FOR DOWN SPOUT
L-11 | SPLASH BLOCK - PC BLOCK
L-12 | MISC. STEEL WORK (GALVANIZED) - FOR EMBEDDED PLATE(FOR PIT COVER), SLEEVE, CORNER ANGLE FOR TRENCH COVER AND CHK'D PLATE - HOT DIP GALVANIZED (4 MILS, 100 MICRONS) - STEEL : ASTM A36 - INCLUDING ERECTION & SHOP DWG. - INCLUDING ERECTION MATERIAL, EQUIPMENT (HIGH STRENGTH BOLT/NUT/WASHER, ACCESSORIES) - INCLUDING PAINTING, TOUCH-UP PAINTING & GRINDING, SCAFFOLDING WORK (IF NECESSARY) - INCLUDING TESTING AS PER TECH.SPEC. - INCLUDING FIXING ANGLE AT MISC STEEL WORK
L-13 | BOLLARD - REMOVABLE(DE-MOUNTED) - STEEL PIPE H 1000MM Φ 150 MM & REMOVAL - STEEL PIPE FILLIED CONCRETE & FOUNDATION - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
L-14 | ROOM DESIGNATION SIGN - INTERNAL / EXTERNAL - SIZE : 260mm x 100mm x THK. 4mm - ALUMINIUM ANODIZED PLATE W/ SPECIALLY TREATED SURFACE - 4 HORIZONTAL GROOVES, 10mm WIDE AT LOWER END OF PLATE TO TAKE PLASTIC STRIP - DESIGNATION PRINTED IN ENGLISH & LOCAL LANGUAGE - ROOM NUMBER ENGRAVED AT UPPER PORT - INCLUDING FIXING BY NON-CORRODING SCREW ON WALL
L-15 | URINAL SCREEN - HEIGHT : 1500mm, WIDE : 600mm - PARTITION : 30mm HIGH DENSITY CHIP BOARD W/ PVC VENEER - INCLUDING ALL HARDWARES & ACCESSORIES
L-16 | SHOWER TRAY - TRANSLUCENT SHOWER STALL (2-SIDES BLOCK) - STALL SIZE : 900mm x 900mm - SHOWER TRENCH COVER (W150mm x L1200mm) - INCLUDING FIXING & ACCESSORIES
L-17 | VANITY TOP - L=750MM (1 BOWL) - ACRYLIC, 4" FRONT/BACK SPLASH - FOR TOILET, WITHOUT BOWL - L=1500MM (2 BOWL) - ACRYLIC, 4" FRONT/BACK SPLASH - FOR TOILET, WITHOUT BOWL - INCLUDING FIXING & ACCESSORIES
L-18 | MIRROR - FOR TOILET - WATER AND MOISTURE PROOFING - 1500Wx800Hx5T - INCLUDING FIXING & ACCESSORIES
L-19 | TOWEL BAR - STAINLESS STEEL - INCLUDING FIXING & ACCESSORIES
L-20 | SOAP DISPENSER - STAINLESS STEEL - INCLUDING FIXING & ACCESSORIES
L-21 | ROLLER PAPER HOLDER - STAINLESS STEEL - BALL-JOINT TYPE - INCLUDING FIXING & ACCESSORIES
L-22 | Fire Sealing Compound (Fire Rating 3Hr) - Fire Sealing Compound to fill and seal gaps in openings where cables and pipes go through floors and walls - To contain the spread of smoke and fires by compartmentalizing rooms. - INCLUDING UL CERTIFICATION - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
L-23 | Fire Sealing Compound (Fire Rating 1.5Hr) - Fire Sealing Compound to fill and seal gaps in openings where cables and pipes go through floors and walls - To contain the spread of smoke and fires by compartmentalizing rooms. - INCLUDING UL CERTIFICATION - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
L-24 | CHAIN LINK FENCE - 2.5M HIGH GALVANIZED STEEL WIRE PVC - INCLUDING APPROXIMATELY 50mm DIAMOND MESH PATTERN AND 45 DEGREE TO VERTICAL - MIN. BREAKING STRENGTH OF MESH WIRE : 585kg - MIN. THICKNESS OF PVC : 0.38mm
L-25 | CHAIN LINK GATE - HEIGHT 2.5m / WIDTH 2.0m - DOUBLE WING GATE - PLASTIC COATED GALVANIZED CHAIN LINK MESH ON A PLASTIC COATED GALVANIZED STEEL FRAME