## Datasheet
DS201
Instrument Datasheet |  |  |  |  | CONTROL VALVE
1 | Tag No.
2 | Service
3 | P&ID No.
4 | Line No.
5 | Line Size: Inlet / Outlet |  |  |  | Line Spec.
6 | Tightness Requirements |  |  |  | Area Classification
7 | NACE Requirement |  |  |  | Others
8 | PROCESS CONDITIONS
9 | Fluid Name |  | State | [8 empty] | Unit | Min. |  |  | Max.
10 |  |  |  | Unit | Min. |  | Nor. | Max. | Design Temperature |  |  | ºC
11 | Flow Rate |  |  | kg/hr |  |  |  |  | Design Pressure |  |  | kg/cm²-g
12 | Inlet Pressure |  |  | kg/cm²-g |  |  |  |  | Ambient Temperature |  |  | ºC
13 | Pressure Drop |  |  | kg/cm² |  |  |  |  | Available Air Supply Press. |  |  | kg/cm²-g
14 | Inlet Temperature |  |  | ºC |  |  |  |  | Allowable Noise SPL |  |  | dBA
15 | Inlet Viscosity |  |  | cP |  |  |  |  | Max. Shut-Off d/P |  |  | kg/cm²
16 | Inlet Vapour Pressure |  |  | kg/cm²-a |  |  |  |  | Critical Temp. |  | Critical Press. |  |  |  | ºC |  |  | kg/cm²-g
17 | Valve Opening |  |  | % |  |  |  |  | Density |  | Spec. Gravity
18 | Cv Calculated |  |  | - |  |  |  |  | Mol. Weight |  | Com. Factor (Z)
19 | Calc. Noise SPL |  |  | dBA |  |  |  |  | Cp/Cv |  | Flash
20 | Others
21 | BODY AND TRIM
22 | Body Type | [7 empty] | Bonnet Type
23 | Body Size |  | Trim Size | [5 empty] | Trim Form
24 | Required Cv |  | Rated Cv | [5 empty] | Material | Body / Bonnet
25 | Trim Characteristic | [8 empty] | Plug/Ball/Disk
26 | End Conn. & Rating | [8 empty] | Seat
27 | Flow Direction |  | Flow Action To | [6 empty] | Cage / Stem
28 | Guiding |  | No. of Ports | [6 empty] | Gasket / Packing
29 | Leakage Class | [7 empty] | Others
30 | ACTUATOR
31 | Actuator Type | [7 empty] | Handwheel |  | Travel Stop
32 | Actuator Size |  | Actuator Area | [5 empty] | Bench Range
33 | Valve Fail Position | [7 empty] | To Actuator Pressure Range
34 | Others
35 | OTHERS
36 | Positioner | Positioner Type | [6 empty] | Limit Switch | Type / Qty
37 |  | Electrical Connection | [7 empty] | Electrical Connection
38 |  | Power Supply | [7 empty] | Enclosure Class
39 |  | Encl. Class / Charac' | [7 empty] | Contacts/Rating
40 |  | Bypass / Gauges | [7 empty] | Switching Position
41 |  | Signal : Inlet / Outlet | [6 empty] | Air Set | Set Pressure
42 | Sol. Valve | Solenoid Valve Type | [7 empty] | Filter / Gauge
43 |  | Electrical Connection | [7 empty] | Pneumatic Conn.
44 |  | Power Supply | [6 empty] | Tests | Hydro Pressure
45 |  | Encl. Class / Body Mat'l | [7 empty] | Leakage
46 | Others
47 | MANUFACTURER & MODEL
48 | Item |  | Tag |  |  | Manufacturer |  | Model |  |  |  |  | IP Rating |  | Explosion Proof Certi.
49 | Valve |  | 0
50 | Actuator
51 | Positioner
52 | Solenoid Valve
53 | Limit Switch
54 | Air Set
NOTES:
Project Name : LINE Project |  |  |  |  | Plant Code : |  |  | Req. No. : | [5 empty] | Tag Index : |  |  | of
[5 empty] | Rev | By | Date | Description |  |  |  | Chkd | Appd | Document No.
[14 empty] | SHEET |  |  | Rev
Of

## HELP - Sample(DS201)
DS201 | [20 empty] | APPENDIX-03 | Process Units
Instrument Datasheet |  |  |  |  | CONTROL VALVE | [15 empty] | Process Property | Units | Default
1 | Tag No. | [19 empty] | Area | cm²
2 | Service | [20 empty] | ft²
3 | P&ID No. | [20 empty] | in²
4 | Line No. | [7 empty] | P&ID 기준 기입 | [12 empty] | m² | O
5 | Line Size: Inlet / Outlet |  |  |  | Line Spec. |  |  |  | Line no에 있는 piping Size |  | Line no에 있는 piping Size |  |  | Line no에 있는 piping class | [7 empty] | mm²
6 | Tightness Requirements |  |  |  | Area Classification |  |  |  | ANSI Class IV (General) / V or VI (forTSO) |  |  |  |  | Zone1, 2(or 21, 22), IIB, T4, IP65 | [6 empty] | Conductivity | µS | O
7 | NACE Requirement |  |  |  | Others |  |  |  | NACE MR 0103(piping spec에 있으면) | [12 empty] | µS/cm
8 | PROCESS CONDITIONS (as per process data 공정한테 받은것 기입) | [19 empty] | Density | kg/l
9 | Fluid Name |  | State |  |  |  |  | Liquid, Vaor, Steam |  |  |  |  | Unit | Min. |  |  | Max. |  |  |  |  | kg/m³ | O
10 |  |  |  | Unit | Min. |  | Nor. |  | Max. | Design Temperature |  |  | ºC | [8 empty] | lb/ft³
11 | Flow Rate |  |  | kg/hr | as per process data |  |  |  |  | Design Pressure |  |  | kg/cm²-g | [7 empty] | Flow | in³/hr
12 | Inlet Pressure |  |  | kg/cm²-g | [5 empty] | Ambient Temperature |  |  | ºC | [8 empty] | in³/s
13 | Pressure Drop |  |  | kg/cm² | [5 empty] | Available Air Supply Press. |  |  | kg/cm²-g | 5 |  |  | 9 |  |  |  |  | kg/hr | O
14 | Inlet Temperature |  |  | ºC | [5 empty] | Allowable Noise SPL |  |  |  | 85 dBA | [7 empty] | kg/s
15 | Inlet Viscosity |  |  | cP | [5 empty] | Max. Shut-Off d/P |  |  | kg/cm² | [8 empty] | lb/hr
16 | Inlet Vapour Pressure |  |  | kg/cm²-a | [5 empty] | Critical Temp. |  | Critical Press. |  |  |  | ºC |  |  | kg/cm²-g |  |  | lb/min
17 | Valve Opening |  |  | % | by vendor per Cal. |  | by vendor per Cal. |  | by vendor per Cal. | Density |  | Spec. Gravity | [9 empty] | m³/hr
18 | Cv Calculated |  |  | - | by vendor |  | by vendor |  | by vendor | Mol. Weight |  | Com. Factor (Z) | [9 empty] | m³/min
19 | Calc. Noise SPL |  |  | dBA | [5 empty] | Cp/Cv |  | Flash | [9 empty] | Nm³/hr
20 | Others | [20 empty] | t/d
21 | BODY AND TRIM | [20 empty] | t/hr
22 | Body Type |  |  |  | Globe, Vee ball, butterfly, etc |  |  |  |  | Bonnet Type |  |  |  | Plain or extended (온도가 232도보다 높거나 -40도보다 낮으면) 벤더 선정되면 벤더 data따름 | [7 empty] | US gal/d
23 | Body Size |  | Trim Size |  | by vendor, (INDEX항목) |  |  | by vendor |  | Trim Form |  |  |  | Contour, Plug guide, Single Stem, Multi-Stage etc | [7 empty] | US gal/min
24 | Required Cv |  | Rated Cv |  | by vendor |  |  | by vendor |  | Material | Body / Bonnet |  |  | Piping spec, (INDEX항목) |  |  | Piping spec |  |  | PO시 벤더 data |  | US gal/s
25 | Trim Characteristic |  |  |  | RFQ EQ% and PO는 벤더 data | [5 empty] | Plug/Ball/Disk |  |  | 316 SS + Stellite or bettter(piping spec 참조), (INDEX항목) | [5 empty] | PO시 벤더 data | Frequency | Hz | O
26 | End Conn. & Rating |  |  |  | Piping spec에 따라 작성, (INDEX항목) | [5 empty] | Seat |  |  | plug 같은 material | [5 empty] | PO시 벤더 data |  | kHz
27 | Flow Direction |  | Flow Action To |  | Up or down |  |  | open or close |  |  | Cage / Stem |  |  | plug 같은 material |  |  | plug 같은 material |  |  | PO시 벤더 data |  | rpm
28 | Guiding |  | No. of Ports |  | Top or Top/Botton |  |  | one or two |  |  | Gasket / Packing |  |  | MFR.STD |  |  | PTFE for Graphite(232도 이상시 적용) |  |  | PO시 벤더 data | Length | cm
29 | Leakage Class |  |  |  | Class IV(or V), tight shutoff가 있으면 VI (온도가 높아서 Metal seat만 허용 되면 V도 OK |  |  |  |  | Others | [11 empty] | in
30 | ACTUATOR | [20 empty] | km
31 | Actucator Type |  |  |  | Diaphragm(기본) or Cylinder w/Spring |  |  |  |  | Handwheel |  | Travel Stop |  | Yes or No(PID 확인하고 작성) |  |  | Yes or No (P&ID상 Mech. Stop 필요시) |  |  |  |  | m
32 | Actucator Size |  | Actucator Area |  | MFR.STD |  |  | MFR.STD |  | Bench Range |  |  |  | MFR.STD | [7 empty] | mm | O
33 | Valve Fail Position |  |  |  | Close(FC), Open(FO). Lock(FL) (PID 확인하고 작성) , (INDEX항목) |  |  |  |  | To Actuator Pressure Range |  |  |  | MFR.STD | [6 empty] | Level | cm
34 | Others | [20 empty] | in
35 | OTHERS | [20 empty] | mm | O
36 | Positioner | Positioner Type |  |  | SMART HART |  |  |  |  | Limit Switch | Type / Qty |  |  | Mechanical or Proximity(contact type) |  |  |  | PID보고 필요하면 |  |  | Mass | kg | O
37 |  | Electrical Connection |  |  | 1/2" NPT(F) | [5 empty] | Electrical Connection |  |  | 1/2" NPT(F) | [7 empty] | lb
38 |  | Power Supply |  |  | DC24V | [5 empty] | Enclosure Class |  |  | Ex d IIB+H2 T4, IP65 | [7 empty] | oz
39 |  | Encl. Class / Charac' |  |  | Exd IIB+H2 T4, IP65 |  |  | Direct |  |  | Contacts/Rating |  |  | SPDT / 2A AC110V | [6 empty] | Pressure | bar | O
40 |  | Bypass / Gauges |  |  | N.A |  |  | Yes |  |  | Switching Position |  |  | Open or Close 혹은 둘다(PID보고) | [7 empty] | bar-a
41 |  | Signal : Inlet / Outlet |  |  | 4~20mA |  |  | MFR.STD |  | Air Set | Set Pressure |  |  | MFR.STD | [7 empty] | bar-g
42 | Sol. Valve | Solenoid Valve Type |  |  | PID보고 필요하면 3Way or 4Way | [5 empty] | Filter / Gauge |  |  | Yes |  |  | Yes |  |  |  |  | in H2O
43 |  | Electrical Connection |  |  | 1/2" NPT(F) | [5 empty] | Pneumatic Conn. | [10 empty] | kg/cm² | O
44 |  | Power Supply |  |  | DC24V |  |  |  |  | Tests | Hydro Pressure |  |  | ANSI B16.37 | [7 empty] | kg/cm²-a
45 |  | Encl. Class / Body Mat'l |  |  | Ex d IIB+H2 T4, IP65 |  |  | 316SS |  |  | Leakage |  |  | ANSI / FCI 70-2 | [7 empty] | kg/cm²-g | O
46 | Others | [20 empty] | kg/m²
47 | MANUFACTURER & MODEL | [20 empty] | kPa
48 | Item |  | Tag |  |  | Manufacturer |  |  | Model |  |  |  |  | IP Rating |  | Explosion Proof Certi. | [5 empty] | kPa-a
49 | Valve |  | 0 | [18 empty] | kPa-g
50 | Actuator | [20 empty] | lb/in²
51 | Positioner | [20 empty] | lbf/ft²
52 | Solenoid Valve | [20 empty] | mbar
53 | Limit Switch | [20 empty] | mmH2O
54 | Air Set | [20 empty] | mmHg
NOTES: | [21 empty] | MPa
Pa
Pa-a
Pa-g
psi
psi-a
psi-g
[21 empty] | Temperature | ºC | O
ºF
Project Name : LINE Project |  |  |  |  | Plant Code : |  |  |  | Req. No. : | [5 empty] | Tag Index : |  |  | of |  |  |  | ºK
[5 empty] | Rev | By | Date |  | Description |  |  |  | Chkd | Appd | Document No. | [5 empty] | Viscosity | cP | O
mPa.s
[21 empty] | Weight | g
[15 empty] | SHEET |  |  | Rev |  |  |  | kg | O
[17 empty] | Of |  |  |  |  | t
Note on E13: kg/h, Nm/h(Air, N2)
Note on F44: In General, 3-Way Type

## LIST
GENERAL | [10 empty] | PROCESS CONDITIONS (as per process data 공정한테 받은것 기입) | [62 empty] | BODY AND TRIM | [22 empty] | ACTUATOR | [8 empty] | OTHERS | [25 empty] | MANUFACTURER & MODEL | [35 empty] | NOTES | [8 empty] | HEADER
Tag No. | Service | P&ID No. | Line No. | Line Size: Inlet | Line Size: Outlet | Line Spec. | Tightness Requirements | Area Classification | NACE Requirement | Others | Fluid Name | State | Flow Rate |  |  |  | Inlet Press |  |  |  | Press Drop |  |  |  | Inlet Temp |  |  |  | Inlet Viscosity |  |  |  | Inlet Vapour Press |  |  |  | Valve Opening |  |  |  | Cv Calculated |  |  | Calc. Noise SPL |  |  |  | Design Temp |  |  | Design Press |  |  | Ambient Temp |  |  | Available Air Supply Press. |  |  | Allowable Noise SPL | Max. Shut-Off d/P |  | Critical Temp. |  | Critical Press. |  | Density | Spec. Gravity | Mol. Weight | Com. Factor (Z) | Cp/Cv | Flash | Others | Body Type | Body Size | Trim Size | Required Cv | Rated Cv | Trim Characteristic | End Conn. & Rating | Flow Direction | Flow Action To | Guiding | No. of Ports | Leakage Class | Bonnet Type | Trim Form | Material | [7 empty] | Others | Actucator Type | Actucator Size | Actucator Area | Valve Fail Position | Handwheel | Travel Stop | Bench Range | To Actuator Press Range | Others | Positioner | [8 empty] | Sol. Valve |  |  |  |  | Limit Switch | [5 empty] | Air Set |  |  |  | Tests |  | Item1 | Tag1 | Manufacturer1 | Model1 | IP Rating1 | Explosion Proof Certi.1 | Item2 | Tag2 | Manufacturer2 | Model2 | IP Rating2 | Explosion Proof Certi.2 | Item3 | Tag3 | Manufacturer3 | Model3 | IP Rating3 | Explosion Proof Certi.3 | Item4 | Tag4 | Manufacturer4 | Model4 | IP Rating4 | Explosion Proof Certi.4 | Item5 | Tag5 | Manufacturer5 | Model5 | IP Rating5 | Explosion Proof Certi.5 | Item6 | Tag6 | Manufacturer6 | Model6 | IP Rating6 | Explosion Proof Certi.6 | Note01 | Note02 | Note03 | Note04 | Note05 | Note06 | Note07 | Note08 | Note09 | Project |  |  | DOC No
[13 empty] | Unit | Min | Nor | Max | Unit | Min | Nor | Max | Unit | Min | Nor | Max | Unit | Min | Nor | Max | Unit | Min | Nor | Max | Unit | Min | Nor | Max | Unit | Min | Nor | Max | Min | Nor | Max | Unit | Min | Nor | Max | Unit | Min | Max | Unit | Min | Max | Unit | Min | Max | Unit | Min | Max |  | Unit | Max. Shut-Off d/P | Critical Temp. | Unit | Critical Press. | Unit | [21 empty] | Body | Bonnet | Plug/Ball/Disk | Seat | Cage | Stem | Gasket | Packing | [10 empty] | Positioner Type | Electrical Conn. | Power Supply | Encl. Class | Charac' | Bypass | Gauges | Signal - Inlet | Signa l- Outlet | Solenoid Valve Type | Electrical Conn. | Power Supply | Encl. Class | Body Mat'l | Type | Qty | Electrical Conn. | Enclosure Class | Contacts/Rating | Switching Position | Set Press | Filter | Gauge | Pneumatic Conn. | Hydro Press | Leakage | [45 empty] | Req No | IDX - Sh | IDX- Tot
SAMPLE DATA |  |  | P&ID 기준 기입 | Line no에 있는 piping Size | Line no에 있는 piping Size | Line no에 있는 piping class | ANSI Class IV (General) / V or VI (forTSO) | Zone1, 2(or 21, 22), IIB, T4, IP65 | NACE MR 0103(piping spec에 있으면) |  |  | Liquid, Vaor, Steam | kg/hr | as per process data |  |  | kg/cm²-g |  |  |  | kg/cm² |  |  |  | ºC |  |  |  | cP |  |  |  | kg/cm²-a |  |  |  | % | by vendor per Cal. | by vendor per Cal. | by vendor per Cal. | by vendor | by vendor | by vendor | dBA |  |  |  | ºC |  |  | kg/cm²-g |  |  | ºC |  |  | kg/cm²-g | 5 | 9 | 85 dBA | kg/cm² |  |  | ºC |  | kg/cm²-g | [7 empty] | Globe, Vee ball, butterfly, etc | by vendor | by vendor | by vendor | by vendor | RFQ EQ% and PO는 벤더 data | Piping spec에 따라 작성 | Up or down | open or close | Top or Top/Botton | one or two | Class IV(or V), tight shutoff가 있으면 VI (온도가 높아서 Metal seat만 허용 되면 V도 OK | Plain or extended (온도가 232도보다 높거나 -40도보다 낮으면) 벤더 선정되면 벤더 data따름 | Contour, Plug guide, Single Stem, Multi-Stage etc | Piping spec | Piping spec | 316 SS + Stellite or bettter(piping spec 참조) | plug 같은 material | plug 같은 material | plug 같은 material | MFR.STD | PTFE for Graphite(232도 이상시 적용) |  | Diaphragm(기본) or Cylinder w/Spring | MFR.STD | MFR.STD | Close(FC), Open(FO). Lock(FL) (PID 확인하고 작성) | Yes or No(PID 확인하고 작성) | Yes or No (P&ID상 Mech. Stop 필요시) | MFR.STD | MFR.STD |  | SMART HART | 1/2" NPT(F) | DC24V | Exd IIB+H2 T4, IP65 | Direct | N.A | Yes | 4~20mA | MFR.STD | PID보고 필요하면 3Way or 4Way | 1/2" NPT(F) | DC24V | Ex d IIB+H2 T4, IP65 | 316SS | Mechanical or Proximity(contact type) | PID보고 필요하면 | 1/2" NPT(F) | Ex d IIB+H2 T4, IP65 | SPDT / 2A AC110V | Open or Close 혹은 둘다(PID보고) | MFR.STD | Yes | Yes |  | ANSI B16.37 | ANSI / FCI 70-2 | Valve | 0 |  |  |  |  | Actuator | [5 empty] | Positioner | [5 empty] | Solenoid Valve | [5 empty] | Limit Switch | [5 empty] | Air Set