## (AR) BOQ
BOQ
Work Master Code | Gauge Code | Description | Spec. | Additional Spec. (설계자 작성) | Reference to (설계자 작성) | UoM | Total | _
[8 empty] | Steam Turbine Building | Steam Turbine Foundation | Gate House
[8 empty] | 00.20.00 | 00.20.00 | 00.21.00
[8 empty] | STB | STF | GAH
Earth Work
-
A01ZZ001-00005 |  | Excavation | Soil, Mech. 2.0M < D ≤ 4.0M | D=3.0m |  | M3 |  |  |  | 551.735
A01ZZ003-00001 |  | Backfill | Re-use, Soil Compaction=( )% | Compaction=( 95 )% |  | M3 |  |  |  | 482.521
A01ZZ004-00001 |  | Disposal | Soil Disposal Distance=Appx. ( )km from Site | Disposal Distance=Appx. (20 )km from Site |  | M3 |  |  |  | 69.216
A01ZZ005-00001 |  | Base Course | THK≤150mm THK=( )mm CBR=( )% | THK=( 150 )mm CBR=( )% |  | M2
A01ZZ006-00001 |  | Subbase Course | Including Compaction of Sub-Grade THK≤150mm THK=( )mm CBR=( )% for Subgrade, ( )% for Subbase Compaction=( )% for Subgrade, ( )% for Subbase | THK=( 150 )mm / CBR=(10 )% for Subgrade, (80 )% for Subbase Compaction=(90 )% for Subgrade, (95 )% for Subbase |  | M2
A01ZZ012-00001 |  | PE Sheet (Vapor Barrier) | THK=( )mm | THK=( 0.1 )mm |  | M2
Pile Work
Piling Work
A02AA020-00001 |  | Steel Pipe Pile Work | Direct Driving Including Pile Connection and Joint Welding Work D=( )mm / THK=( )mm Pile Length per Hole=( )M | D=( 508 )mm / THK=(12 )mm Pile Length per Hole=( 30 )M |  | M
Pile Head Treatment
A02AB020-00001 |  | Steel Pipe Pile Work | D=( )mm / THK=( )mm | D=( 508 )mm / THK=(12 )mm Pile Length per Hole=( 30 )M |  | EA
Concrete Work
Substructure Work
A03AD032-00010 |  | Structural Concrete | Cement Type-1 20MPa < F'c (Cylinder Strength) ≤ 25MPa | F'c (Cylinder Strength) = 24MPa |  | M3 |  |  |  | 21.046
A03AD032-00012 |  | Structural Concrete | Cement Type-5 20MPa < F'c (Cylinder Strength) ≤ 25MPa | F'c (Cylinder Strength) = 24MPa |  | M3 |  |  |  | 46.618
A03AD034-00004 |  | Lean Concrete (including Form work) | Cement Type-1 10MPa < F'c (Cylinder Strength) ≤ 20MPa | F'c (Cylinder Strength) = 18MPa |  | M3
A03AD035-00001 |  | Form Work (3 times in use) | Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | Form Work (3 times in use) |  | M2 |  |  |  | 137.729
A03AD037-00002 |  | Rebar Work | Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | ASTM A615 GRADE 60 (Fy=420MPa) |  | TON |  |  |  | 11.641
Mass Concrete Work
A03AE032-00009 |  | Structural Concrete | Cement Type-5 25MPa < F'c (Cylinder Strength) ≤ 30MPa Including Concrete Temperature Control (Pile Cooling & Curing), Max Temperature of Concrete : 30℃ | F'c (Cylinder Strength) = 30MPa |  | M3
A03AE037-00002 |  | Rebar Work | Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | ASTM A615 GRADE 60 (Fy=420MPa) |  | TON
A03AE052-00001 |  | Concrete Temperature Monitoring | Including Themo Coupler, Monitoring & Record Acc. To Approved MS | Including Themo Coupler, Monitoring & Record Acc. To Approved MS |  | M3
A03AE054-00001 |  | System Form | Heavy Duty Forms, Metal Framed Playwood forms Including Form Tie, All Accessories, Sealing of Form Tie Hole, Separator & Anchor Box out, Chamfer for Exposed Edge, Opening & Sleeve, Shoring, Scaffording, Safety Measures and Shop Drawing | Including Form Tie, All Accessories, Sealing of Form Tie Hole, Separator & Anchor Box out, Chamfer for Exposed Edge, Opening & Sleeve, Shoring, Scaffording, Safety Measures and Shop Drawing |  | M3
Superstructure Work
A03AF032-00010 |  | Structural Concrete | Cement Type-1 20MPa < F'c (Cylinder Strength) ≤ 25MPa | F'c (Cylinder Strength) = 24MPa |  | M3 |  |  |  | 69.622
A03AF036-00001 |  | Form Work (1 time in use) | Flat Form Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer |  |  | M2 |  |  |  | 429.503
A03AF037-00002 |  | Rebar Work | Deformed Bar (Non-Coat.) 400MPa<Fy≤470MPa | ASTM A615 GRADE 60 (Fy=420MPa) |  | TON |  |  |  | 6.389
Concrete Protective Coating (U/G)
A03AH056-00001 |  | Bitumen/Bituminous/Asphalt Coating |  | Bitumen/Bituminous/Asphalt Coating |  | M2 |  |  |  | 127.28
A03AH059-00001 |  | Sheet Membrane | Adhesive Rubber Sheet or Bitumen Polyethylene Laminated Waterproofing Membrane THK=( )mm | THK=( 4 )mm |  | M2
A03AH060-00001 |  | Memebrane Protection Board | Bitumen Impregnated Fiberboard THK=( )mm | THK=( 6 )mm |  | M2
Finishing Work
Masonry Work
A04AL069-00001 |  | Reinforced Concrete Block | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 50mm<THK≤100mm THK=( )mm | THK=( 100 )mm |  | M2 |  |  |  | 59.604
A04AL069-00002 |  | Reinforced Concrete Block | w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 100mm<THK≤200mm THK=( )mm | THK=( 200 )mm |  | M2 |  |  |  | 169.835
A04AL073-00001 |  | Concrete Brick | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. THK≤90mm THK=( )mm | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. / THK=(90)mm |  | M2
A04AL073-00002 |  | Concrete Brick | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. 90mm<THK≤190mm THK=( )mm | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. / / THK=(190)mm |  | M2
A04AL076-00002 |  | Insulation | Mineral Wool (Rock Wool) Minimum Density of 50 kg/m3 50mm≤THK<75mm THK=( )mm | THK=( 50 )mm |  | M2 |  |  |  | 59.604
A04AL076-00008 |  | Insulation | Glass Wool (Fiberglass) Minimum Density of 50 kg/m3 100mm≤THK THK=( )mm | THK=( 100 )mm |  | M2
Painting Work
A04AM077-00001 |  | External Wall Painting | Acrylic Emulsion Paint |  |  | M2 |  |  |  | 82.554
A04AM078-00001 |  | Internal Wall Painting | Acrylic Emulsion Paint |  |  | M2 |  |  |  | 40.831
A04AM078-00002 |  | Internal Wall Painting | Water Emulsion Paint | Water Emulsion Paint |  | M2 |  |  |  | 269.954
A04AM080-00003 |  | Floor Painting | Acid/Alkaline Resistant Paint | Acid/Alkaline Resistant Paint |  | M2
A04AM080-00006 |  | Floor Painting | Epoxy Paint | Epoxy Paint |  | M2
Tile Work
A04AN082-00002 |  | Wall Tile | Glazed Ceramic Tile w/ Mortar Bond Coat or Adhesive Tile Size=W( )mm x L( )mm x THK( )mm | Glazed Ceramic Tile |  | M2 |  |  |  | 10.112
A04AN083-00001 |  | Floor Tile | Ceramic Tile Non-Slip Type, w/ Mortar Bond Coat or Adhesive Tile Size=W( )mm x L( )mm x THK( )mm | Non-Slip Type, w/ Mortar Bond Coat or Adhesive |  | M2
Waterproofing Work
A04AP085-00001 |  | Liquid Waterproofing | for Internal Floor Area Min. 2 Coats | for Internal Floor Area |  | M2
Roof Work
A04AQ012-00001 |  | PE Sheet (Vapor Barrier) | THK=( )mm | THK=( 0.1 )mm |  | M2
A04AQ038-00001 |  | Welded Wire Fabric | DIA≤6mm Mesh Size=DIA( )mm x ( )mm x ( )mm | Mesh Size=DIA( #8 )mm x ( 150 )mm x (150 )mm |  | M2
A04AQ086-00004 |  | Roof Screed | Bed Mortar Screed w/o Welded Wire Fabric 30mm≤Min. THK<50mm Min. THK=( )mm, Slope=( ) | Min. THK=(50 )mm, Slope=(1:100 ) |  | M3
A04AQ088-00004 |  | Roof Insulation | Rigid Extruded Polystyrene Foam Insulation 100mm≤THK THK=( )mm | Rigid Extruded Polystyrene Foam Insulation 압출법 보온판 / THK=( 150 )mm |  | M2
A04AQ089-00001 |  | Protective Concrete w/ Steel Trowel Finish |  | Protective Concrete w/ Steel Trowel Finish |  | M3
A04AQ090-00001 |  | Concrete Tile | w/ Plastic Spacer THK≤50mm THK=( )mm | 300x300xT50 |  | M2
A04AQ310-00001 |  | Waterproofing Membrane | EPDM(or Equivalent) w/ Accessories THK=( )mm | EPDM(or Equivalent) THK=( 4 )mm |  | M2
Door & Window Work
A04AR099-00001 |  | Steel Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Single Door w/ Hardware & Accessories W x H=( )mm x ( )mm | W x H=( 1000 )mm x (2100 )mm |  | EA |  |  |  | 5
A04AR103-00002 |  | Steel Door w/ Steel Frame & Panic Bar (UoM: EA) | Fire Protective Rating: N/A, Double Door w/ Hardware & Accessories W x H=( )mm x ( )mm | W x H=( 2100 )mm x (2100 )mm |  | EA
A04AR127-00001 |  | Steel Roll Up Door w/ Steel Frame (UoM: EA) | Fire Protective Rating: N/A, Motorized Type w/ Hardware & Accessories W x H=( )mm x ( )mm | W x H=( 5000 )mm x (6000 )mm |  | EA
A04AR159-00001 |  | Aluminum Window (UoM: EA) | Fire Protective Rating: N/A w/ Hardware & Accessories W x H=( )mm x ( )mm | W x H=( 600 )mm x (600 )mm |  | EA |  |  |  | 4
A04AR161-00001 |  | uPVC Window (UoM: EA) | w/ Hardware & Accessories W x H=( )mm x ( )mm | W x H=( 1200 )mm x (1200 )mm X Double |  | EA |  |  |  | 2
A04AR164-00001 |  | Louver (UoM: EA) | Aluminum w/ Hardware & Accessories W x H=( )mm x ( )mm | W x H=( 610 )mm x (610 )mm |  | EA |  |  |  | 1
Exterior/Interior Finish Work
A04AS173-00001 |  | Steel Trowel Finish |  | Steel Trowel Finish |  | M2
A04AS173-00003 |  | Steel Trowel Finish | Hardener Finish(Powder Type) | Hardener Finish(Powder Type) |  | M2
A04AS174-00001 |  | Raised Floor | Top Finish: Anti-Static Vinyl Tile 600mm x 600mm / H≤600mm H=( )mm | H=( 600 )mm Top Finish: Anti-Static Vinyl Tile |  | M2
A04AS185-00001 |  | Coved Rubber Skirting | for Skirt w/ Adhesive H<150mm H=( )mm | H=( 100 )mm |  | M
A04AS190-00002 |  | Acoustic Tiled Ceiling System | T-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) Tile Size=( )mm x ( )mm | Tile Size=( 600 )mm x (600 )mm |  | M2 |  |  |  | 81.652
A04AS191-00001 |  | Moisture Resistant Tiled Ceiling System | M-Bar System w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) Tile Size=( )mm x ( )mm | Tile Size=( 600 )mm x (1200 )mm |  | M2 |  |  |  | 5.635
Plastering Work
A04AT198-00001 |  | Plastering | for External Masonry Wall THK=( )mm | for External Masonry Wall / THK=(18)mm |  | M2 |  |  |  | 59.604
A04AT198-00002 |  | Plastering | for Internal Masonry Wall THK=( )mm | for Internal Masonry Wall / THK=(12)mm |  | M2 |  |  |  | 269.954
Misc. Work
Furniture Installation
Cladding Work
-
A05ZZ199-00005 |  | Single Metal Sheet | Corrugated Galvanized Steel Sheet for Wall w/ Accessories, Flashing THK=( )mm | THK=( 0.7 )mm |  | M2
A05ZZ199-00006 |  | Single Metal Sheet | Corrugated Galvanized Steel Sheet for Roof w/ Accessories, Flashing THK=( )mm | THK=( 0.7 )mm |  | M2
A05ZZ200-00003 |  | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Wall w/ Accessories, Flashing 100mm≤THK<150mm THK=( )mm | THK=( 120 )mm |  | M2
A05ZZ200-00008 |  | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Mineral Wool (Rock Wool) for Roof w/ Accessories, Flashing 150mm≤THK THK=( )mm | THK=( 200 )mm |  | M2
A05ZZ200-00032 |  | Sandwich Panel | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A Glass Wool (Fiberglass) for Roof w/ Accessories, Flashing 150mm≤THK THK=( )mm | THK=( 200 )mm |  | M2
A05ZZ204-00001 |  | Gutter | Galvanized Steel Eave Gutter w/ Coating w/ Accessories THK=( )mm | THK=( 0.7 )mm |  | M
Main Steel Structure Fabrication Work
Shelter/Building
S01AA001-00001 |  | Heavy Steel - Standard (Weight≥90KG/M) | Material: ( ) | Material: (KSD3515, SM355) W= 322.4 kg/m |  | TON
S01AA002-00001 |  | Medium Steel - Standard (90KG/M>Weight≥30KG/M) | Material: ( ) | Material: ( KS D 3503 SS275 ) A=63.53 cm2, W=49.9 kg/m, S=1.162 m2/m |  | TON
S01AA003-00001 |  | Light Steel - Standard (30KG/M>Weight) | Material: ( ) | W=22.898 kg/m |  | TON
S01AA007-00001 |  | Girth & Purlin | Material: ( ) |  |  | TON
S01AA010-00001 |  | Steel Painting/Coating | for Non-Fireproofed Steel Surface, Surface Preparation, Primer, Second & Final Coat Material: ( ) |  |  | M2
Miscellaneous Steel Fabrication Work
Shelter/Building
S02AA017-00001 |  | Checkered/Flooring Plate | Material: ( ) THK=( )mm | Material: ( ASTM A36 ) THK=( 6 )mm |  | M2
S02AA018-00001 |  | Grating | Material: ( ) THK=( )mm | Material: ( ASTM A 1011M ) THK=( 32 )mm |  | M2
S02AA020-00001 |  | Steel Handrails | Material: ( ) H=( )mm | Material: ( KS D 3566, ASTM A53 grade B ) H=(1100)mm |  | M |  |  |  | 23.478
S02AA024-00001 |  | Galvanized Steel Deck Plate | THK=( )mm | THK=(1.6) mm 600x200x75 |  | M2
Main Steel Structure Erection Work
Shelter/Building
S03AA007-00001 |  | Girth & Purlin | Material: ( ) |  |  | TON
S03AA027-00001 |  | Heavy Steel (Weight≥90KG/M) | Material: ( ) | Material: (KSD3515, SM355) W= 322.4 kg/m |  | TON
S03AA028-00001 |  | Medium Steel (90KG/M>Weight≥30KG/M) | Material: ( ) | Material: ( KS D 3503 SS275 ) A=63.53 cm2, W=49.9 kg/m, S=1.162 m2/m |  | TON
S03AA029-00001 |  | Light Steel (30KG/M>Weight) | Material: ( ) |  |  | TON
Miscellaneous Steel Erection Work
Shelter/Building
S04AA017-00001 |  | Checkered/Flooring Plate | Material: ( ) THK=( )mm | Material: ( ASTM A36 ) THK=( 6 )mm |  | M2
S04AA018-00001 |  | Grating | Material: ( ) THK=( )mm | Material: ( ASTM A 1011M ) THK=( 32 )mm |  | M2
S04AA020-00001 |  | Steel Handrails | Material: ( ) H=( )mm | Material: ( KS D 3566, ASTM A53 grade B ) H=(1100)mm |  | M |  |  |  | 23.478
S04AA024-00001 |  | Galvanized Steel Deck Plate | THK=( )mm | THK=(1.6) mm 600x200x75 |  | M2