## Rev.7
BUILDING LIST
<현대차 울산공장 복합화력 발전소, P-UHP / 울산>
[14 empty] | Rev.7 (변경사항 청색 Text) |  |  |  | 2022.03.22
NO. | PLOT PLAN NO. | BUILDING NAME | STR. TYPE | Q'TY | STORY | LOCATION |  |  | SIZE |  | Building Area | Floor Total Area | Volume | LIFTING | SANITARY |  |  | Remark
[8 empty] | W(m) | L(m) | H(m) | for 1 unit (m2) | for 1 unit (m2) | for 1 unit (m3) | FACILITY | TOILET | SHOWER | KITCHEN TEA ROOM
1 | 1 | Gas Turbine Building #1 & #2 | ST | 1 | 1 | - |  | 24.2 | 47.8 | 11.35 | 1156.76 | 1156.76 | 13129.226 |  |  |  |  | * 괌 기준 2호기 해당 Size = 69x24.2 * Plot plan Seq.23 (22mx44m 증가)
[6 empty] | Ground Floor |  | 24.2 | 47.8 | 11.35 | 1156.76 | 1156.76 | 13129.226 |  |  |  |  | * Air Intake - Roof (괌)
[6 empty] | Ground | Turbine Hall #1 | 24.2 | 23.3 | 11.35 |  | 563.86 | 6399.811 | Crane 미적용(괌)
[7 empty] | GCB Platform #1 | 4.8 | 9.8 | 4.5
[7 empty] | Turbine Hall #2 | 24.2 | 24.5 | 11.35 |  | 592.9 | 6729.415
[7 empty] | GCB Platform #2 | 4.8 | 9.8 | 4.5 | [7 empty] | * 괌 기준 GCB Platform 2개호기
1-1 | 1 | Gas Turbine Foundation #1 & #2 | RC | 2 | 1 | - |  | 7.5 | 21.4 | 2.5 | 160.5 | 321 | [5 empty] | * 괌 기준 동일 적용
[6 empty] | GT FDN |  | 7.5 | 21.4 | 2.5 | 160.5
[6 empty] | GT FDN | GT FDN | 7.5 | 21.4 | 2.5
2 | 3 | Steam Turbine Building | ST | 1 | 2 | - |  | 20 | 58 | 7 / 17 | 1160 | 2040 | 16920 |  |  |  |  | * Plot Plan Seq.23 (18x50 => 20x58 증가)
[6 empty] | Ground Floor |  | 20 | 58 | 4 |  | 1160 | 5480
[6 empty] | Ground | Turbine Hall Area | 20 | 44 | 4 |  | 880 | 3520 | OHC 40/5 ton |  |  |  | * Siemens TG Hall Layout 18mx40m * Plot plan Seq.23 (22mx44m 증가)
[6 empty] | Ground | CCW Pump & Cooler Area | 20 | 10 | 7 |  | 200 | 1400
[6 empty] | Ground | Air Compressor Room | 20 | 4 | 7 |  | 80 | 560 |  |  |  |  | [기계 확인 요망-Hoist]
[6 empty] | Operating Floor |  | 20 | 44 | 13 |  | 880 | 11440
[6 empty] | Operating Floor |  | 20 | 44 | 13 |  | 880 | 11440 |  |  |  |  | * Plot Plan Seq.23
* Piperack 삭제, Mezzanine FL 하부로 Hanging (Plot plan Seq.11)
2-1 | 3 | Steam Turbine Foundation | RC | 1 | - | - |  | 8.7 | 23 | 6.5 | 200.1 | 200.1 | [5 empty] | * Siemens GA 적용
[6 empty] | ST FDN |  | 8.7 | 23 | 6.5 | 200.1
[6 empty] | ST FDN | ST + Condensor FDN | 8.7 | 23 | 6.5
3 | 25 | Control & Electrical and Administration Building | RC | 1 | 4 | - |  | 15 | 58 | 20.5 | 870 | 3480 | 17835 |  |  |  |  | * 괌 24x40 (지상3층) => 지하1층+지상3층 : CCB+ Administration Building+GIS : 첨부 평면 Rev.C 참조 * 지하수위 높음, 가시설 물량 절감을 위해 지상4층 * 금액절감을 위한 구조변경 (STL > RC)
[6 empty] | Ground Floor |  | 15 | 58 | 3.5 | 870
[6 empty] | Ground Floor | Cable Room | 15 | 44 | 3.5 | 585
[6 empty] | Ground Floor | Battery Room | 5 | 11 | 3.5 | 55 | [6 empty] | 건축) 07/22 -층 이동
[6 empty] | Ground Floor | Toilet (M) | 2.5 | 5.5 | 3 | 13.75
[6 empty] | Ground Floor | Toilet (F) | 2.5 | 5.5 | 3 | 13.75
[6 empty] | Ground Floor | Lobby-1 | 14 | 9.5 | 3 | 83.5
[6 empty] | Ground Floor | Lobby-2 | 6 | 7.5 | 3 | 45
[6 empty] | Ground Floor | Elevator | 3.5 | 4 | 3.5 | 14
[6 empty] | Ground Floor | Staircase-1 | 4 | 7.5 | 3.5 | 30
[6 empty] | Ground Floor | Staircase-2 | 4 | 7.5 | 3.5 | 30
[6 empty] | 2nd Floor |  | 15 | 58 | 6 | 870
[6 empty] | 2nd Floor | Electrical Room-1 | 7.5 | 39 | 6 | 292.5
[6 empty] | 2nd Floor | Electrical Room-2 | 7.5 | 39 | 6 | 280 | [6 empty] | '건축) 07/22 -Room 면적 확대
[6 empty] | 2nd Floor | Electrical Room (GIS) | 7.5 | 10 | 6 | 75 | [6 empty] | '건축) 07/22 -Room 면적 확대
[6 empty] | 2nd Floor | Toilet (M) | 2.5 | 5.5 | 3 | 13.75
[6 empty] | 2nd Floor | Toilet (F) | 2.5 | 5.5 | 3 | 13.75
[6 empty] | 2nd Floor | Lobby-1 | 9 | 9.5 | 3 | 63.5
[6 empty] | 2nd Floor | Lobby-2 | 6 | 7.5 | 3 | 45
[6 empty] | 2nd Floor | Elevator | 3.5 | 4 | 6 | 14
[6 empty] | 2nd Floor | Staircase-1 | 4 | 7.5 | 6 | 30
[6 empty] | 2nd Floor | Staircase-2 | 4 | 7.5 | 6 | 30
[6 empty] | 2nd Floor | Duct Shaft | 2.5 | 5 | 6 | 12.5
[6 empty] | 3rd Floor |  | 15 | 58 | 6.5 | 870
[6 empty] | 3rd Floor | Central Control Room | 7.5 | 39 | 3 | 244
[6 empty] | 3rd Floor | Electronic Room | 7.5 | 27 | 3 | 202.5
[6 empty] | 3rd Floor | Engineering Room | 4.5 | 8 | 3 | 36 | [6 empty] | *계장 (7/13) : Aux. Control Room 삭제
[6 empty] | 3rd Floor | Electrical Room -3 | 7.5 | 12 | 6.5 | 90 | [6 empty] | *전기 (7/16) :IOM
[6 empty] | 3rd Floor | Communication Room | 4.5 | 8 | 3 | 36 | [6 empty] | *전기 (7/16) :IOM
[6 empty] | 3rd Floor | Duct Shaft-1 | 2.5 | 5 | 6.5 | 12.5
[6 empty] | 3rd Floor | Duct Shaft-2 | 2 | 7.5 | 6.5 | 15
[6 empty] | 3rd Floor | Toilet (M) | 2.5 | 5 | 3 | 12.5
[6 empty] | 3rd Floor | Toilet (F) | 2.5 | 5 | 3 | 12.5
[6 empty] | 3rd Floor | Lobby-1 | 9 | 9.5 | 3 | 63.5
[6 empty] | 3rd Floor | Lobby-2 | 8 | 10.5 | 3 | 69
[6 empty] | 3rd Floor | Elevator | 3.5 | 4 | 6.5 | 14
[6 empty] | 3rd Floor | Staircase-1 | 4 | 7.5 | 6.5 | 30
[6 empty] | 3rd Floor | Staircase-2 | 4 | 7.5 | 6.5 | 30
[6 empty] | 4th Floor |  | 15 | 58 | 4.5 | 870
[6 empty] | 4th Floor | Manager Office-1 | 7.5 | 4.5 | 3 | 33.75
[6 empty] | 4th Floor | Meeting Room-2 | 7.5 | 4.5 | 3 | 33.75
[6 empty] | 4th Floor | Meeting Room-1 | 5.1 | 9 | 3 | 45.9
[6 empty] | 4th Floor | Training Room | 7.5 | 7 | 3 | 52.5
[6 empty] | 4th Floor | Open Office | 7.5 | 18 | 3 | 135
[6 empty] | 4th Floor | Shift Operator Room | 5.1 | 6 | 3 | 30.6
[6 empty] | 4th Floor | Fire Gas Room | 5.1 | 8 | 4.5 | 40.8
[6 empty] | 4th Floor | Document Room | 5.1 | 6 | 3 | 30.6
[6 empty] | 4th Floor | Storage | 5.1 | 6 | 4.5 | 30.6
[6 empty] | 4th Floor | Break Room | 5.1 | 12 | 3 | 48.7
[6 empty] | 4th Floor | Toilet/Shower/Locker(M) | 4 | 9 | 3 | 36
[6 empty] | 4th Floor | Toilet/Shower/Locker(F) | 5.1 | 5 | 3 | 25.5
[6 empty] | 4th Floor | Lobby-1 | 9.9 | 10 | 3 | 79
[6 empty] | 4th Floor | Lobby-2 | 9.9 | 8 | 3 | 64.2
[6 empty] | 4th Floor | Corridor | 2.4 | 34 | 3 | 81.6
[6 empty] | 4th Floor | Duct Shaft-1 | 2.5 | 5 | 4.5 | 12.5
[6 empty] | 4th Floor | Duct Shaft-2 | 2 | 7.5 | 4.5 | 15
[6 empty] | 4th Floor | Elevator | 3.5 | 4 | 4.5 | 14
[6 empty] | 4th Floor | Staircase-1 | 4 | 7.5 | 4.5 | 30
[6 empty] | 4th Floor | Staircase-2 | 4 | 7.5 | 4.5 | 30
4 | 13 | Water Treatment Building | RC | 1 | 2 | - |  | 19 | 41 | 6.0 /4.5 | 779 | 1007 | 5700 |  |  |  |  | *환경(11/12 메일) : 열병합추가로 Size증가 '* Plot Plan Seq.11 반영
[6 empty] | Ground Floor |  | 19 | 41 | 6 | 779 | 779 | 4674
[6 empty] | Ground Floor | Equipment Room | 19 | 41 | 6 | 707 |  |  | Hoist 2 ton |  |  |  | 기계(200707)Hoist 3 ton , Eye Washer
[6 empty] | Ground Floor | Chemical Storage | 6 | 9 | 6 | 54
[6 empty] | Ground Floor | Stair | 3 | 6 | 6 | 18
[6 empty] | 2nd Floor |  | 19 | 12 | 4.5 | 228 | 228 | 1026 |  |  |  |  | * Plot Plan Rev.A 반영(07/10)
[6 empty] | 2nd Floor | MCC Room | 10 | 12 | 4.5 | 120
[6 empty] | 2nd Floor | Control Room | 6 | 9 | 4.5 | 54
[6 empty] | 2nd Floor | Fire Gas Room | 3 | 2 | 4.5 | 6 | [6 empty] | 소방) 07/15 메일 회신
[6 empty] | 2nd Floor | Toilet | 3 | 4 | 4.5 | 12
[6 empty] | 2nd Floor | Stair | 3 | 6 | 4.5 | 18
[6 empty] | 2nd Floor | Corridor | 3 | 6 | 4.5 | 18
5 | 36 | Compressor Air Package Building |  |  |  | - | [11 empty] | * Plot Plan S23(22.01.20) : STB에 통합
6 |  | Gate House - Option | [15 empty] | * Plot Plan S23(22.01.20)에서 삭제
BUILDING TOTAL |  |  |  | 4 | [6 empty] | 3965.76 | 7683.76 | 53584.226
S-1 | 11 | Chemical Dosing Shelter for Cooling Tower | ST | 1 | 1 | - |  | 5 | 8 | 4 | 40 | 40 | 160 |  |  |  |  | * 환경) 사이즈 축소(12/29-email)
[6 empty] | Ground Floor | Shelter Area | 5 | 8 | 4 | 40 | [6 empty] | * 환경) shelter 적용(7/14-IOM)
S-2 | 26 | Chemical Dosing Shelter for HRSG | ST | 1 | 1 | - |  | 4.3 | 7.6 | 4 | 32.68 | 32.68 | 130.72 |  |  |  |  | * 배관) IOM회신(7/15) Size 반영 * 환경) Size 재검토 요망 : IOM 5x8
[6 empty] | Ground Floor | Shelter Area | 4.3 | 7.6 | 4 | 32.68
S-4 | 19 | Service Gas Storage Shelter (N2) | ST | 1 | 1 | - |  | 4 | 11 | 4 | 44 | 44 | 176 |  |  |  |  | * 사이즈 증가 (Plot plan Seq.12 반영, 1/8) * Building 적용여부 기계팀 검토중(1/8)
[6 empty] | Ground Floor | Shelter Area | 4 | 11 | 4 | 44
S-5 | 37 | Chemical Storage Tank Shelter | ST | 1 | 1 | - |  | 6.6 | 5.4 | 5 | 35.64 | 35.64 | 178.2 |  |  |  |  | '* 건축(11/11) : Building 항목에서 분리 * 환경) IOM회신(11/20) : 사이즈 축소, Deviation 예정사항
[6 empty] | Ground Floor | Chemical Tank Area | 6.6 | 5.4 | 5 | 35.64
SHELTER TOTAL |  |  |  | 4 | [6 empty] | 152.32 | 152.32 | 644.92
TOTAL |  |  |  | 8 | [6 empty] | 4118.08 | 7836.08 | 54229.146
※ Note : | 1. The dimension of each building specified above are indicative only, and shall be subject to change according to the detail design of project implementation stage. 2. OHC : Overhead Crane, H : Hoist, ELEV : Elevator

## Rev.3
BUILDING LIST
<현대차 울산공장 복합화력 발전소, P-UHP / 울산>
[14 empty] | Rev.3 (변경사항 청색 Text) |  |  |  | 2021.01.08
NO. | PLOT PLAN NO. | BUILDING NAME | STR. TYPE | Q'TY | STORY | LOCATION |  |  | SIZE |  | G. FLOOR AREA | TOTAL AREA | VOLUME | LIFTING | SANITARY |  |  | Remark
[8 empty] | W(m) | L(m) | H(m) | for 1 unit (m2) | for 1 unit (m2) | for 1 unit (m3) | FACILITY | TOILET | SHOWER | KITCHEN TEA ROOM
1 | 1 | Gas Turbine Building | ST | 1 | 1 | - |  | 46.3 | 24.2 | 11.35 | 1120.46 | 1213.56 | 12717.221 |  |  |  |  | * 괌(69x24.2) 기준 2호기 해당 Size 적용
[6 empty] | Ground Floor |  | 46.3 | 24.2 | 11.35 | 1120.46 | [6 empty] | * Air Intake - Roof (괌)
[6 empty] | Ground | Turbine Hall | 46.3 | 24.2 | 11.35 | 1120.46 |  |  | Crane 미적용(괌)
[6 empty] | Mezzanine Floor |  | - | - | - | 93.1
[6 empty] | Mezz. | GCB Platform | 4.75 | 9.8 | 4.5 | 93.1 | [6 empty] | * 괌 기준 GCB Platform 2호기
1-1 | 1 | Gas Turbine Foundation | RC | 2 | 1 | - |  | 21.4 | 7.5 | 2.5 | 160.5 | 321 | [5 empty] | * 괌 기준 동일 적용
[6 empty] | GT FDN |  | 21.4 | 7.5 | 2.5 | 160.5
[6 empty] | GT FDN | GT FDN | 21.4 | 7.5 | 2.5 | 160.5
2 | 3 | Steam Turbine Building | ST | 1 | 2 | - |  | 18 | 50 | 17 / 6 | 900 | 1436 | 13320 |  |  |  |  | * Siemens GA반영 (Plot plan Seq.11)
[6 empty] | Ground Floor |  | 18 | 50 | 4 | 900
[6 empty] | Ground | Turbine Hall | 18 | 40 | 4 | 720 |  |  | OHC 40/5 ton |  |  |  | * Siemens GA반영 (Plot plan Seq.11)
Grand Steam Condenser
[7 empty] | CEP |  |  |  | L=7.7m
[6 empty] | Ground | Aux Bay | 18 | 10 | 6 | 180 | [6 empty] | * Plot plan Seq.11 반영
[6 empty] | Operating Floor |  | 18 | 43 | 13 | 536
[6 empty] | Operating Floor |  | 18 | 43 | 13 | 536 |  |  | OHC 40/5 ton |  |  |  | * Siemens GA반영 (Plot plan Seq.11)
[6 empty] | Ground | Pipe Rack | [10 empty] | * Piperack 삭제, Mezzanine FL 하부로 Hanging (Plot plan Seq.11)
2-1 | 3 | Steam Turbine Foundation | RC | 1 | - | - |  | 23 | 8.7 | 6.5 | 200.1 | 200.1 | [5 empty] | * Siemens GA 적용(Plot plan Seq.11)
[6 empty] | ST FDN |  | 23 | 8.7 | 6.5 | 200.1
[6 empty] | ST FDN | ST FDN | 23 | 8.7 | 6.5 | 200.1
3 | 2 | HRSG Building - Option | ST |  | 1 | - |  | 23.5 | 36.7 | 29.5/13.5 | 862.45 | 0 | 22108.3 |  |  |  |  | * Plot Plan Seq.10 반영(12/29) : HRSG Building 삭제
|  | (HRSG Building Type 미적용시 삭제 예정) |  |  |  | Ground Floor |  | 23.5 | 36.7 | 29.5 | 862.45
|  | (하기 4-1 물량을 제외한 건물 전체) |  |  |  | Ground | HRSG Area #1 | 23.5 | 14 | 29.5 | 329 |  |  | Hoist 2ton
[6 empty] | Ground | HRSG Area #2 | 23.5 | 14 | 29.5 | 329 |  |  | Hoist 2ton |  |  |  | * (Elevator 1대 반영에 따른) Walkway 반영
[6 empty] | Ground | HRSG Maintenance Area | 23.5 | 8.7 | 13.5 | 204.45
[6 empty] | Ground | HRSG Maintenance Area #2 | 18 | 11.1 | 13.5 | 199.8 | [6 empty] | * Including Platform (4.85x9.5x5.3 + 4.85x12x9.8)
3-1 | 2 | HRSG Foundation | ST |  | 1 | - |  | 12 | 23.5 | 2.5 | 282 | 0
|  | (HRSG Building Area내 모든 기초) |  |  |  | Ground Floor |  | 12 | 23.5 | 2.5 | 282
[6 empty] | Ground | HRSG Foundation | 12 | 23.5 | 2.5 | 282
3 | 25 | Control & Electrical and Administration Building | RC | 1 | 4 | - |  | 18 | 42 | 18 | 756 | 3024 | 13608 |  |  |  |  | * 괌 24x40 (지상3층) => 지하1층+지상3층 : CCB+ Administration Building+GIS : 첨부 평면 Rev.C 참조 * 지하수위 높음, 가시설 물량 절감을 위해 지상4층 * 금액절감을 위한 구조변경 (STL > RC)
[6 empty] | Ground Floor |  | 18 | 42 | 3.5 | 756
[6 empty] | Ground Floor | Cable Room | 18 | 42 | 3.5 | 625.5
[6 empty] | Ground Floor | Battery Room(CCB+GIS) | 9 | 6.5 | 3.5 | 58.5 | [6 empty] | 건축) 07/22 -층 이동
[6 empty] | Ground Floor | Lobby | 4 | 9 | 3.5 | 36
[6 empty] | Ground Floor | Elevator | 4 | 3 | 3.5 | 12
[6 empty] | Ground Floor | Staircase | 4 | 6 | 3.5 | 24
[6 empty] | 2nd Floor |  | 18 | 42 | 5.5 | 756
[6 empty] | 2nd Floor | Electrical Room-1 | 9 | 34 | 5.5 | 306
[6 empty] | 2nd Floor | Electrical Room-2 | 9 | 32 | 5.5 | 288 | [6 empty] | '건축) 07/22 -Room 면적 확대
[6 empty] | 2nd Floor | Electrical Room (GIS) | 9 | 10 | 5.5 | 90 | [6 empty] | '건축) 07/22 -Room 면적 확대
[6 empty] | 2nd Floor | Lobby | 4 | 9 | 5.5 | 36
[6 empty] | 2nd Floor | Elevator | 4 | 3 | 5.5 | 12
[6 empty] | 2nd Floor | Staircase | 4 | 6 | 5.5 | 24
[6 empty] | 3rd Floor |  | 18 | 42 | 5.5 | 756
[6 empty] | 3rd Floor | Central Control Room | 9 | 24 | 5.5 | 216
[6 empty] | 3rd Floor | Electronic Room | 9 | 24 | 5.5 | 216
[6 empty] | 3rd Floor | Computer Room | 7 | 3.5 | 5.5 | 24.5 | [6 empty] | *계장 (7/13) : Aux. Control Room 삭제
[6 empty] | 3rd Floor | Electrical Room -3 | 9 | 10 | 5.5 | 90 | [6 empty] | *전기 (7/16) :IOM
[6 empty] | 3rd Floor | Communication Room | 7 | 3.5 | 5.5 | 24.5 | [6 empty] | *전기 (7/16) :IOM
[6 empty] | 3rd Floor | Duct Shaft | 2.4 | 4.5 | 5.5 | 10.8
[6 empty] | 3rd Floor | Toilet (M) | 4 | 4.5 | 5.5 | 18
[6 empty] | 3rd Floor | Toilet/Shower/Locker(F) | 5.6 | 4.5 | 5.5 | 25.2
[6 empty] | 3rd Floor | Corridor | 4 | 13.5 | 5.5 | 95
[6 empty] | 3rd Floor | Elevator | 4 | 3 | 5.5 | 12
[6 empty] | 3rd Floor | Staircase | 4 | 6 | 5.5 | 24
[6 empty] | 4th Floor |  | 18 | 42 | 3.5 | 756
[6 empty] | 4th Floor | Manager Office-1 | 6.5 | 4 | 3.5 | 26
[6 empty] | 4th Floor | Manager Office-2 | 6.5 | 4 | 3.5 | 26
[6 empty] | 4th Floor | Meeting Room-1 | 6 | 11.5 | 3.5 | 69
[6 empty] | 4th Floor | Meeting Room-2 | 6.5 | 8 | 3.5 | 52
[6 empty] | 4th Floor | Open Office | 9 | 16.5 | 3.5 | 148.5
[6 empty] | 4th Floor | Office-1 | 6.5 | 5 | 3.5 | 32.5
[6 empty] | 4th Floor | Fire Gas Room | 6.5 | 5 | 3.5 | 32.5
[6 empty] | 4th Floor | Document Room | 3 | 11.5 | 3.5 | 34.5
[6 empty] | 4th Floor | Storage | 6.5 | 5 | 3.5 | 32.5
[6 empty] | 4th Floor | Break Room | 4.5 | 7 | 3.5 | 31.5
[6 empty] | 4th Floor | Toilet/Shower/Locker(M) | 6 | 8.6 | 3.5 | 51.6
[6 empty] | 4th Floor | Toilet(F) | 3 | 5.6 | 3.5 | 16.8
[6 empty] | 4th Floor | Corridor | 2.5 | 38 | 3.5 | 145
[6 empty] | 4th Floor | Duct Shaft | 2.4 | 9 | 3.5 | 21.6
[6 empty] | 4th Floor | Elevator | 4 | 3 | 3.5 | 12
[6 empty] | 4th Floor | Staircase | 4 | 6 | 3.5 | 24
4 | 13 | Water Treatment Building | RC | 1 | 2 | - |  | 19 | 41 | 6.0 /4.5 | 779 | 1007 | 5700 |  |  |  |  | *환경(11/12 메일) : 열병합추가로 Size증가 '* Plot Plan Seq.11 반영
[6 empty] | Ground Floor |  | 19 | 41 | 6 | 779 | 779 | 4674
[6 empty] | Ground Floor | Equipment Room | 19 | 41 | 6 | 707 |  |  | Hoist 2 ton |  |  |  | 기계(200707)Hoist 3 ton , Eye Washer
[6 empty] | Ground Floor | Chemical Storage | 6 | 9 | 6 | 54
[6 empty] | Ground Floor | Stair | 3 | 6 | 6 | 18
[6 empty] | 2nd Floor |  | 19 | 12 | 4.5 | 228 | 228 | 1026 |  |  |  |  | * Plot Plan Rev.A 반영(07/10)
[6 empty] | 2nd Floor | MCC Room | 10 | 12 | 4.5 | 120
[6 empty] | 2nd Floor | Control Room | 6 | 9 | 4.5 | 54
[6 empty] | 2nd Floor | Fire Gas Room | 3 | 2 | 4.5 | 6 | [6 empty] | 소방) 07/15 메일 회신
[6 empty] | 2nd Floor | Toilet | 3 | 4 | 4.5 | 12
[6 empty] | 2nd Floor | Stair | 3 | 6 | 4.5 | 18
[6 empty] | 2nd Floor | Corridor | 3 | 6 | 4.5 | 18
5 | 36 | Compressor Air Package Building | RC | 1 | 1 | - |  | 9.4 | 11 | 7.3 | 103.4 | 103.4 | 754.82 |  |  |  |  | * 기계(11/11 Plot Plan회의) : Building으로 재변경 7x13.5 => 9.4x11
[6 empty] | Ground Floor | Air Compressor Room | 9.4 | 11 | 7.3 | 103.4
7 |  | Gate House - Option | RC |  | 1 | - |  | 6 | 6 | 3.5 | 36 | 0 | 126 |  |  |  |  | * 괌 기준 동일 적용
|  | (현대차 협의에 따라 삭제 될수 있음) |  |  |  | Ground Floor |  | 6 | 6 | 3.5 | 36
[6 empty] | Ground Floor | Guard Room | 6 | 3 | 3.5 | 18
[6 empty] | Ground Floor | Toilet | 3 | 3 | 3.5 | 9
[6 empty] | Ground Floor | Rest Room | 3 | 3 | 3.5 | 9
BUILDING TOTAL |  |  |  | 5 | [6 empty] | 3658.86 | 6783.96 | 46100.041
S-1 | 11 | Chemical Dosing Shelter for Cooling Tower | ST | 1 | 1 | - |  | 5 | 8 | 4 | 40 | 40 | 160 |  |  |  |  | * 환경) 사이즈 축소(12/29-email)
[6 empty] | Ground Floor | Shelter Area | 5 | 8 | 4 | 40 | [6 empty] | * 환경) shelter 적용(7/14-IOM)
S-2 | 26 | Chemical Dosing Shelter for HRSG (HRSG Building에서 분리) | ST | 1 | 1 | - |  | 4.3 | 7.6 | 4 | 32.68 | 32.68 | 130.72 |  |  |  |  | * 배관) IOM회신(7/15) Size 반영 * 환경) Size 재검토 요망 : IOM 5x8
[6 empty] | Ground Floor | Shelter Area | 4.3 | 7.6 | 4 | 32.68
S-3 | 23 | UREA Storage & Unloading Shelter | ST | 1 | 1 | - |  | 11 | 12 | 8 | 132 | 132 | 1056 |  |  |  |  | * 환경(11/11 Plot Plan회의) : Ammonia=>UREA * 괌 13m x 21m
[6 empty] | Ground Floor | Shelter Area | 11 | 12 | 8 | 132 | [6 empty] | * 환경) (06/24) e-mail : 9 x 9
S-4 | 19 | Service Gas Storage Shelter (N2) | ST | 1 | 1 | - |  | 4 | 11 | 4 | 44 | 44 | 176 |  |  |  |  | * 사이즈 증가 (Plot plan Seq.12 반영, 1/8) * Building 적용여부 기계팀 검토중(1/8)
[6 empty] | Ground Floor | Shelter Area | 4 | 11 | 4 | 44
S-5 | 37 | Chemical Storage Tank Shelter | ST | 1 | 1 | - |  | 6.6 | 5.4 | 5 | 35.64 | 35.64 | 178.2 |  |  |  |  | '* 건축(11/11) : Building 항목에서 분리 * 환경) IOM회신(11/20) : 사이즈 축소, Deviation 예정사항
[6 empty] | Ground Floor | Chemical Tank Area | 6.6 | 5.4 | 5 | 35.64
SHELTER TOTAL |  |  |  | 5 | [6 empty] | 284.32 | 284.32 | 1700.92
TOTAL |  |  |  | 10 | [6 empty] | 3943.18 | 7068.28 | 47800.961
※ Note : | 1. The dimension of each building specified above are indicative only, and shall be subject to change according to the detail design of project implementation stage. 2. OHC : Overhead Crane, H : Hoist, ELEV : Elevator