## BOQ_R8
7.4.3 BOQ
B. BOQ (Construction)
[P-현대차CCPP] 현대자동차 울산공장 복합화력 발전소, Rev. No : 8 ]
Discipline : Architecture | [38 empty] | 2022-03-30
NO. | Work Master Code | WBS Name | Brief Spec. | Reference to | Group | Group | Group | Group | Group | Group | Sequence | Sequence | Sequence | Sequence | Sequence | Sequence | Sequence | Sequence | Sequence | Sequence | BOQ | BOQ | BOQ | BOQ | Unit | Total (Q'ty) Rev.7
[5 empty] | L01 | L01 | L02 | L02 | L03 | L03 | L04 | L04 | L04 | L04 | L05 | L05 | L06 | L06 | L07 | L07 | B01 | B02 | B03 | B04
[5 empty] | Code | Work Category | Code | Work Category | Code | Work Category | Code | Spec01 | Code | Spec01 | Code | Spec01 | Code | Spec01 | Code | Spec01 | BOQ_Spec | BOQ_Spec | BOQ_Spec | BOQ_Spec |  |  | Gas Turbine Building | Gas Turbine Foundation Unit1 | Gas Turbine Foundation Unit2 | Steam Turbine Building | Steam Turbine Foundation | Control & Electrical and Administration Building | Compressor Air Package Building | Water Treatment Building | Chemical Dosing Shelter for Cooling Tower | Chemical Dosing Shelter for HRSG | UREA Storage & Unloading Shelter | N2 Gas Storage Shelter | Chemical Storage Shelter
1 |  | EARTH WORKS | [37 empty] | 24.56%
1) | A01ZZ001-00004 | EXCAVATION | COMMON SOIL | B-01 | A01 | Earth Work | ZZ |  | 001 | Excavation | 02 | Soil, Mech. | 04 | D < 2.0M | [10 empty] | M3 | 3443.96 | 771.27 |  |  | 655.7 | 417.01 | 995.47 |  | 410.18 | 44.16 | 32.85 |  | 45.42 | 71.9 | 0.3008%
2) | A01ZZ001-00005 | EXCAVATION | BELOW 2M DEPTH | B-01 | A01 | Earth Work | ZZ |  | 001 | Excavation | 02 | Soil, Mech. | 03 | D ≥ 2.0M | [10 empty] | M3 | 1176 | 430.59 | 267.3 | 267.3 | 156.87 |  | 28.6 |  | 25.34 | [5 empty] | 0.1027%
3) | A01ZZ003-00001 | BACKFILL (GENERAL FILL) | SELECTED EXCAVATED SOIL | B-02 | A01 | Earth Work | ZZ |  | 003 | Backfill | 06 | Re-use, Soil | [8 empty] | Compaction=( 95 )% |  |  |  | M3 | 721.05 | 309.25 | 9.92 | 9.92 | 182.52 | 36.18 | 72.48 |  | 59.34 | 9.06 | 6.21 |  | 8.18 | 17.99 | 0.1111%
4) | A01ZZ004-00001 | DISPOSAL | 부지내부사토 | B-04 | A01 | Earth Work | ZZ |  | 004 | Disposal | 09 | Soil | [8 empty] | Disposal Distance=Appx. (1)km from Site |  |  |  | M3 | 4575.74 | 1071.14 | 257.38 | 257.38 | 756.06 | 456.99 | 1141.91 |  | 451.41 | 42.12 | 31.97 |  | 44.69 | 64.69 | 0.7052%
5) | A01ZZ012-00001 | PE SHEET (VAPOR BARRIER) | THK. 0.15mm, 2 LAYERS | H-17 | A01 | Earth Work | ZZ |  | 012 | PE Sheet (Vapor Barrier) | [10 empty] | THK=(0.15)mm |  |  |  | M2 | 8489.87 | 2153.6 | 166.32 | 166.32 | 1881.45 | 206.48 | 2205.98 |  | 1379.52 | 88.48 | 62.92 |  | 93.44 | 85.36 | 0.2181%
6) | A02AA018-00004 | PHC PILE (D400) | INCLUDING PRE-BORING | Q-02 | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 14 | Soil Cement Injected Precast(S.I.P) Pile Method | 03 | Including Pile Connection and Joint Welding Work | [6 empty] | DIA=( 400 )mm, Pile Length per Hole=( 40 )M |  |  |  | M | 840 | [8 empty] | 200 | 200 |  | 200 | 240 | 0.7231%
7) | A02AA018-00007 | Pile Head Cutting |  | Q-02 | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 17 | Pile Head Cutting & Reinforcement | [8 empty] | DIA=( 400 )mm |  |  |  | EA | 21 | [8 empty] | 5 | 5 |  | 5 | 6 | 0%
8) | A02AA018-00004 | PHC PILE (D500) | INCLUDING PRE-BORING | Q-03 | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 14 | Soil Cement Injected Precast(S.I.P) Pile Method | 03 | Including Pile Connection and Joint Welding Work | [6 empty] | DIA=( 500 )mm, Pile Length per Hole=( 40 )M |  |  |  | M | 16560 | 3960 |  |  | 4840 |  | 5000 |  | 2760 | [5 empty] | 15.77%
9) | A02AA018-00007 | Pile Head Cutting |  | Q-03 | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 17 | Pile Head Cutting & Reinforcement | [8 empty] | DIA=( 500 )mm |  |  |  | EA | 414 | 99 |  |  | 121 |  | 125 |  | 69 | [5 empty] | 0%
10) | A02AA018-00004 | PHC PILE (D600) | INCLUDING PRE-BORING | Q-04 | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 14 | Soil Cement Injected Precast(S.I.P) Pile Method | 03 | Including Pile Connection and Joint Welding Work | [6 empty] | DIA=( 600 )mm, Pile Length per Hole=( 40 )M |  |  |  | M | 5360 |  | 1600 | 1600 |  | 2160 | [8 empty] | 6.626%
11) | A02AA018-00007 | Pile Head Cutting |  | Q-04 | A02 | Pile Work | AA | Piling Work | 018 | Pretensioned High-strength Concrete Pile (Type-A) | 17 | Pile Head Cutting & Reinforcement | [8 empty] | DIA=( 600 )mm |  |  |  | EA | 134 |  | 40 | 40 |  | 54 | [8 empty] | 0%
0%
2 |  | CONCRETE WORKS | [37 empty] | 36.26%
1) | A03AC034-00004 | LEAN CONCRETE | [UG] F'C = 18 MPA, W/CONSTRUCTION JOINT | C-01 | A03 | Concrete Work | AC | Substructure Work | 034 | Lean Concrete (including Form work) | 01 | Cement Type-1 | 07 | 10MPa < F'c (Cylinder Strength) ≤ 20MPa | [10 empty] | M3 | 718.51 | 212.37 | 16.63 | 16.63 | 194.87 | 20.65 | 126.22 |  | 104.9 | 5.7 | 4.84 |  | 7.16 | 8.54 | 0.7242%
2) | A03AD032-00010 | CONCRETE | [AG] F'C = 24 MPA, W/CONSTRUCTION JOINT | C-05 | A03 | Concrete Work | AD | Superstructure Work | 032 | Structural Concrete | 01 | Cement Type-1 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [10 empty] | M3 | 3141.54 | 264.27 |  |  | 90.37 |  | 2007.15 |  | 755.52 | 7.06 | 5.31 |  | 0.75 | 11.11 | 3.434%
3) | A03AC032-00010 | CONCRETE | [UG] F'C = 24 MPA, W/CONSTRUCTION JOINT | C-06 | A03 | Concrete Work | AC | Substructure Work | 032 | Structural Concrete | 01 | Cement Type-1 | 04 | 20MPa < F'c (Cylinder Strength) ≤ 25MPa | [10 empty] | M3 | 2641.06 | 759.81 |  |  | 706.77 |  | 796.69 |  | 219.14 | 40.2 | 30.92 |  | 42.15 | 45.38 | 2.887%
4) | A03AD032-00007 | CONCRETE (FOR MAJOR EQUIPMENT FDN) | [AG] F'C = 30 MPA, W/CONSTRUCTION JOINT (for TG) | C-07 | A03 | Concrete Work | AD | Superstructure Work | 032 | Structural Concrete | 01 | Cement Type-1 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [10 empty] | M3 | 286.34 |  |  |  |  | 286.34 | [8 empty] | 0.3407%
5) | A03AC032-00007 | CONCRETE (FOR MAJOR EQUIPMENT FDN) | [UG] F'C = 30 MPA, W/CONSTRUCTION JOINT (for TG, HRSG) | C-08 | A03 | Concrete Work | AC | Substructure Work | 032 | Structural Concrete | 01 | Cement Type-1 | 03 | 25MPa < F'c (Cylinder Strength) ≤ 30MPa | [10 empty] | M3 | 1157.58 |  | 398.7 | 398.7 |  | 360.18 | [8 empty] | 1.377%
6) | A03AG052-00001 | TEMPERATURE CONTROL MONITORING | FOR MASS CONCRETE | C-09 | A03 | Concrete Work | AG | Mass Concrete Work | 052 | Concrete Temperature Monitoring | 16 | Including Themo Coupler, Monitoring & Record Acc. To Approved MS | [12 empty] | L/S | 3 |  | 1 | 1 |  | 1 | [8 empty] | 0.03082%
7) | A03AD036-00001 | FORM WORKS(Fair faced form) | 1 TIMES, FAIR FACE FOR ABOVE GROUND | C-12 | A03 | Concrete Work | AD | Superstructure Work | 036 | Form Work (1 time in use) | 25 | Flat Form | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [10 empty] | M2 | 17764.92 | 404.32 |  |  | 300.09 |  | 12637.71 |  | 4372.72 | 18.6 | 15.12 |  | 2.6 | 13.76 | 10.95%
8) | A03AC035-00001 | FORM WORKS(Normal faced form) | 3 TIMES, GENERAL FOR UNDERGROUND | C-13 | A03 | Concrete Work | AC | Substructure Work | 035 | Form Work (3 times in use) | 25 | Flat Form | 05 | Dressed Lumber, Plywood or Steel Form(Wood Planks are not Allowed) incl. Chamfer | [10 empty] | M2 | 2409.7 | 965.72 |  |  | 569.56 |  | 386.58 |  | 337.68 | 33.6 | 23.82 |  | 31.2 | 61.54 | 1.485%
9) | A03AG054-00001 | SYSTEM FORM | FOR STEAM TURBINE GENERATOR FOUNATION TOP TABLE | C-14 | A03 | Concrete Work | AG | Mass Concrete Work | 054 | System Form | 36 | Heavy Duty Forms, Metal Framed Playwood forms | 18 | Including Form Tie, All Accessories, Sealing of Form Tie Hole, Separator & Anchor Box out, Chamfer for Exposed Edge, Opening & Sleeve, Shoring, Scaffording, Safety Measures and Shop Drawing | [10 empty] | M2 | 971.19 |  | 259.15 | 259.15 |  | 452.89 | [8 empty] | 0.898%
10) | A03AD037-00002 | REINFORCEMENT | HIGH YIELD DEFORMED BAR WORK (BLACK DEFORMED BARS) | C-11 | A03 | Concrete Work | AD | Superstructure Work | 037 | Rebar Work | 27 | Deformed Bar (Non-Coat.) | 10 | 400MPa<Fy≤470MPa | [10 empty] | TON | 908.14 | 112.31 | 45.7 | 45.7 | 88.05 | 75.05 | 389.09 |  | 133.05 | 5.03 | 3.89 |  | 4.64 | 5.63 | 12.5%
11) | A03AD044-00001 | ISOLATION JOINT (SEPARATION JOINT) | FOR SLAB+TIE GIRDER, | O-04 | A03 | Concrete Work | AD | Superstructure Work | 044 | Isolation Joint (Separation Joint) | 11 | w/ Flexible Joint Filler, Sealant | [8 empty] | THK=(12)mm |  |  |  | M | 306 | 156 |  |  | 85.4 |  |  |  | 64.6 | [5 empty] | 0.05345%
12) | A03AC044-00001 | ISOLATION JOINT (SEPARATION JOINT) | FOR EQUIPMENT FOUNDATION | O-01 | A03 | Concrete Work | AC | Substructure Work | 044 | Isolation Joint (Separation Joint) | 11 | w/ Flexible Joint Filler, Sealant | [8 empty] | THK=(50)mm |  |  |  | M | 179.4 | 116 |  |  | 63.4 | [9 empty] | 0.03133%
13) | A03AD045-00001 | CONTROL JOINT |  |  | A03 | Concrete Work | AD | Superstructure Work | 045 | Control Joint | 12 | w/ Joint Sealant, Backstop | [8 empty] | Saw Cut: W( 10 )mm x D( 15 )mm |  |  |  | M | 1276.2 | 571 |  |  | 228 |  | 382.8 |  | 94.4 | [5 empty] | 0.2229%
14) | A03AE056-00001 | BITUMINOUS COATING | FOR UNDERGROUND CONCRETE PROTECTION | H-11 | A03 | Concrete Work | AE | Concrete Protective Coating (U/G) | 056 | Bitumen/Bituminous/Asphalt Coating | [14 empty] | M2 | 7800.64 | 2168.62 | 247.2 | 247.2 | 1804.89 | 145.82 | 1473.99 |  | 1347.5 | 95.2 | 56.56 |  | 85.5 | 128.16 | 1.282%
15) | A03AC046-00001 | WATER STOP | PVC WATERSTOP | H-12 | A03 | Concrete Work | AC | Substructure Work | 046 | Water Stop | 29 | PVC Type | [8 empty] | W=( 150 )mm |  |  |  | M | 338.6 | 156 |  |  | 100.6 |  | 8 |  | 74 | [5 empty] | 0.01739%
16) | A03AJ068-00001 | PRECAST CONCRETE (THK.250) | FOR MISC PART SUCH AS PIT COVER, EQUIPEMENT PAD, ETC | C-20 | A03 | Concrete Work | AJ | Precast Concrete Work | 068 | PC Cover | 20 | Including Supply and Install Work w/ All Items to Complete the Work | [8 empty] | W( )mm x L( )mm x THK( 250 )mm |  |  |  | M2 | 160 | 160 | [12 empty] | 0.02466%
0%
3 |  | BLOCK WORKS | [37 empty] | 5.647%
1) | A04AK073-00001 | BRICK(T=115) | [0.5B] CEMENT BRICK W/LINTEL FOR OPENING | E-02 | A04 | Finishing Work | AK | Masonry Work | 073 | Concrete Brick | 22 | [0.5B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 22 | THK≤90mm | [6 empty] | THK=( 115 )mm |  |  |  | M2 | 3180.3 | 144 |  |  | 133.2 |  | 1862.4 |  | 1040.7 | [5 empty] | 1.824%
2) | A04AK073-00002 | BRICK(T=230) | [1.0B] CEMENT BRICK W/LINTEL FOR OPENING | E-03 | A04 | Finishing Work | AK | Masonry Work | 073 | Concrete Brick | 23 | [1.0B] w/ All Reinf.(Lath, Steel Tie, Anchor Bar, Mortar, ETC.), Filler, Sealant, Lintel/Sill for Opening, ETC. | 23 | 90mm<THK≤190mm | [6 empty] | THK=( 230 )mm |  |  |  | M2 | 3351.5 | [5 empty] | 2046.5 |  | 1305 | [5 empty] | 3.299%
3) | A04AK076-00003 | INSULATION | ONLY FOR BRICK WALL INSULATION(THK.100) | E-01 | A04 | Finishing Work | AK | Masonry Work | 076 | Insulation | 43 | Mineral Wool | 26 | Minimum Density of 50 kg/m3 | 11 | 100mm≤THK |  |  |  |  | THK=( 100 )mm |  |  |  | M2 | 4407.7 | 144 |  |  | 133.2 |  | 3162.5 |  | 968 | [5 empty] | 0.4127%
4 |  | PAINTING WORKS | [37 empty] | 1%
1) | A04AL077-00001 | ACRYLIC EMULSION PAINT (AEP) | EXTERNAL WALL | G-03 | A04 | Finishing Work | AL | Painting Work | 077 | External Wall Painting | 45 | Acrylic Emulsion Paint | [12 empty] | M2 | 4654.6 | 144 |  |  | 133.2 |  | 3378.4 |  | 999 | [5 empty] | 0.1913%
2) | A04AL080-00006 | EPOXY PAINT | FLOOR | G-07 | A04 | Finishing Work | AL | Painting Work | 079 | Ceiling Painting | 50 | Epoxy Paint | [12 empty] | M2 | 3784.26 | 1180.96 |  |  | 1160 |  | 1273.3 |  | 126 |  |  |  | 44 |  | 0.2644%
3) | A04AL081-00007 | EPOXY PAINT | SKIRT, H=100MM | G-11 | A04 | Finishing Work | AL | Painting Work | 081 | Skirt Painting | 50 | Epoxy Paint | 66 | 100mm≤H<150mm | [6 empty] | H=( 100 )mm |  |  |  | M | 709.4 | 194.4 |  |  | 134 |  | 327 |  | 54 | [5 empty] | 0.02041%
4) | A04AL080-00003 | ACID RESISTANT PAINT | FLOOR | G-12 | A04 | Finishing Work | AL | Painting Work | 080 | Floor Painting | 52 | Acid/Alkaline Resistant Paint | [12 empty] | M2 | 55 | [5 empty] | 55 | [7 empty] | 0.009041%
5) | A04AL078-00004 | ACID RESISTANT PAINT | INTERNAL WALL | G-13 | A04 | Finishing Work | AL | Painting Work | 078 | Internal Wall Painting | 52 | Acid/Alkaline Resistant Paint | [12 empty] | M2 | 102.7 | [5 empty] | 102.7 | [7 empty] | 0.002954%
6) | A04AL079-00004 | ACID RESISTANT PAINT | CEILING | G-13 | A04 | Finishing Work | AL | Painting Work | 079 | Ceiling Painting | 52 | Acid/Alkaline Resistant Paint | [12 empty] | M2 | 55 | [5 empty] | 55 | [7 empty] | 0.003843%
7) | A04AL081-00004 | ACID RESISTANT PAINT | SKIRT, H=100MM |  | A04 | Finishing Work | AL | Painting Work | 081 | Skirt Painting | 52 | Acid/Alkaline Resistant Paint | 66 | 100mm≤H<150mm | [6 empty] | H=( 100 )mm |  |  |  | M | 28.6 | [5 empty] | 28.6 | [7 empty] | 0.0008228%
8) | A04AL080-00003 | CHEMICAL RESISTANT PAINT | FLOOR | G-14 | A04 | Finishing Work | AL | Painting Work | 080 | Floor Painting | 52 | Acid/Alkaline Resistant Paint | [12 empty] | M2 | 941.32 | [7 empty] | 833 | 40 | 32.68 |  |  | 35.64 | 0.06577%
9) | A04AL078-00004 | CHEMICAL RESISTANT PAINT | INTERNAL WALL | G-15 | A04 | Finishing Work | AL | Painting Work | 078 | Internal Wall Painting | 52 | Acid/Alkaline Resistant Paint | [12 empty] | M2 | 1767.54 | [7 empty] | 1691.1 | 24 | 19.44 |  |  | 33 | 0.1235%
10) | A04AL078-00002 | WATER EMULSION PAINT | INTERNAL WALL |  | A04 | Finishing Work | AL | Painting Work | 078 | Internal Wall Painting | 47 | Water Emulsion Paint | [12 empty] | M2 | 5602.6 | 144 |  |  | 337.8 |  | 4516 |  | 604.8 | [5 empty] | 0.2303%
11) | A04AL079-00002 | WATER EMULSION PAINT | CEILING |  | A04 | Finishing Work | AL | Painting Work | 079 | Ceiling Painting | 47 | Water Emulsion Paint | [12 empty] | M2 | 1846.8 | [5 empty] | 1684.8 |  | 162
12) | A04AL080-00005 | ANTI-DUST PAINT | FLOOR | G-08 | A04 | Finishing Work | AL | Painting Work | 080 | Floor Painting | 53 | Anti-Dust Paint | [12 empty] | M2 | 662.5 | [5 empty] | 608.5 |  | 54 | [5 empty] | 0.0759%
0.01225%
5 |  | TILE WORKS | [37 empty] | 0%
1) | A04AM082-00002 | GLAZED CERAMIC TILE | WALL W/ BEDDING, WIREMESH IF NECESSARY | I-13 | A04 | Finishing Work | AM | Tile Work | 082 | Wall Tile | 60 | Glazed Ceramic Tile | 27 | w/ Mortar Bond Coat or Adhesive | [6 empty] | Tile Size=W( )mm x L( )mm x THK( 6 )mm |  |  |  | M2 | 435.3 | [5 empty] | 393.3 |  | 42 | [5 empty] | 1.023%
2) | A04AM083-00001 | NON-SLIP CERAMIC TILE | FLOOR W/ BEDDING, WIREMESH IF NECESSARY | I-12 | A04 | Finishing Work | AM | Tile Work | 083 | Floor Tile | 68 | Ceramic Tile | 29 | Non-Slip Type, w/ Mortar Bond Coat or Adhesive | [6 empty] | Tile Size=W( )mm x L( )mm x THK( 10 )mm |  |  |  | M2 | 423.5 | [5 empty] | 375.5 |  | 48 | [5 empty] | 0.3176%
3) | A04AM084-00004 | NON-SLIP CERAMIC TILE | SKIRTS, H= MM. W/ BEDDING, WIREMESH IF NECESSARY |  | A04 | Finishing Work | AM | Tile Work | 084 | Skirt Tile | 60 | Glazed Ceramic Tile | 27 | w/ Mortar Bond Coat or Adhesive | 66 | 100mm≤H<150mm |  |  |  |  | H=( 100 )mm |  |  |  | M | 263 | [5 empty] | 229 |  | 34 | [5 empty] | 0.309%
4) | A04AM083-00004 | HEAVY DUTY PVC TILE | FLOOR W/ BEDDING, WIREMESH IF NECESSARY | I-06 | A04 | Finishing Work | AM | Tile Work | 083 | Floor Tile | 70 | Vinyl Tile | 27 | w/ Mortar Bond Coat or Adhesive | [6 empty] | Tile Size=W( )mm x L( )mm x THK( 3 )mm |  |  |  | M2 | 921.2 | [5 empty] | 903.2 |  | 18 | [5 empty] | 0.05539%
5) | A04AM084-00013 | HEAVY DUTY PVC TILE | SKIRTS W/ BEDDING, WIREMESH IF NECESSARY | I-07 | A04 | Finishing Work | AM | Tile Work | 084 | Skirt Tile | 70 | Vinyl Tile | 27 | w/ Mortar Bond Coat or Adhesive | 66 | 100mm≤H<150mm |  |  |  |  | H=( 100 )mm |  |  |  | M | 518.6 | [5 empty] | 500.6 |  | 18 | [5 empty] | 0.2319%
6) |  | DAMP-PROOF COURSE | For masonry work | E-20 | [20 empty] | M2 | 391 | [5 empty] | 300 |  | 91 | [5 empty] | 0.1092%
0%
6 |  | WATERPROOFING WORKS | [37 empty] | 0.2225%
1) | A04AN085-00001 | LIQUID WATERPROOFING | INTERNAL FLOOR AREA | H-06 | A04 | Finishing Work | AN | Waterproofing Work | 085 | Liquid Waterproofing | 02 | for Internal Floor Area | 30 | Min. 2 Coats | [10 empty] | M2 | 153.5 | [5 empty] | 141.5 |  | 12 | [5 empty] | 0.0606%
2) | A04AN085-00002 | LIQUID WATERPROOFING | INTERNAL WALL AREA | H-06 | A04 | Finishing Work | AN | Waterproofing Work | 085 | Liquid Waterproofing | 03 | for Internal Wall Area | 30 | Min. 2 Coats | [10 empty] | M2 | 410.1 | [5 empty] | 393.3 |  | 16.8 | [5 empty] | 0.1619%
0%
7 |  | ROOF WORKS | [37 empty] | 1.818%
1) | A04AP086-00003 | LIGHT-WEIGHT CONCRETE SCREED | W/ TROWELING, WITHOUT WIREMESH (for SLOPE,1/100) | H-08 | A04 | Finishing Work | AP | Roof Work | 086 | Roof Screed | 75 | Light-Weight Concrete Screed | 31 | w/o Welded Wire Fabric | 27 | 75mm≤THK |  |  |  |  | THK=( 40 )mm, Min. |  |  |  | M3 | 162.86 | [5 empty] | 84.96 |  | 77.9 | [5 empty] | 0.178%
2) | A04AP089-00001 | PROTECTIVE CONCRETE | W/ TROWELING, Min.60mm |  | A04 | Finishing Work | AP | Roof Work | 089 | Protective Concrete w/ Steel Trowel Finish | [14 empty] | M3 | 177.17 | 73.79 |  |  |  |  | 56.64 |  | 46.74
3) | A04AP000-00001 | WATERPROOFING MEMBRANE | FOR ROOF AREA ONLY | H-02 | A04 | Finishing Work | AP | Roof Work | 000 | Waterproofing Membrane | 77 | EPDM(or Equivalent) | 32 | w/ Accessories | [6 empty] | THK=( 4 )mm |  |  |  | M2 | 3222.44 | 1301.76 |  |  |  |  | 1044 |  | 876.68 | [5 empty] | 0.03641%
4) | A04AP088-00003 | RIGID INSULATION FOR ROOF | THK. 200mm Rigid Extruded Polystyrene Insulation | H-01 | A04 | Finishing Work | AP | Roof Work | 088 | Roof Insulation | 81 | Rigid Extruded Polystyrene Foam Insulation | 11 | 100mm≤THK | [6 empty] | THK=( 200 )mm |  |  |  | M2 | 2952.76 | 1229.76 |  |  |  |  | 944 |  | 779 | [5 empty] | 1.175%
5) | A04AP012-00001 | PE SHEET (VAPOR BARRIER) |  | H-17 | A04 | Finishing Work | AP | Roof Work | 012 | PE Sheet (Vapor Barrier) | [10 empty] | THK=( 0.15 )mm |  |  |  | M2 | 2952.76 | 1229.76 |  |  |  |  | 944 |  | 779 | [5 empty] | 0.3671%
6) | A04AP038-00001 | WIRE MESH | ONLY FOR WIRE MESH |  | A04 | Finishing Work | AP | Roof Work | 038 | Welded Wire Fabric | 53 | DIA≤6mm | [8 empty] | Mesh Size=DIA( 6 )mm x ( )mm x ( )mm |  |  |  | M2 | 2952.76 | 1229.76 |  |  |  |  | 944 |  | 779 | [5 empty] | 0%
0.06068%
8 |  | DOOR & WINDOW WORKS | [37 empty] | 0%
1) | A04AQ098-00002 | NORMAL STEEL DOOR (1.0 x2.1) | SINGLE DOOR W/HARDWARE | L-03 | A04 | Finishing Work | AQ | Door & Window Work | 098 | Steel Door w/ Steel Frame | 90 | Fire Protective Rating: N/A, Single Door | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(1000)mm x (2100)mm |  |  |  | EA | 35 | 4 |  |  | 2 |  | 21 |  | 8 | [5 empty] | 2.01%
2) | A04AQ098-00003 | NORMAL STEEL DOOR (2.0x 2.1) | DOUBLE DOOR W/HARDWARE | L-03 | A04 | Finishing Work | AQ | Door & Window Work | 098 | Steel Door w/ Steel Frame | 91 | Fire Protective Rating: N/A, Double Door | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(2000)mm x (2100)mm |  |  |  | EA | 8 | 1 |  |  | 1 |  | 4 |  | 2 | [5 empty] | 0.3068%
3) | A04AQ099-00003 | NORMAL STEEL DOOR (2.4 x 3.0) | DOUBLE DOOR W/HARDWARE | L-03 | A04 | Finishing Work | AQ | Door & Window Work | 099 | Steel Door w/ Steel Frame & Vision Panel for Each Leaf | 91 | Fire Protective Rating: N/A, Double Door | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(2400)mm x (3000)mm |  |  |  | EA | 4 | [5 empty] | 2 |  | 2 | [5 empty] | 0.1236%
4) | A04AQ101-00011 | FIRE RESIST. STEEL DOOR W/90 MIN (1.0 x2.1) | SINGLE DOOR W/HARDWARE | L-02 | A04 | Finishing Work | AQ | Door & Window Work | 101 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf | AD | Fire Protective Rating: 1.5-hrs, Single Door | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(1000)mm x (2100)mm |  |  |  | EA | 32 | [5 empty] | 32 | [7 empty] | 0.09918%
5) | A04AQ101-00012 | FIRE RESIST. STEEL DOOR W/90 MIN (2.0x 2.1) | DOUBLE DOOR W/HARDWARE | L-02 | A04 | Finishing Work | AQ | Door & Window Work | 101 | Steel Door w/ Steel Frame, Panic Bar & Vision Panel for Each Leaf | AE | Fire Protective Rating: 1.5-hrs, Double Door | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(2000)mm x (2100)mm |  |  |  | EA | 17 | [5 empty] | 17 | [7 empty] | 0.3529%
6) | A04AQ112-00010 | SHUTTER (6.0 x 6.0) | W/HARDWARE | L-04 | A04 | Finishing Work | AQ | Door & Window Work | 112 | Steel Roll Up Door w/ Steel Frame | AQ | Fire Protective Rating: 1-hr, Motorized Type | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(6000)mm x (6000)mm |  |  |  | EA | 1 |  |  |  | 1 | [9 empty] | 0.3394%
7) | A04AQ112-00002 | SHUTTER (4.0 x 5.0) | W/HARDWARE | L-04 | A04 | Finishing Work | AQ | Door & Window Work | 112 | Steel Roll Up Door w/ Steel Frame | AL | Fire Protective Rating: N/A, Motorized Type | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(4000)mm x (5000)mm |  |  |  | EA | 3 | 2 | [6 empty] | 1 | [5 empty] | 0.113%
8) | A04AQ127-00002 | ALUMINUM WINDOW (1.2 x 1.2) | DOUBLE GLASS / W/HARDWARE | M-01 | A04 | Finishing Work | AQ | Door & Window Work | 127 | Aluminum Window | 89 | Fire Protective Rating: N/A | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(1200)mm x (1200)mm |  |  |  | EA | 5 | [5 empty] | 5 | [7 empty] | 0.3021%
9) | A04AQ127-00002 | ALUMINUM WINDOW (1.8 x 1.2) | W/HARDWARE | M-01 | A04 | Finishing Work | AQ | Door & Window Work | 127 | Aluminum Window | 89 | Fire Protective Rating: N/A | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(1800)mm x (1200)mm |  |  |  | EA | 50 | [5 empty] | 30 |  | 20 | [5 empty] | 0.009761%
10) | A04AQ127-00002 | ALUMINUM WINDOW (3.6 x 1.2) | W/HARDWARE | M-01 | A04 | Finishing Work | AQ | Door & Window Work | 127 | Aluminum Window | 89 | Fire Protective Rating: N/A | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(3600)mm x (1200)mm |  |  |  | EA | 36 | 10 |  |  | 16 |  | 10 | [7 empty] | 0.1043%
11) | A04AQ130-00002 | ALUMINUM LOUVER | 1400x1000 | M-07 | A04 | Finishing Work | AQ | Door & Window Work | 130 | Louver | BJ | Aluminum | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(1400)mm x (1000)mm |  |  |  | EA | 37 | 15 |  |  | 22 | [9 empty] | 0.1605%
12) | A04AQ130-00002 | ALUMINUM LOUVER | 900x600 | M-07 | A04 | Finishing Work | AQ | Door & Window Work | 130 | Louver | BJ | Aluminum | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(900)mm x (600)mm |  |  |  | EA | 10 | [5 empty] | 6 |  | 4 | [5 empty] | 0.06158%
13) | A04AQ130-00002 | ALUMINUM LOUVER | 600x400 | M-07 | A04 | Finishing Work | AQ | Door & Window Work | 130 | Louver | BJ | Aluminum | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(600)mm x (400)mm |  |  |  | EA | 3 | [5 empty] | 2 |  | 1 | [5 empty] | 0.01664%
14) | A04AQ130-00002 | ALUMINUM LOUVER | 400x300 | M-07 | A04 | Finishing Work | AQ | Door & Window Work | 130 | Louver | BJ | Aluminum | 36 | w/ Hardware & Accessories | [6 empty] | W x H=(400)mm x (300)mm |  |  |  | EA | 8 | [5 empty] | 7 |  | 1 | [5 empty] | 0.004993%
15) | A04AQ125-00001 | MASTER KEY SYSTEM |  | L-11 | A04 | Finishing Work | AQ | Door & Window Work | 125 | Master Key System | BD | Three Levels Master Key | 37 | w/ Accessories (Key Box, Key Tag and ETC) | [10 empty] | SET | 1 | [5 empty] | 1 | [7 empty] | 0.01332%
0.002055%
9 |  | EXTERIOR/INTERIOR FINISH WORKS | [37 empty] | 0%
1) | A04AR143-00008 | GYPSUM BOARD | WALL (one side) | J-07 | A04 | Finishing Work | AR | Exterior/Interior Finish Work | 143 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides | 01 | Mineral Wool Thk.=50mm | 39 | Including Supporting Frame(Stud) & Accessories | 77 | 1-Layer Gypsumboard THK=12.5mm | [6 empty] | M2 | 0 | [13 empty] | 8.283%
2) | A04AR143-00008 | GYPSUM BOARD | WALL, (both side) | J-06 | A04 | Finishing Work | AR | Exterior/Interior Finish Work | 143 | Gypsumboard Partition Wall (Fixed Type) | BW | Fire Protective Rating: N/A, 1-Layer Gypsum Board to Both Sides | 01 | Mineral Wool Thk.=50mm | 39 | Including Supporting Frame(Stud) & Accessories | 77 | 1-Layer Gypsumboard THK=12.5mm | [6 empty] | M2 | 810 | [5 empty] | 810 | [7 empty] | 0%
3) | A04AR143-00023 | GYPSUM BOARD | WALL, 2HR FIRE-RATING. | J-08 | A04 | Finishing Work | AR | Exterior/Interior Finish Work | 143 | Gypsumboard Partition Wall (Fixed Type) | CC | Fire Protective Rating: 2-hrs, 2-Layer Gypsum Boards to Both Sides | 01 | Mineral Wool Thk.=50mm | 39 | Including Supporting Frame(Stud) & Accessories | 77 | 1-Layer Gypsumboard THK=12.5mm | [6 empty] | M2 | 1364 | [5 empty] | 1364 | [7 empty] | 0.5909%
4) | A04AR156-00002 | SUSPENDED ACOUSTIC CEILING SYSTEM | 600x600xTHK.15mm, NON COMBUSTIBLE | J-01 | A04 | Finishing Work | AR | Exterior/Interior Finish Work | 156 | Acoustic Tiled Ceiling System | CE | T-Bar System | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | [6 empty] | Tile Size=(600 )mm x ( 600 )mm |  |  |  | M2 | 1830.7 | [5 empty] | 1758.7 |  | 72 | [5 empty] | 0.995%
5) | A04AR157-00001 | PVC STRIP CEILING | FOR TOILET & SHOWER ROOM | J-03 | A04 | Finishing Work | AR | Exterior/Interior Finish Work | 157 | Moisture Resistant Tiled Ceiling System | CD | M-Bar System | 43 | w/ Hot-Dip Galvanized Suspension System & Accessories(Moldings, Ceiling Access Door/Hatch, Curtain Boxes and etc.) | [6 empty] | Tile Size=(600 )mm x ( 600 )mm |  |  |  | M2 | 153.5 | [5 empty] | 141.5 |  | 12 | [5 empty] | 0.7899%
6) | A04AS164-00001 | EXTERNAL PLASTER | WALL | F-02 | A04 | Finishing Work | AS | Plastering Work | 164 | Plastering | 12 | for External Masonry Wall | [8 empty] | THK=( 21 )mm |  |  |  | M2 | 2598 | [5 empty] | 1599 |  | 999 | [5 empty] | 0.07412%
7) | A04AS164-00002 | INTERNAL PLASTER | WALL | F-03 | A04 | Finishing Work | AS | Plastering Work | 164 | Plastering | 13 | for Internal Masonry Wall | [8 empty] | THK=( 18 )mm |  |  |  | M2 | 5060 | 144 |  |  | 204.6 |  | 3206.5 |  | 1504.9 | [5 empty] | 0.5872%
8) | A04AR139-00001 | RAISED FLOOR W/ VINYL TILE | 600 x 600 H:600 | I-09 | A04 | Finishing Work | AR | Exterior/Interior Finish Work | 139 | Raised Floor | BQ | Top Finish: Anti-Static Vinyl Tile | 73 | 600mm x 600mm / H≤600mm | [6 empty] | H=( 600 )mm |  |  |  | M2 | 662.5 | [5 empty] | 608.5 |  | 54 | [5 empty] | 1.092%
9) | A05ZZ165-00005 | GALVANIZED STEEL SHEET W/FLASHING IF NECESSORY | Wall | K-05 | A05 | Cladding Work | ZZ |  | 165 | Single Metal Sheet | DA | Corrugated Galvanized Steel Sheet | 08 | for Wall | 47 | w/ Accessories, Flashing |  |  |  |  | THK=( 0.6 )mm |  |  |  | M2 | 103.8 | [8 empty] | 26 | 23.8 |  | 30 | 24 | 0.1668%
10) | A05ZZ165-00006 | GALVANIZED STEEL SHEET W/FLASHING IF NECESSORY | ROOF | K-04 | A05 | Cladding Work | ZZ |  | 165 | Single Metal Sheet | DA | Corrugated Galvanized Steel Sheet | 15 | for Roof | 47 | w/ Accessories, Flashing |  |  |  |  | THK=( 0.6 )mm |  |  |  | M2 | 208.22 | [8 empty] | 54 | 45.58 |  | 60 | 48.64 | 0.03306%
11) | A05ZZ166-00002 | SANDWICH PANEL W/FLASHING IF NECESSORY | WALL | K-02 | A05 | Cladding Work | ZZ |  | 166 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | 03 | Mineral Wool | 08 | for Wall | 47 | w/ Accessories, Flashing | 33 | 70mm≤THK<100mm | THK=( 75 )mm |  |  |  | M2 | 2694.2 | 1402.2 |  |  | 1292 | [9 empty] | 0.06632%
12) | A05ZZ166-00019 | SANDWICH PANEL W/FLASHING IF NECESSORY | WALL, 2HOUR FIRE RATING | K-03 | A05 | Cladding Work | ZZ |  | 166 | Sandwich Panel | DD | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: 2-hrs | 03 | Mineral Wool | 08 | for Wall | 47 | w/ Accessories, Flashing | 34 | 100mm≤THK<150mm | THK=( 100 )mm |  |  |  | M2 | 0 | [13 empty] | 1.702%
13) | A05ZZ166-00007 | SANDWICH PANEL W/FLASHING IF NECESSORY | ROOF | K-01 | A05 | Cladding Work | ZZ |  | 166 | Sandwich Panel | DB | Corrugated Galvanized Steel Sheet Sandwich Panel, Fire Protective Rating: N/A | 03 | Mineral Wool | 15 | for Roof | 47 | w/ Accessories, Flashing | 34 | 100mm≤THK<150mm | THK=( 100 )mm |  |  |  | M2 | 1239 |  |  |  | 1239 | [9 empty] | 0%
14) | A05ZZ170-00001 | GUTTER | EAVE GUTTER. | K-08 | A05 | Cladding Work | ZZ |  | 170 | Gutter | DL | Galvanized Steel Eave Gutter w/ Coating | 32 | w/ Accessories | [6 empty] | THK=( 1.2 )mm |  |  |  | M | 281.4 | 95 |  |  | 118 |  |  |  |  | 16 | 17.2 |  | 22 | 13.2 | 1.057%
15) | A05ZZ170-00002 | GUTTER | VALLEY GUTTER. |  | A05 | Cladding Work | ZZ |  | 170 | Gutter | DM | Galvanized Steel Valley Gutter w/ Coating | 32 | w/ Accessories | [6 empty] | THK=( 1.2 )mm |  |  |  | M | 0 | [13 empty] | 0.3238%
16) | A04AR145-00001 | CUBICLE PARTITION | FOR TOILET, | J-10 | A04 | Finishing Work | AR | Exterior/Interior Finish Work | 145 | Cubicle Partition | 07 | for Toilet | 32 | w/ Accessories | [6 empty] | H=( 2000 )mm |  |  |  | M2 | 248 | [5 empty] | 236 |  | 12 | [5 empty] | 0%
17) | A04AU206-00001 | URINAL SCREEN | 1500mm(H) x 600mm(W) | [21 empty] | EA | 14 | [5 empty] | 12 |  | 2 | [5 empty] | 0.4459%
18) | A04AR138-00001 | STEEL TROWEL FINISH | FOR CONCRETE SURFACE | F-05 | A04 | Finishing Work | AR | Exterior/Interior Finish Work | 138 | Steel Trowel Finish | [14 empty] | M2 | 3138.12 | [5 empty] | 1936.8 |  | 1049 | 40 | 32.68 |  | 44 | 35.64 | 0.1451%
19) | A04AR138-00003 | SURFACE HARDENER | HEAVY DUTY FLOOR CHEMICAL SURFACE HARDENER ANTI-DUST FINISH | G-20 | A04 | Finishing Work | AR | Exterior/Interior Finish Work | 138 | Steel Trowel Finish | BN | Hardener Finish(Powder Type) | [12 empty] | M2 | 2340.96 | 1180.96 |  |  | 1160 | [9 empty] | 0.2141%
0%
10 |  | STEEL WORKS | [37 empty] | 18.19%
1) | S01AA007-00001 | STEEL(KS D 3530 SSC275) | (FOR PURLIN & GIRTH) | D-01 | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 007 | Girth & Purlin | [10 empty] | Material KS D 3530 SSC275 |  |  |  | TON | 58.14 | 18.85 |  |  | 36.65 |  |  |  |  | 0.69 | 0.57 |  | 0.79 | 0.59 | 1.193%
2) | S01AA010-00001 |  |  |  | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 010 | Steel Painting/Coating | 01 | for Non-Fireproofed Steel Surface, Surface Preparation, Primer, Second & Final Coat | [8 empty] | Purpose | Coating Type | Material |  | M2 | 3594.004 | 1165.18 |  |  | 2265.76 |  |  |  |  | 42.84 | 35.088 |  | 48.96 | 36.176 | 0%
3) | S03AA007-00001 |  |  |  | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 007 | Girth & Purlin | [10 empty] | Material |  |  |  | TON | 58.14 | 18.85 |  |  | 36.65 |  |  |  |  | 0.69 | 0.57 |  | 0.79 | 0.59 | 0%
4) | S03AE015-00001 |  |  |  | S03 | Main Steel Structure Erection Work | AE | Structural Steel | 015 | Steel Painting | [10 empty] | Purpose | Coating Type | Material |  | M2 | 3594.004 | 1165.18 |  |  | 2265.76 |  |  |  |  | 42.84 | 35.088 |  | 48.96 | 36.176 | 0%
5) | S01AA001-00001 | STEEL(KS D 3866 SHN355) | (INDOOR STEEL / BUILT-UP MEMBER) | D-05 | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 001 | Heavy Steel - Standard (Weight≥90KG/M) | [10 empty] | Material KS D 3866 SHN355 |  |  |  | TON | 31.81 |  |  |  | 31.81 | [9 empty] | 0.6529%
6) | S01AA010-00001 |  |  |  | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 010 | Steel Painting/Coating | 01 | for Non-Fireproofed Steel Surface, Surface Preparation, Primer, Second & Final Coat | [8 empty] | Purpose | Coating Type | Material |  | M2 | 320.64 |  |  |  | 320.64 | [9 empty] | 0%
7) | S03AA027-00001 |  |  |  | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 027 | Heavy Steel (Weight≥90KG/M) | [10 empty] | Material |  |  |  | TON | 31.81 |  |  |  | 31.81 | [9 empty] | 0%
8) | S03AE015-00001 |  |  |  | S03 | Main Steel Structure Erection Work | AE | Structural Steel | 015 | Steel Painting | [10 empty] | Purpose | Coating Type | Material |  | M2 | 320.64 |  |  |  | 320.64 | [9 empty] | 0%
9) | S01AA002-00001 | STEEL(KS D 3866 SHN355) | (INDOOR STEEL / ROLL MEMBER) | D-04 | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 002 | Medium Steel - Standard (90KG/M>Weight≥30KG/M) | [10 empty] | Material KS D 3866 SHN355 |  |  |  | TON | 602.61 | 245.59 |  |  | 357.02 | [9 empty] | 12.37%
10) | S01AA010-00001 |  |  |  | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 010 | Steel Painting/Coating | 01 | for Non-Fireproofed Steel Surface, Surface Preparation, Primer, Second & Final Coat | [8 empty] | Purpose | Coating Type | Material |  | M2 | 12264.96 | 4410.84 |  |  | 7854.12 | [9 empty] | 0%
11) | S03AA028-00001 |  |  |  | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 028 | Medium Steel (90KG/M>Weight≥30KG/M) | [10 empty] | Material |  |  |  | TON | 602.61 | 245.59 |  |  | 357.02 | [9 empty] | 0%
12) | S03AE015-00001 |  |  |  | S03 | Main Steel Structure Erection Work | AE | Structural Steel | 015 | Steel Painting | [10 empty] | Purpose | Coating Type | Material |  | M2 | 12264.96 | 4410.84 |  |  | 7854.12 | [9 empty] | 0%
13) | S01AA002-00001 | STEEL(KS D 3866 SHN355) | (OUTDOOR STEEL / ROLL MEMBER) | D-06 | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 002 | Medium Steel - Standard (90KG/M>Weight≥30KG/M) | [10 empty] | Material KS D 3866 SHN355 |  |  |  | TON | 17.61 | [8 empty] | 4.71 | 4.08 |  | 4.66 | 4.16 | 0.3615%
14) | S01AA010-00001 |  |  |  | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 010 | Steel Painting/Coating | 01 | for Non-Fireproofed Steel Surface, Surface Preparation, Primer, Second & Final Coat | [8 empty] | Purpose | Coating Type | Material |  | M2 | 433.486 | [8 empty] | 119.483 | 100.168 |  | 114.277 | 99.558 | 0%
15) | S03AA028-00001 |  |  |  | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 028 | Medium Steel (90KG/M>Weight≥30KG/M) | [10 empty] | Material |  |  |  | TON | 17.61 | [8 empty] | 4.71 | 4.08 |  | 4.66 | 4.16 | 0%
16) | S03AE015-00001 |  |  |  | S03 | Main Steel Structure Erection Work | AE | Structural Steel | 015 | Steel Painting | [10 empty] | Purpose | Coating Type | Material |  | M2 | 433.486 | [8 empty] | 119.483 | 100.168 |  | 114.277 | 99.558 | 0%
17) | S02AA025-00005 | ANCHOR BOLT | DIA 24MM, L=800 | D-07 | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) | 05 | M24 | [8 empty] | Material | Size |  |  | EA | 64 | [8 empty] | 16 | 16 |  | 16 | 16 | 0.0263%
18) | A03AC029-00005 |  |  |  | A03 | Concrete Work | AC | Substructure Work | 029 | Anchor Bolt (Installation only) | 41 | M24 | [8 empty] | L=( 800 )mm |  |  |  | EA | 64 | [8 empty] | 16 | 16 |  | 16 | 16 | 0%
19) | S02AA025-00008 | ANCHOR BOLT | DIA 36MM, L=1100 | D-07 | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 025 | Anchor Bolt (Straight Type) | 08 | M36 | [8 empty] | Material | Size |  |  | EA | 889 | 400 |  |  | 489 | [9 empty] | 0.3654%
20) | A03AC029-00008 |  |  |  | A03 | Concrete Work | AC | Substructure Work | 029 | Anchor Bolt (Installation only) | 44 | M36 | [8 empty] | L=( 1100 )mm |  |  |  | EA | 889 | 400 |  |  | 489 | [9 empty] | 0%
21) | S02AA020-00001 | STEEL HANDRAIL | W/ PAINT (OR) HOT DIP GALVANIZED. | N-08 | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 020 | Steel Handrails | [10 empty] | Handrail Type | Material | Height | Requirement | M | 707.1 | 357.1 |  |  | 350 | [9 empty] | 0.9444%
22) | S04AA020-00001 |  |  |  | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 020 | Steel Handrails | [10 empty] | Handrail Type | Material | Height | Requirement | M | 707.1 | 357.1 |  |  | 350 | [9 empty] | 0%
23) | S01AA010-00002 | STEEL PAINTING | FOR-FIRE-PROOFED, PAINT TYPE (2HOUR) | D-12 | S01 | Main Steel Structure Fabrication Work | AA | Shelter/Building | 010 | Steel Painting/Coating | 02 | for Fireproofed Steel Surface, Surface Preparation & Primer Coat | [8 empty] | Purpose | Coating Type | Material |  | M2 | 0 | [13 empty] | 0%
24) | F01AC000-00004 |  |  |  | F01 | Building/Shelter Fire Proofing Work | AC | Intumescent Coating Type | 000 |  | 04 | 2 hr. rating (UL 1709) | [8 empty] | Material | DFT |  |  | M2 | 0 | [13 empty] | 0%
25) | S02AA023-00001 | CAGED LADDER(2.5m < H ≤ 10m) | W/ PAINT (OR) HOT DIP GALVANIZED. | N-13 | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 023 | Steel Ladder | 05 | With Cage | [8 empty] | Material | Requirement |  |  | M | 49.5 |  |  |  | 15 |  | 7 |  | 10.5 | 4 | 4 |  | 4 | 5 | 0.1017%
26) | S04AA023-00001 |  |  |  | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 023 | Steel Ladder | 05 | With Cage | [8 empty] | Item Type | Material | Requirement |  | M | 49.5 |  |  |  | 15 |  | 7 |  | 10.5 | 4 | 4 |  | 4 | 5 | 0%
27) | S02AA023-00001 | CAGED LADDER(10.0m < H) | W/ PAINT (OR) HOT DIP GALVANIZED. | N-14 | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 023 | Steel Ladder | 05 | With Cage | [8 empty] | Material | Requirement |  |  | M | 98.8 | 22.8 |  |  | 34 |  | 42 | [7 empty] | 0.203%
28) | S04AA023-00001 |  |  |  | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 023 | Steel Ladder | 05 | With Cage | [8 empty] | Item Type | Material | Requirement |  | M | 98.8 | 22.8 |  |  | 34 |  | 42 | [7 empty] | 0%
29) | S02AA018-00001 | GRATING | THK.>=32MM, GALVANIZED | N-03 | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 018 | Grating | [10 empty] | Material | THK32 |  |  | M2 | 690.46 | 224.08 |  |  | 440 |  | 4 |  | 18 | 2.7 | 1.68 |  |  |  | 0.9577%
30) | S04AA018-00001 |  |  |  | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 018 | Grating | [10 empty] | Material | THK |  |  | M2 | 690.46 | 224.08 |  |  | 440 |  | 4 |  | 18 | 2.7 | 1.68 |  |  |  | 0%
31) | S02AA017-00001 | CHECKERED PLATE | GALVANIZED, 6 MM | N-04 | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 017 | Checkered/Flooring Plate | [10 empty] | Material | THK6 |  |  | M2 | 97.66 |  |  |  | 54.41 |  | 6.25 |  | 37 | [5 empty] | 0.0602%
32) | S04AA017-00001 |  |  |  | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 017 | Checkered/Flooring Plate | [10 empty] | Material | THK |  |  | M2 | 97.66 |  |  |  | 54.41 |  | 6.25 |  | 37 | [5 empty] | 0%
33) | S02AA024-00001 | DECK PLATE | GALVANIZED. 1.6 t | D-09 | S02 | Miscellaneous Steel Fabrication Work | AA | Shelter/Building | 024 | Galvanized Steel Deck Plate | [10 empty] | THK1.6 | Requirement |  |  | M2 | 1584.76 | 1229.76 |  |  | 355 | [9 empty] | 0.863%
34) | S04AA024-00001 |  |  |  | S04 | Miscellaneous Steel Erection Work | AA | Shelter/Building | 024 | Galvanized Steel Deck Plate | [10 empty] | THK | Requirement |  |  | M2 | 1584.76 | 1229.76 |  |  | 355 | [9 empty] | 0%
35) | S03AA030-00001 | GROUTING | NON-SHRINK CEMENT BASED GROUT. | D-08 | S03 | Main Steel Structure Erection Work | AA | Shelter/Building | 030 | Non-Shrink Cement Based Grout | [10 empty] | Material | THK |  |  | M3 | 2.91 | 1.65 |  |  | 1.21 |  |  |  |  | 0.01 | 0.01 |  | 0.01 | 0.02 | 0.08969%
0%
11 |  | MISC. WORKS | [37 empty] | 0.9841%
1) | A04AU171-00001 | ROOF DRAIN (Φ100 / CAST IRON) | FOR BUILDING | K-15 | A04 | Finishing Work | AU | Misc. Work | 171 | Roof Drain (for Building) | DQ | Cast Iron Type | 56 | DIA=100mm | [10 empty] | EA | 0 | [13 empty] | 0%
2) | A04AU171-00002 | ROOF DRAIN (Φ150 / CAST IRON) | FOR BUILDING | K-16 | A04 | Finishing Work | AU | Misc. Work | 171 | Roof Drain (for Building) | DQ | Cast Iron Type | 57 | DIA=150mm | [10 empty] | EA | 36 | 10 |  |  |  |  | 12 |  | 14 | [5 empty] | 0.03699%
3) | A04AU173-00001 | DOWNSPOUT(Φ100 / GALV. STL) | FOR BUILDING, GALV. STEEL. | K-19 | A04 | Finishing Work | AU | Misc. Work | 173 | Downspout | DR | Galvanized Steel Type | 34 | w/ Fixing Accessories | 56 | DIA=100mm | [8 empty] | M | 34 | [8 empty] | 8 | 8 |  | 8 | 10 | 0.01816%
4) | A04AU173-00002 | DOWNSPOUT(Φ150 / GALV. STL) | FOR BUILDING, GALV. STEEL. | K-20 | A04 | Finishing Work | AU | Misc. Work | 173 | Downspout | DR | Galvanized Steel Type | 34 | w/ Fixing Accessories | 57 | DIA=150mm | [8 empty] | M | 759 | 114 |  |  | 288 |  | 246 |  | 111 | [5 empty] | 0.5069%
5) | A04AU174-00001 | WATER COLLECTION BOX | GALV. STEEL DOWN SPOUT HEAD | K-23 | A04 | Finishing Work | AU | Misc. Work | 174 | Water Collection Box | DR | Galvanized Steel Type | 34 | w/ Fixing Accessories | [10 empty] | EA | 60 | 10 |  |  | 16 |  | 12 |  | 14 | 2 | 2 |  | 2 | 2 | 0.04623%
6) | A04AU178-00002 | CHAINLINK FENCE |  | P-03 | A04 | Finishing Work | AU | Misc. Work | 178 | Chain Link Fence (Fixed Type) | DU | Self-Standing Type w/ Steel Frame | 34 | w/ Fixing Accessories | 70 | 2000mm≤H<2500mm |  |  |  |  | H=( 2300 )mm |  |  |  | M | 54 | [11 empty] | 30 | 24 | 0.06824%
7) | A04AU181-00001 | CHAINLINK GATE |  | P-04 | A04 | Finishing Work | AU | Misc. Work | 181 | Chain Link Fence Double Gate | EB | Self-Standing Type, Double | 50 | w/ Frame, Fixing Accessories | [6 empty] | W x H=( 6000 )mm x ( 2400 )mm |  |  |  | EA | 2 | [11 empty] | 1 | 1
8) | A04AU185-00002 | STEEL BOLLARD | GUARD POST, CONCRETE FILL. | N-15 | A04 | Finishing Work | AU | Misc. Work | 185 | Steel Bollard | EH | Removable Type | 51 | w/ Paint, Concrete Fill | [6 empty] | DIA=( 150 )mm / H=( 1000 )mm |  |  |  | EA | 12 | 4 |  |  | 2 |  |  |  | 2 |  |  |  | 2 | 2 | 0.01438%
9) | A04AU186-00001 | BUILDING SIGNAGE |  |  | A04 | Finishing Work | AU | Misc. Work | 186 | Building Signage | [14 empty] | EA | 8 | 1 |  |  | 1 |  | 1 |  | 1 | 1 | 1 |  | 1 | 1 | 0.02836%
10) | A04AU187-00001 | ROOM SIGNAGE |  |  | A04 | Finishing Work | AU | Misc. Work | 187 | Room Signage | [14 empty] | EA | 62 | [5 empty] | 54 |  | 8 | [5 empty] | 0.01274%
11) | A04AU191-00001 | MIRROR / W GLASS SHELF | 750Wx800Hx5T | [21 empty] | EA | 1 | [7 empty] | 1 | [5 empty] | 0%
12) | A04AU191-00001 | MIRROR / W GLASS SHELF | 1500Wx800Hx5T | [21 empty] | EA | 10 | [5 empty] | 10 | [7 empty] | 0%
13) | A04AU192-00001 | SOAP DISPENSERS | [22 empty] | EA | 21 | [5 empty] | 20 |  | 1 | [5 empty] | 0%
14) | A04AU194-00001 | TOWEL BAR | [22 empty] | EA | 17 | [5 empty] | 16 |  | 1 | [5 empty] | 0%
15) | A04AU199-00001 | PAPER HOLDER | [22 empty] | EA | 23 | [5 empty] | 22 |  | 1 | [5 empty] | 0%
16) | A04AU210-00001 | VANITY TOP | L=750MM (1 BOWL) | O-17 | [20 empty] | EA | 1 | [7 empty] | 1 | [5 empty] | 0%
17) | A04AU210-00001 | VANITY TOP | L=1500MM (2 BOWL) | O-18 | [20 empty] | EA | 10 | [5 empty] | 10 | [7 empty] | 0.05733%
18) | A03AC049-00001 | MISC STEEL | GALVANIZED. | N-01 | A03 | Concrete Work | AC | Substructure Work | 049 | Embedded Steel(Steel Plate, Corner Angle and etc.) w/ Anchor Bar (Purchase & Installation) | 33 | Hot-Dip Galvanized Steel | 14 | Galv.: ASTM A123 | [10 empty] | TON | 6.84 | 1.59 |  |  | 3 |  | 1.2 |  | 0.7 | 0.2 | 0.15 |  |  |  | 0.006473%
19) | A03AG053-00001 | STEEL FORM | FOR CEP | N-18 | A03 | Concrete Work | AG | Mass Concrete Work | 053 | Steel Casing for CEP | 17 | Including Anchoring, Tar Epoxy Coating, Frame & Accessories, Weldings | [8 empty] | Steel Pipe: D( 1000 )mm x THK( 10 )t x L(9 )m, Steel Plate: W( 1000 )mm x L(1000 )mm x THK( 10 )t |  |  |  | EA | 2 |  |  |  | 2 | [9 empty] | 0.1027%
0.0773%
[26 empty] | EXCA | 1201.86 | 267.3 | 267.3 | 812.57 | 417.01 | 1024.07 |  | 435.52 | 44.16 | 32.85 |  | 45.42 | 71.9 | 0.008219%
[26 empty] | STEEL | 264.44 | 0 | 0 | 425.48 | 0 | 0 |  | 0 | 5.4 | 4.65 |  | 5.45 | 4.75
[26 empty] | CONC | 1024.08 | 398.7 | 398.7 | 797.14 | 646.52 | 2803.84 |  | 974.66 | 47.26 | 36.23 |  | 42.9 | 56.49
[26 empty] | FORM | 2599.8 | 259.15 | 259.15 | 1224.65 | 452.89 | 13024.29 |  | 4710.4 | 52.2 | 38.94 |  | 33.8 | 75.3
[26 empty] | REBAR | 112.31 | 45.7 | 45.7 | 88.05 | 75.05 | 389.09 |  | 133.05 | 5.03 | 3.89 |  | 4.64 | 5.63
[26 empty] | PILE | 99 | 40 | 40 | 121 | 54 | 125 |  | 69 | 5 | 5 |  | 5 | 6

## Description
7.4.3 BOQ
C. MATERIAL BRIEF SPECIFICATION
[P-현대차CCPP] 현대자동차 울산공장 복합화력 발전소, Rev. No : 6 ]
Discipline : Architecture |  | 2021-07-29
A-01 | SYSTEM SUPPORT WORK - FOR STEAM TURBINE GENERATOR FOUNATION TOP TABLE (ELEVATED TOP TABLE TYPE) - INCLUDING ERECT & DISMANTLE COST - HEAVY DUTY SHORING, STEEL TUBULAR, ACCESSORIES - INCLUDING SHOP DWG.
B-01 | EXCAVATION COMMON SOIL - REGARDLESS of EXCAVATION DEPTH AND METHOD (MACHINERY OR HAND DIGGING) - INCLUDING SURVEY, MARKING & LEVELING - INCLUDING DEWATERING WITH a PROVISION of SUMP AND PUMP, IF REQUIRED - INCLUDING SAFETY PRECAUTION SUCH as STRUTTING, SHEETING AND BRACING - INCLUDING PROTECTION MEASURES to EXISTING & NEW STRUCTURE / UTILITIES ENCOUNTERED DURING THE WORK - INCLUDING COMPACTION AT EXCAVATED LEVEL - INCLUDING TEST(PLATE LOAD TEST) BENEATH FOUNDATION, IF REQUIRED
B-02 | BACK FILL -FILL MATERIALS - COMPACTION AT A LAYER OF 15cm MAX. - TO KEEP 95% OF MAX. DRY DENSITY IN ACCORDANCE WITH AASHTO T-180 METHOD D - BOTH SELECTED SOIL - INCLUDING ALL ACCESSARY EQUIPMENT SUCH AS VIBRATING ROLLER. RAMMER AND WATER SPRING WHEN REQUIRED
B-03 | BACK FILL - IMPORTED SOIL (반입토) - MAX. SOIL PARTICLE SIZE : 50mm - COURSE-GRAINED SOIL - 다짐도 95% 이상(MODIFIED PROCTOR TEST)
B-04 | DISPOSAL - 부지 내부 사토 (굴착토 재사용 목적) - DISPOSAL DISTANCE : 약 1.0km
B-05 | DISPOSAL - TO BE DISPOSED OUTSIDE THE PLANT BOUNDARY LIMIT(AT THE MUNICIPAL CORPORATION DESIGNATED DUMPING AREA) 부지 외부 사토 - DISPOSAL DISTANCE ( KM), 토취장, 사토장 위치 및 거리 확인 및 관련 인허가 획득은 계약자 역무임
B-06 | CRUSHED STONE W/ SAND FILL - INCLUDING COMPACTION, GRADING & TEST
B-07 | SOIL REPLACEMENT - SELECTED EXCAVATED AND SCREENED LIMESTONE ROCK MAX. SIEVE SIZE : 50mm - FOR BENEATH FOUNDATION - COMPACTION ONE LAYER OF MAX. 150mm AND MAX. 95% OF DRY DENSITY IN ACCORDANCE WITH ASTM D1557 - INCLUDING NECESSARY TEST AS PER SPEC. - THIS SHALL BE GOOD HARD WELL GRADED MATERIAL SCREENED AND CRUSHED AS NECESSARY TO LIE WITHIN THE GRADING ENVELOPE GIVEN BELOW WHEN TESTED IN ACCORDANCE WITH ASTM.
B-08 | COMPACTED SUB-BASE- STRUCTURE COMPACTION - FOR BENEATH SHALLOW FOUNDATION - THK. 0.5m ~ 1.0m -THE VALUE OF CBR NOT LESS THAN 35% (ASTM D 1883) -COMPACTION AT A LAYER OF 15cm MAX. AND 95% OF MAX. DRY DENSITY IN ACCORDANCE WITH ASTM D1557.
B-09 | GRAVEL LAYER - FOR COAL STORAGE SHED - DIA 100
B-10 | P.P. MAT - FOR COAL STORAGE SHED - THK. 5MM - POLYPROPYLENE MAT
B-11 | GRAVEL PAVING - FOR COAL STORAGE SHED - THK. 200MM - SUB-GRADE TO BE COMPACTED TO 95% OF MAX. DRY DENSITY AS PER ASTM D1557 - SPREADING MAX. Φ40 mm CRUSHED ROCKS OR GRAVELS - INCLUDING EXCAVATION & DISPOSAL
C-01 | LEAN CONCRETE - f'c=18 MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I - FOR LEAN CONC., BLINDING, SCREED, BACKFILL - INCLUDING MARKING, LEVELING, SCAFFOLDING, STAGING, CURING & TESTING - INCLUDING POURING & VIBRATING WORK - INCLUDING SMOOTH CONCRETE FINISHING - INCLUDING ALL CONSTRUCTION AND JOINTS WORK - INCLUDING LABOR & EQUIPMENT FOR ERECTION - INCLUDING CRACKED REPAIR & REQUIRED DAMAGED SURFACE - INCLUDING EMBEDDING MATERIALS IN CONCRETE AND TEMPLATE - INCLUDING TESTING, SUPERVISION, INSPECTION AT SITE - INCLUDING CONVEY OF CONCRETE FROM BATCH PLANT TO THE PLACE OF FINAL DEPOSIT - INCLUDING STORAGE/MAINTENANCE/PRESERVATION OF ALL CONCRETE MATERIALS AT SUBCONTRACTOR'S WAREHOUSE OR STORAGE AREA
C-02 | LEAN CONCRETE - f'c=20 MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I - FOR LEAN CONC., BLINDING, SCREED, BACKFILL
C-03 | REINF. CONCRETE - f'c=25MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I - FOR GENERAL USE SUB STRUCTURE (ABOVE GROUND LEVEL)
C-04 | REINF. CONCRETE - f'c=25MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I - FOR GENERAL USE SUB STRUCTURE (UNDER GROUND LEVEL)
C-05 | REINF. CONCRETE - f'c=24MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I / KS L 5201, TYPE I - FOR GENERAL USE SUPER STRUCTURE (ABOVE GROUND LEVEL)
C-06 | REINF. CONCRETE - f'c=24MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I / KS L 5201, TYPE I - FOR GENERAL USE SUB STRUCTURE (UNDER GROUND LEVEL)
C-07 | REINF. CONCRETE - f'c=30MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I / KS L 5201, TYPE I - FOR TG FOUNDATION (ABOVE GROUND LEVEL)
C-08 | REINF. CONCRETE - f'c=30MPa(CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I / KS L 5201, TYPE I - FOR TG FOUNDATION & HRSG BUILDING & HRSG FOUNDATION (UNDER GROUND LEVEL)
C-09 | TEMPERATURE CONTROL MONITORING - FOR MASS CONCRETE STRUCTURE(T=800mm OVER) & TG FOUNDATION - INCLUDING THERMO COUPLER, MONITORING & RECORD ACC. TO APPROVED MS
C-10 | HIGH YIELD DEFORMED BAR (EPOXY COATED) - ASTM A615 GRADE 60 (Fy=420MPa) - FUSION BONDED EPOXY COATED REINFORCING BAR(ASTM A775) - INCLUDING PRESSURE WELDED JOINT WORK WHERE NECESSARY & STRENGTH TEST - INCLUDING BAR SUPPORTS, TIE WIRES, SPACER, FABRICATED BAR MESH - INCLUDING RE-BAR SHOP DRAWING & BAR BENDING SCHEDULE - INCLUDING BAR BENDING & CUTTING - INCLUDING SLIP ROUND BAR AT SEPARATION JOINT - INCLUDING LABOR & EQUIPMENT - INCLUDING SITE INSPECTION
C-11 | HIGH YIELD DEFORMED BAR (BLACK DEFORMED BARS) - KS D 3504 SD400 - ASTM A615 GRADE 60 (Fy=420MPa) - BS 4449 : 2005 GRADE 500 - INCLUDING PRESSURE WELDED JOINT WORK WHERE NECESSARY & STRENGTH TEST - INCLUDING BAR SUPPORTS, TIE WIRES, SPACER, FABRICATED BAR MESH - INCLUDING RE-BAR SHOP DRAWING & BAR BENDING SCHEDULE - INCLUDING BAR BENDING & CUTTING - INCLUDING SLIP ROUND BAR AT SEPARATION JOINT
C-12 | FAIR FACED FORM - FOR EXPOSED SUPERSTRUCTURE FORM FACE / PAINTED CONCRETE FORM FACE - FOR EQUIPMENT PLINTH AND FLOOR OPENING - COATED PLYWOOD THK. 18MM, 3 USE - INCLUDING, FORM TIE, ALL ACCESSORIES, SEALING OF FORM TIE HOLE, SEPARATOR & ANCHOR BOX OUT. - INCLUDING CHAMFER FOR EXPOSED EDGE - INCLUDING FLOOR AND WALL OPENING WORK & SLEEVE - INCLUDING BOXOUT FOR EQUIPMENT ANCHOR BOLT - INCLUDING LABOR & EQUIPMENT - INCLUDING FABRICATION / FORM INSTALL & REMOVAL - INCLUDING SHORING, SCAFFORDING AND SAFETY MEASURES - INCLUDING FORMWORK CALCULATION FOR STG PEDESTAL & TOP DECK (INCLUDING SHOP DRAWING)
C-13 | NORMAL FACED FORM - FOR UNDERGROUND CONCRETE - FOR HIDDEN SURFACE & APPLIED FINISHING CONCRETE FORM FACE (EXCLUDE PAINTED CONCRETE FORM FACE) - NORMAL PLYWOOD THK. 18MM, 6 USE
C-14 | SYSTEM FORM - FOR STEAM TURBINE GENERATOR FOUNATION TOP TABLE - HEAVY-DUTY FORMS, METAL FRAMED PLAYWOOD FORMS
C-15 | FAIR FACED ROUND FORM FOR EXPOSED TO VIEW - INCLUDING, FORM TIE, ALL ACCESSORIES, SEALING OF FORM TIE HOLE, SEPARATOR & ANCHOR BOX OUT. - INCLUDING CHAMFER FOR EXPOSED EDGE - INCLUDING FLOOR AND WALL OPENING WORK & SLEEVE - INCLUDING BOXOUT FOR EQUIPMENT ANCHOR BOLT - INCLUDING LABOR & EQUIPMENT - INCLUDING FABRICATION / FORM INSTALL & REMOVAL - INCLUDING SHORING, SCAFFORDING AND SAFETY MEASURES
C-16 | NORMAL FACED ROUND FORM FOR HIDDEN SURFACE
C-17 | PRECAST CONC. COVER - THK.100 (SINGLE FABRIC) - FOR PIPE & CABLE TRENCH - INCLUDING LIFTING HANDLE, CORNER ANGLE
C-18 | PRECAST CONC. COVER - THK.150 (SINGLE FABRIC) - FOR PIPE & CABLE TRENCH - INCLUDING LIFTING HANDLE, CORNER ANGLE
C-19 | PRECAST CONC. COVER - THK.200 (DOUBLE FABRIC) '- FOR PIPE & CABLE TRENCH - INCLUDING LIFTING HANDLE, CORNER ANGLE
C-20 | PRECAST CONC. COVER - THK.250 (DOUBLE FABRIC) '- FOR PIPE & CABLE TRENCH - INCLUDING LIFTING HANDLE, CORNER ANGLE
D-01 | STRUCTURAL STEEL (INDOOR STEEL / ROLL MEMBER) - KS D 3530 SSC275 - ASTM A36 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 or ISO 8501-1 Sa 2.5 Primer : Inorganic Zinc 75㎛ 2nd : High Build Polyamide Epoxy 100㎛ - DFT : TOTAL 175㎛ 􀁹 Common bolts : KS B 1002 or ASTM A307 􀁹 Nuts : KS B 1012 or ASTM A563 􀁹 Washer : KS B 1326 or ASTM F436 􀁹 Hot dip galvanized
D-02 | STRUCTURAL STEEL (INDOOR STEEL / ROLL MEMBER) - KS D 3515 SM355 - ASTM A572 G50 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-6 Primer : Inorganic Zinc 80㎛ 2nd : High Build Epoxy 80㎛ Finish : High Build Epoxy 80㎛ - DFT : TOTAL 240㎛ 􀁹- High-strength bolts : KS B 1010 F10T or ASTM A325(DACRO) 􀁹 Nuts : KS B 1010 or ASTM A563(DACRO) 􀁹 Washer : KS B 1326 or ASTM F436 (DACRO) 􀁹 Detail Description FABRICATION work includes followings but not limited to; - Shop drawings with Master member list. - Supply of Raw materials consisting of steel structures like Main members(roll or built up), Purlin & Girth, Stair, Canopy, Fasteners and Stud Shear Connector(Stud bolt) - Supply of Paints for touch up painting at the site. - Fabrication of Steel structures including Painting. - Transportation of the Materials to Construction Site(FOT). - Submissions : Certificate of Raw materials,Factory Test Report. ERECTION Work includes followings but not limited to; - Erection, Bolting, Welding, Touch up Painting and Grouting work for Column base. - Supply of Equipment for Material Handling and Lifting , Scaffolding, Tools and Consumables. - Submissions : Test and Inspection Report. In case of the seismic resistant frame in steel structure, the welding procedure shall be done in accordance with the requirements of AWS D1.8. The specific details will be indicated in the detail drawings of the engineering design stage
D-03 | STRUCTURAL STEEL (OUTDOOR STEEL / ROLL MEMBER) - KS D 3515 SM355 - ASTM A572 G50 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-6 Primer : Inorganic Zinc 80㎛ 2nd : High Build Epoxy 80㎛ Finish : Polyurethane 80㎛ - DFT : TOTAL 240㎛ 􀁹 High-strength bolts : KS B 1010 F10T or ASTM A325 (DACRO) 􀁹 Nuts : KS B 1010 or ASTM A563 ( DACRO) 􀁹 Washer : KS B 1326 or ASTM F436 (DACRO)
D-04 | STRUCTURAL STEEL (INDOOR STEEL / ROLL MEMBER) - KS D 3866 SHN355 - ASTM A992 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 or ISO 8501-1 Sa 2.5 Primer : Inorganic Zinc 75㎛ 2nd : High Build Polyamide Epoxy 100㎛ - DFT : TOTAL 175㎛ 􀁹 High-strength bolts : KS B 1010 F10T or ASTM A325 (DACRO) 􀁹 Nuts : KS B 1010 or ASTM A563 (DACRO) 􀁹 Washer : KS B 1326 or ASTM F436 (DACRO)
D-05 | STRUCTURAL STEEL (INDOOR STEEL / BUILT-UP MEMBER) - KS D 3866 SHN355 - ASTM A992 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 or ISO 8501-1 Sa 2.5 Primer : Inorganic Zinc 75㎛ 2nd : High Build Polyamide Epoxy 100㎛ - DFT : TOTAL 175㎛ 􀁹 High-strength bolts : KS B 1010 F10T or ASTM A325 (DACRO) 􀁹 Nuts : KS B 1010 or ASTM A563 (DACRO) 􀁹 Washer : KS B 1326 or ASTM F436 (DACRO)
D-06 | STRUCTURAL STEEL (OUTDOOR STEEL / ROLL MEMBER) - KS D 3866 SHN355 - ASTM A992 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 or ISO 8501-1 Sa 2.5 Primer : Inorganic Zinc 75㎛ 2nd : High Build Polyamide Epoxy 125㎛ Finish : Polyurethane 40㎛ - DFT : TOTAL 240㎛ 􀁹 High-strength bolts : KS B 1010 F10T or ASTM A325 (DACRO) 􀁹 Nuts : KS B 1010 or ASTM A563 (DACRO) 􀁹 Washer : KS B 1326 or ASTM F436 (DACRO)
D-07 | ANCHOR BOLT - KS B 1016 or ASTM F 1554 - Nuts : KS B 1012 or ASTM A563 - Washer : KS B 1326 or ASTM F436 - Hot dip galvanized - FOR STEEL COLUMN BASE - INCLUDING INSTALLATION & ALIGNMENT FOR ANCHOR FRAMES & TEMPLATES
D-08 | NON-SHRINKAGE GROUT - Fcu= 50 MPa AT 28 DAYS - CEMENTIOUS - FOR STEEL COLUMN BASE - INCLUDING FORM WORK
D-09 | DECK PLATE - KS D 3602 - THK. 1.6mm GALVANIZED STEEL - HOT DIPPED GALVANIZED AS PER ASTM A653-01a ZINC WEIGHT OF NOT LESS THAN 0.275kg/m2 ON EACH SIDE OF SHEET - INCLUDING ALL SUBSIDIARY WORK SUCH AS OPENING ARRANGEMENT, INSTALLATION OF END PLATE & ENCLOSURE, CONC. STOPPER, WELDING, etc. - AS PER TECH SPEC. - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION
D-10 | DECK PLATE - KS D 3602 - THK. 1.2mm GALVANIZED STEEL - HOT DIPPED GALVANIZED AS PER ASTM A653-01a ZINC WEIGHT OF NOT LESS THAN 0.275kg/m2 ON EACH SIDE OF SHEET - INCLUDING ALL SUBSIDIARY WORK SUCH AS OPENING ARRANGEMENT, INSTALLATION OF END PLATE & ENCLOSURE, CONC. STOPPER, WELDING, etc. - AS PER TECH SPEC. - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION
D-11 | FIRE PROOFING COATING 2.0 HOUR (INDOOR STEEL) - 2.0 HOUR FIRE PROOFING COATING - INTUMESCENT FIREPROOF PAINT - 한국공인인증기관 인증제품 - INCLUDING SCAFFOLDING WORK - INCLUDING PROTECTION FOR EQUIPMENT AND FACILITY - INCLUDING REACTIFICATION OF DAMAGED PARTS ON SITE - INCLUDING CERTIFICATION
D-12 | FIRE PROOFING COATING 2.0 HOUR (INDOOR STEEL) - 2.0 HOUR FIRE PROOFING COATING - INTUMESCENT FIREPROOF PAINT - 한국공인인증기관 인증제품 - INCLUDING SCAFFOLDING WORK - INCLUDING PROTECTION FOR EQUIPMENT AND FACILITY - INCLUDING REACTIFICATION OF DAMAGED PARTS ON SITE - INCLUDING CERTIFICATION
D-13 | STRUCTURAL STEEL (ELECTION ONLY) - BRIEF SPEC.: SEE ITEM NO. 4.1 & 4.2 - INCLUDING TOUCH-UP PAINTING & GRINDING, WELDING, SCAFFOLDING WORK (IF NECESSARY) - INCLUDING WELDING OF STUD SHEAR CONNECTOR (STUD BOLTS) - INCLUDING TESTING AS PER TECH.SPEC.
E-01 | INSULATION FOR CAVITY WALL - THK.100 GLASS WOOL (64kg/m3 DENSITY) - INCLUDING FIXING ACCESSORIES - INCLUDING SCAFFOLDING
E-02 | T115 CLAY/CEMENT BRICK - KS F4004 2nd grade, Min. Compressive strength >= 8.2N/mm2 (시멘트 벽돌은 KS F 4004 C종 2급으로 압축강도는 8.2 N/mm2 이상) - INCLUDING TIES & GALV. ANCHOR TO BE WELDED TO STEEL - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING SEISMIC REINFORCEMENT BAR (VERTICAL, HORIZONTAL) - INCLUDING HEADER, STIFF COLUMN, LINTEL, CONC. FRAME FOR LARGE OPENING
E-03 | T230 CLAY/CEMENT BRICK - KS F4004 2nd grade, Min. Compressive strength >= 8.2N/mm2 (시멘트 벽돌은 KS F 4004 C종 2급으로 압축강도는 8.2 N/mm2 이상) - INCLUDING TIES & GALV. ANCHOR TO BE WELDED TO STEEL - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING SEISMIC REINFORCEMENT BAR (VERTICAL, HORIZONTAL) - INCLUDING HEADER, STIFF COLUMN, LINTEL, CONC. FRAME FOR LARGE OPENING
E-04 | 4" SAND-LIME BRICK - ASTM C55 - COMPRESSIVE STRENGTH : 20 N/mm2 - SIZE 222x108x67 Detail Description -INCLUDING TIES & GALV. ANCHOR TO BE WELDED TO STEEL - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING SEISMIC REINFORCEMENT BAR (VERTICAL, HORIZONTAL) - INCLUDING HEADER, STIFF COLUMN, LINTEL, CONC. FRAME FOR LARGE OPENING
E-05 | HOLLOW CONC. BLOCK - TYPE I AS PER ASTM C90 - WALL TIE : GALVANIZED STEEL, ASTM A153 CLASS B2 OR EQUIVALANT : FISHTAILED TYPE (150 mm x 75mm) : Max. @450mm (VERTICAL) : Max. @900mm (HORIZONTAL) - WALL LUG : BUTTERFLY TYPE : Max. @450mm (VERTICAL) - INCLUDING GALV. ANCHOR, TIES, LUGS - INCLUDING METAL LATH (Min.300mm Wide) - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING VERTICAL JOINTS POINTED FLUSH AND HORIZONTAL JOINTS POINTED STRUCK FOR FAIR FACED CONC. BLOCK ONLY - INCLUDING GALV. ANCHOR STRIP TO BE WELDED TO STEEL - INCLUDING SOLID CONC. BLOCK FOR END BLOCKS - INCLUDING HEADER, STIFF COLUMN, LINTEL, CONC. FRAME FOR LARGE OPENING - INCLUDING SEISMIC REINFORCEMENT BAR (VERTICAL, HORIZONTAL)
E-06 | 8" HOLLOW CONC. BLOCK
E-07 | 6" HOLLOW CONC. BLOCK
E-08 | 4" HOLLOW CONC. BLOCK
E-09 | 8" FAIR FACED CONC. BLOCK
E-10 | 6" FAIR FACED CONC. BLOCK
E-11 | 4" FAIR FACED CONC. BLOCK
E-12 | CAVITY WALL W/INSULATION (8" BLOCK+ INSULATION+ 4"HOLLOW BLCOK or 4'' SAND-LIME BRICK)
E-13 | CAVITY WALL W/INSULATION (4" BLOCK+ INSULATION+ 4"HOLLOW BLCOK or 4'' SAND-LIME BRICK)
E-14 | 8" HOLLOW CONC. BLOCK (SWYD) - GRADE N, TYPE II AS PER ASTM C90 - WALL TIE : GALVANIZED STEEL, ASTM A153 CLASS B2 OR EQUIVALANT : FISHTAILED TYPE (150 mm x 75mm) : Max. @450mm (VERTICAL) : Max. @900mm (HORIZONTAL) - WALL LUG : BUTTERFLY TYPE : Max. @450mm (VERTICAL) - INCLUDING GALV. ANCHOR, TIES, LUGS - INCLUDING METAL LATH (Min.300mm Wide) - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING VERTICAL JOINTS POINTED FLUSH AND HORIZONTAL JOINTS POINTED STRUCK FOR FAIR FACED CONC. BLOCK ONLY - INCLUDING GALV. ANCHOR STRIP TO BE WELDED TO STEEL - INCLUDING SOLID CONC. BLOCK FOR END BLOCKS - INCLUDING HEADER, STIFF COLUMN, LINTEL, CONC. FRAME FOR LARGE OPENING - INCLUDING SEISMIC REINFORCEMENT BAR (VERTICAL, HORIZONTAL)
E-15 | 4" HOLLOW CONC. BLOCK (SWYD)
E-16 | 8" U-CONC. BLOCK - TYPE I AS PER ASTM C90 - 4-D12 REINFORCING BARS TO BE USED AND TO BE FILLED W/ CONC - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING GALV. ANCHOR STRIP TO BE WELDED TO STEEL
E-17 | 6" U-CONC. BLOCK - TYPE I AS PER ASTM C90 - 4-D12 REINFORCING BARS TO BE USED AND TO BE FILLED W/ CONC - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING GALV. ANCHOR STRIP TO BE WELDED TO STEEL
E-18 | 4" U-CONC. BLOCK - TYPE I AS PER ASTM C90 - 2-D12 REINFORCING BARS TO BE USED AND TO BE FILLED W/ CONC - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING GALV. ANCHOR STRIP TO BE WELDED TO STEEL
E-19 | HOLLOW GLASS BLOCK - 200mm x 200mm x thk.90 - COMFORMING TO BS1207 & CP122 - INCLUDNG SCAFFOLDING - INCLUDNG FIXING MATERIAL
E-20 | DAMP-PROOF COURSE - ALUMINUM CORED BITUMENISED HESSIAN COVERED SHEET : BS6398 : 1983, BS743, W=350mm - HORIZONTAL: BOTTOM OF ALL BLOCKWORK INCLUDING 12MM THICK CEMENT MORTAR - VERTICAL: ALL DOOR & WINDOW REVEALS - THE DAMP PROOF MEMBRANE SHALL BE LAPPED AND BE FULLY BONDED TO A DAMP PROOF COURSE IN THE PLINTH WALL.
F-01 | BONDED CEMENT SCREED - THK. MIN. 40mm - INCLUDING CONTROL JOINT WORK WITH ALL RELATED MATERIAL - INCLUDING STEEL TROWEL FINISHING AND/ OR MECHANICAL PLACING & FINISHING - INCLUDING ADHESIVE AND APPROPRIATE SLOPE
F-02 | EXTERIOR CEMENT PLASTER FOR WALL - THK. 21 / 3 COATS (8+8+5)mm - INCLUDING SCAFFOLDING - INCLUDING VERT. /HORIZONTAL CONTROL JOINT WORK - INCLUDING GALV. CORNER & CASING BEAD & PLASTER STOP & LATH WORK - INCLUDING PREPARETION OF SURFACE & MOIST CURING
F-03 | INTERIOR CEMENT PLASTER FOR WALL - THK. 18mm / 3 COATS (7+7+4)mm - INCLUDING SCAFFOLDING - INCLUDING VERT. /HORIZONTAL CONTROL JOINT WORK - INCLUDING GALV. CORNER & CASING BEAD & PLASTER STOP & LATH WORK - INCLUDING PREPARETION OF SURFACE & MOIST CURING
F-04 | INTERIOR CEMENT PLASTER FOR CEILING - THK. 9mm / 2 COATS (4.5+4.5)mm
F-05 | STEEL TROWEL FINISH - FOR CONCRETE FLOOR FACE UNDER THE HARDENER FINISHING, PAINTING AND PVC TILE, CARPET TILE, ETC.
G-01 | EMULSION PAINT (EXT.) - FOR EXT. WALL - Surface Prep - Prime Coat Latex Emulsion - Minimum dry thickness 2 mils. Koppers "600 - Interior, Exterior", Tnemec "6 Tneme - Cryl", or Amerguard 335 Epoxy Acrylic. - Second Coat Latex Emulsion - Minimum dry thickness 2 mils. Koppers "600 - Interior, Exterior", Tnemec "6 Tneme - Cryl", or Amerguard 335 Epoxy Acrylic. - Third Coat Copolymer - Minimum dry thickness 2 mils. Rainguard Products Company "Vandl Guard". - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-02 | ACRYLIC EMULSION PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT OF ALKALI-RESISTING SEALER 30 ~ 35㎛ - 2 COATS EMULSION PAINT 50~60㎛ '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-03 | ACRYLIC EMULSION PAINT (EXT.) - FOR EXT. WALL - 1 COAT OF ALKALI-RESISTING SEALER 30 ~ 35㎛ - 2 COATS ACRYLIC PAINT - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-04 | ACRYLIC PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT OF ALKALI-RESISTING SEALER 30 ~ 35㎛ - 2 COATS ACRYLIC PAINT '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-05 | ACRYLIC PAINT (BASE) - FOR BASE PAINT H=100mm - 1 COAT OF ALKALI-RESISTING SEALER 30 ~ 35㎛ - 2 COATS ACRYLIC PAINT '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-06 | ALKYD ENAMEL PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT PRIMER - 2 COATS OF ALKYD ENAMEL PAINT - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-07 | EPOXY PAINT (FLOOR) - FOR INTERIOR FLOOR - 1 COAT PRIMER - 2 COATS EPOXY POLYAMIDE, SEAL COAT TYPE - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-08 | EPOXY PAINT (DUST PROOF) - FOR BENEATH OF FALSE FLOOR - 1 COAT PRIMER - 1 COATS EPOXY POLYAMIDE '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-09 | EPOXY PAINT (EXT.) - FOR EXT. WALL - 1 COAT PRIMER - 2 COATS EPOXY POLYAMIDE '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-10 | EPOXY PAINT (INT.) - FOR INT. WALL & CEILING - Surface Prep - Prime Coat Acrylic Emulsion - Kopper "Surfacer", Tnemec 51 792 "Vinacryl Primer-sealer", or Amerguard 149. - Second Coat Epoxy - Minimum dry thickness 1.75 mils. Koppers "Glamorglass 200 Epoxy", or Amerguard 335 "Epoxy Acrylic". - Third Coat Epoxy - Minimum dry thickness 1.75 mils. Koppers "Glamorglass 200 Epoxy", or Amerguard 335 "Epoxy Acrylic". '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-11 | EPOXY PAINT (BASE) - FOR BASE PAINT H=100mm - 1 COAT PRIMER - 2 COATS EPOXY POLYAMIDE '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-12 | ACID RESISTANT PAINT (FLOOR) - FOR INTERIOR FLOOR - 1 COAT CHLORINATED RUBBER PRIMER - 2 COATS CHLORINATED RUBBER HIGH BUILD - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-13 | ACID RESISTANT PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT CHLORINATED RUBBER PRIMER - 2 COATS CHLORINATED RUBBER HIGH BUILD - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-14 | CHEMICAL RESISTANT EPOXY PAINT (FLOOR) - FOR INTERIOR FLOOR - 1 COAT EPOXY PRIMER / SEALER - 2 COATS PHENOLIC EPOXY - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-15 | CHEMICAL RESISTANT EPOXY PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT EPOXY PRIMER / SEALER - 2 COATS PHENOLIC EPOXY '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-16 | COLORLESS WATER REPELLENT PAINT - FOR EXT. WALL (4" SAND-LIME BRICK) -1 COAT - INCLUDING SCAFFOLDING
G-17 | THK.5mm EPOXY SCREED & SEAL COAT (FLOOR) - FOR INTERIOR FLOOR - 1 COAT EPOXY PRIMER & SEALER - 1 COAT EPOXY MORTAR SCREED VARIABLE MIN. 5mm THK - 1 COAT EPOXY SEAL COAT ON TOP OF EPOXY SCREED - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-18 | THK.3mm HEAVY DUTY SELF LEVELLING EPOXY PAINT (FLOOR) - FOR INTERIOR FLOOR - 1 COAT EPOXY PRIMER - 1 COAT HIGH BUILT SELF LEVELLING EPOXY SCREED COATING VARIABLE MIN. 3mm THK - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-19 | TEXTURED PAINT (EXT.) - FOR EXT. WALL - 1 COAT PRIMER, - 2 COATS TEXTURED PAINT - 1 COAT DIRT RESISTANCE FINISH COAT - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - WATER RESISTANCE ,ANTI-CONTAMINATION,EASY CLEANING - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-20 | SURFACE HARDENER - FOR INTERIOR FLOOR - HEAVY DUTY FLOOR CHEMICAL SURFACE HARDENER ANTI-DUST FINISH - GRANOLITE® NON-METALLIC FLOOR HARDENER - INCLUDING STEEL TROWEL FINISHING AND/OR MECHANICAL PLACING & FINISHING - INCLUDING JOINT GROUTING - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION - USAGE RATE 5 KG/M2. - INCLUDING ONE COAT OF ‘SEALBOND GR’ CURING COMPOUND.
H-01 | RIGID INSULATION FOR ROOF - FOR ROOF SLAB - THK. 200mm Rigid Extruded Polystyrene Insulation OR EQUIVALENT - COMPRESSIVE STRENGTH : Min. 250 KPa - INCLUDING JOINT TAPE
H-02 | MEMBRANE WATERPROOFING - BUILT-UP ROOFING - FOR ROOF SLAB & PARAPET WALL - INCLUDING COLD WORKED PRIME COAT & 4mm THK. BITUMINUOUS ROOFING FELT - INCLUDING GALV. STEEL FLASHING TO SEAL/COVER THE END OF WATERPROOFING AT PARAPET/UPSTAND - INCLUDING BITUMEN SEALANT AT GROOVE TO END WATERPROOFING MEMBRANE AT UPSTAND - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK
H-03 | MEMBRANE WATERPROOFING - BUILT-UP ROOFING - FOR ROOF SLAB & PARAPET WALL - a. Primer: Shall be MIP-067 epoxy-polyamide, low viscosity, two-component primer sealer. - b. Base Membrane: Shall be "Multi-l-Thane 4000" single-component, high-adhesion, moisture cured, liquid polyurethane membrane, 85% weight solids. - c. Second Coat Membrane: Shall be "Multi-l-Thane 5000" single component, high tensile strength, liquid applied elastomeric polyurethane, 85% weight solids. - d. Aggregate: Equal to or finer than 20 mesh flint shot silica, ground glass, or Monterey sand. Aggregate shall be hard and stable to atmospheric conditions, clean and free of any other material, chemicals or salt. - e. Top Coat: Shall be "Multi-l-Thane 6000" single component, high tensile strength, abrasion resistant and weather-resistant aliphatic polyurethane membrane 53% solids. - f. Caulking: "Multi-l-Seal 1000", one component polyurethane compound. - INCLUDING GALV. STEEL FLASHING TO SEAL/COVER THE END OF WATERPROOFING AT PARAPET/UPSTAND - INCLUDING BITUMEN SEALANT AT GROOVE TO END WATERPROOFING MEMBRANE AT UPSTAND - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK
H-04 | ELATOMERIC COATING - FOR ROOF SLAB & PARAPET WALL - INCLUDING GALV. STEEL FLASHING TO SEAL/COVER THE END OF WATERPROOFING AT PARAPET/UPSTAND - INCLUDING BITUMEN SEALANT AT GROOVE TO END WATERPROOFING MEMBRANE AT UPSTAND - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK
H-05 | EPDM WATERROOFING MEMBRANE - CONTINUOUS SHEET ETHYLENE PROPYLENE DIENE MONOMER (EPDM) ROOFING SYSTEM - FULLY ADHERED EPDM SYSTEM TO MECHANICALLY ATTACHED - INCLUDING ADHESIVE, SHEET, RUBBER FLASHING, SEALANTS - TAPER RIGID INSULATION TO ROOF DRAIN - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK
H-06 | CEMENTITIOUS WATERPROOFING - FOR FLOOR & WALL OF WET ROOM - 2 COAT CEMENT BASE - ACRYLIC-POLYMER EMULSION MIXED WITH CEMENT MORTARS - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK
H-07 | P.E FILM - THK. 0.1mm, 2 LAYERS FOR ROOF - AS PER SPECIFICATION
H-08 | LIGHT WEIGHT CONCRETE ( ROOF ) - LIGHTWEIGHT CELLULAR CONCRETE FILL PORTLAND CEMENT AND FOAMING AGENT - MIN.THK. 60 mm, 1/150 SLOPE - INCLUDING ALL MATERIALS FOR EXPANSION JOINT : @2.0m x 2.0m - INCLUDING WIRE MESH FOR CRACK CONTROL
H-09 | CON'C ROOF TILE - PRECASTE CONC. TILE SIZE : 400x400xT40mm - INCLUDING SEPARATION JOINT OF 15mm FILLED W/ APPROVED SEALANT - INCLUDING CRACK CONTROL JOINT : 8mmx12~15mm(H) @1.25x 1.25M FILLED W/APPROVED SEALANT - INCLUDING SEMI-DRY TYPE CEMENT MORTAR - INCLUDING CONTROL JOINT WORK WITH ALL RELATED MATERIAL - INCLUDING STEEL TROWEL FINISHING AND/ OR MECHANICAL PLACING & FINISHING
H-10 | ROOF AGGREGATE - THK. 50 mm / PROTECTION FOR WATER PROOFING - WASHED AGGREGATE MAX. @ 19MM
H-11 | UNDERGROUND BITUMEN EMULSION PAINT - MASTER SEAL 420 OR EQUIVALENT - 2 COATS - NORMAL DRY CONDITION
H-12 | PVC WATERSTOP - W = 150, THK 9mm FOR FLAT DUMBBELL - INTERNAL TYPE , HEAVY DUTY, FLEXIBLE P.V.C. WITH A CENTRAL EXPANSION BULB
H-13 | HYDROPHILIC POLYMER RUBBER WATERSTOP - BENTONITE CLAY & MICROSCOPIC PLATELETS WATERSTOP - INCLUDING INSTALL
H-14 | UNDERGROUND BITUMEN MEMBRANE - FLEXIBLE MULTY LAYERED COMPOSITE SHEET - FELT MEMBRANE BONDED TO BITUMEN/POLYMER ADHESIVE - FOR ALL UNDERGROUND CONCRETE SURFACE - INCLUDING SEALING JOINT WORK ; RAKING OUT OF WALL & FILLING W/ BITUMEN SEALING COMPOUND - FOR WRAPPING ALL UNDERGROUND FOUNDATION / CONC. STRUCTURE - INCLUDING AEROFOIL OR SIMILAR - INCLUDE'G ALUMINUM FLASHING ACCORDING TO SPEC. - REFER TO TECHNICAL SPEC.
H-15 | CEMENT SCREED FOR WATER PROOFING - THK. 25MM / PROTECTION FOR WATER PROOFING - FOR BOTTOM - INCLUDING CONTROL JOINT WORK WITH ALL RELATED MATERIAL - INCLUDING STEEL TROWEL FINISHING AND/ OR MECHANICAL PLACING & FINISHING
H-16 | PROTECTION BOARD - BITUMEN IMPREGNATED FIBRE BOARD - THK. 6mm - FOR SIDE & TOP SIDE - FOR WALL & VERTICAL SIDE
H-17 | VAPOUR BARRIER - THK. 0.15mm, P.E FILM 2 PLIES - FOR BELOW GROUND SLAB & ROOF
I-01 | RUBBER SKIRTING - H100 x 2T - FOR WALL
I-02 | ANTI-STATIC VINYL SKIRTING - H100 x 15 mm
I-03 | SKIRT PAINTING - EPOXY PAINT - FOR FLOOR SKIRTING - H=100 - INCLUDING SURFACE TREATMENT & PANIT PUTTY
I-04 | VINYL SHEET THK.3mm - INCLUDING ADHESIVE, WELDING - INCLUDING POLISHING WORK
I-05 | ANTI-STATIC VINYL TILE 400 x 400 x 3mm - INCLUDING ADHESIVE, WELDING - INCLUDING POLISHING WORK
I-06 | HEAVY DUTY P.V.C TILE 400 x 400 x 3mm - INCLUDING ADHESIVE, WELDING - INCLUDING POLISHING WORK
I-07 | P.V.C SKIRTING H100 x 2T - INCLUDING ADHESIVE, WELDING
I-08 | ACCESS FLOOR SYSTEM - 600 x 600 H:300 - 600mm x 600mm x Min.35mm ANTI-STATIC PVC TILE - HIGH DENSITY CHIPBOARD CORE(675 kg/m3) WRAPPED W/ 0.9mm GALV. SHEET Detail Description - INCLUDING STEPS, SUPPORTING MATERIAL & ACCESSORIES - INCLUDING ADHESIVE OR ANCHOR & POLISHING - INCLUDING SEISMIC BRACING SYSTEM FOR SUPPORT STRUCTURE INCLUDING CALCULATION
I-09 | ACCESS FLOOR SYSTEM - 600 x 600 H:600 - 600mm x 600mm x Min.35mm ANTI-STATIC PVC TILE - HIGH DENSITY CHIPBOARD CORE(675 kg/m3) WRAPPED W/ 0.9mm GALV. SHEET
I-10 | ACCESS FLOOR SYSTEM - 600 x 600 H:800 - 600mm x 600mm x Min.35mm ANTI-STATIC PVC TILE - HIGH DENSITY CHIPBOARD CORE(675 kg/m3) WRAPPED W/ 0.9mm GALV. SHEET
I-11 | ACCESS FLOOR SYSTEM - 1200 x 1200 H:1200 - 1200mm x 1200mm x Min.35mm ANTI-STATIC PVC TILE - HIGH DENSITY CHIPBOARD CORE(675 kg/m3) WRAPPED W/ 0.9mm GALV. SHEET
I-12 | UNGLAZED NON-SLIP CERAMIC TILE - FOR FLOOR - THK. 10mm / NON-SLIP TYPE - INCLUDING NON-SLIP NOSING TILE - INCLUDING BEDDING MORTAR & JOINT GROUTING & SEALANT - INCLUDING ADHESIVE & POLISHING
I-13 | GLAZED CERAMIC TILE - FOR WALL - THK. 6mm - INCLUDING BEDDING MORTAR & JOINT GROUTING - INCLUDING 3mm THICK REAL CEMENT PASTE OR ADHESIVE & JOINT GROUTING & SEALANT - INCLUDING SCAFFOLDING - INCLUDING ADHESIVE & POLISHING
I-14 | ACID RESISTANT TILE - FOR FLOOR & BASE - THK. 300 x 300 x 16mm - INCLUDING ACID PROOF MEMBRANE, BEDDING, EPOXY BASED ADHESIVE & JOINT GROUTING - INCLUDING POLISHING
I-15 | ACID RESISTANT TILE - FOR WALL - THK. 300 x 300 x 16mm '- INCLUDING ACID PROOF MEMBRANE, BEDDING, EPOXY BASED ADHESIVE & JOINT GROUTING - INCLUDING POLISHING
I-16 | TERRAZZO TILE - FOR FLOOR - THK. 30mm - INCLUDING BEDDING & JOINT GROUTING - INCLUDING POLISHING - INCLUDING ADHESIVE - INCLUDING GRINDING WORK
I-17 | TERRAZZO STAIR TREAD & RISER THK. 30mm - INCLUDING ANTI-SLIP GROOVE ON TREAD - INCLUDING BEDDING & JOINT GROUTING - INCLUDING ADHESIVE - INCLUDING POLISHING
I-18 | TERRAZZO SKIRTING H100 x 20 mm - INCLUDING BEDDING & JOINT GROUTING - INCLUDING GRINDING WORK - INCLUDING ADHESIVE & JOINT GROUTING
I-19 | GRANITE STAIR TREAD & RISER THK. 20mm - INCLUDING ANTI-SLIP GROOVE - INCLUDING BEDDING & JOINT GROUTING - INCLUDING ADHESIVE - INCLUDING GRINDING & POLISHING
I-20 | MARBLE STAIR TREAD & RISER THK. 20mm - INCLUDING ANTI-SLIP GROOVE - INCLUDING BEDDING & JOINT GROUTING - INCLUDING ADHESIVE - INCLUDING GRINDING & POLISHING
I-21 | GRANITE TILE - FOR FLOOR - THK. 30mm - INCLUDING BEDDING & JOINT GROUTING - INCLUDING GRINDING WORK & POLISHING - INCLUDING ADHESIVE
I-22 | GRANITE TILE - FOR WALL - THK. 20mm - INCLUDING 3mm THICK REAL CEMENT PASTE OR ADHESIVE & JOINT GROUTING - INCLUDING STEEL ANCHORING & ACCESSARIES & SEALANT - INCLUDING ADHESIVE & JOINT GROUTING - INCLUDING SCAFFOLDING - INCLUDING GRANITE SKIRTING (H=100)
I-23 | MARBLE TILE - FOR FLOOR - THK. 30mm - INCLUDING BEDDING & JOINT GROUTING - INCLUDING GRINDING WORK & POLISHING - INCLUDING ADHESIVE
I-24 | MARBLE TILE - FOR WALL - THK. 20mm - INCLUDING 3mm THICK REAL CEMENT PASTE OR ADHESIVE & JOINT GROUTING - INCLUDING STEEL ANCHORING & ACCESSARIES & SEALANT - INCLUDING ADHESIVE & JOINT GROUTING - INCLUDING SCAFFOLDING - INCLUDING GRANITE SKIRTING (H=100)
I-25 | GRANITE / MARBLE SILL - THK. 30mm - FOR WINDOW SILL OR DIVIDING STRIP - INCLUDING BEDDING & JOINT GROUTING
I-26 | MARBLE COUNTER - THK. 50mm x 600mm - FOR GUARD HOUSE / COUNTER - INCLUDING BEDDING & JOINT GROUTING
I-27 | CARPET TILE - THK. 7mm - POLYPROPYLENE YARN IN LOOP-PILE (1/10") - ANTISTATIC - INCLUDING ADHESIVE & SURFACE TREATMENT
I-28 | MOSAIC TILE - FOR EXTERIOR & INT. WALL - INCLUDING BEDDING & JOINT GROUTING - INCLUDING SCAFFOLDING - INCLUDING 3mm THICK REAL CEMENT PASTE OR ADHESIVE & JOINT GROUTING
I-29 | WOODEN SKIRTING - H100 x 15 mm - INCLUDING ADHESIVE
J-01 | ACOUSTIC MINERAL BOARD CEILING - SIZE : THK.15mm x 600 x 600mm or 300X1200mm - NON-COMBUSTIBLE CLASS B TO EN13501-1 - INCLUDING GRID, HANGER, EDGE ANGLE - INCLUDING SCAFFOLDING - INCLUDING CURTAIN BOX MADE OF COATED STEEL SHEET - INCLUDING ACCESS PANEL TO THE CEILING - INCLUDING LIGHT FIXTURE & OPENING REINFORCED WORK - INCLUDING SEISMIC BRACING SYSTEMFOR THE SUSPENSION SYSTEM INCLUDING CALCULATION
J-02 | PVC STRIP CEILING - 100mm WIDE x 15mm DEEP WTHI 25mm RECESSED - FOR TOILETS, SHOWERS CEILING
J-03 | ALUMINIUM PANEL CEILING - SIZE : 600x600x0.5mm OR 600x1200x0.5mm - NON DIRECTIONAL PERFORATED ALUMINIUM - ACOUSTIC BLANKET (25mm LOW-DENSITY BLANKET OF GLASS FIBRE INSULATION) - INCLUDING GRID SYSTEM : GALVANIZED STEEL (MOLDING, LOCKING CLIP ETC.) - INCLUDING SUSPENSION SYSTEM : HOT DIP GAL. MILD STEEL FLATS AND/OR RODS (ROD HANGER : GAL. STEEL OF 4mm DIA.) - FIRE RESISTANCE RATING : 1/2 HOUR - INCLUDING CURTAIN BOX - EPOXY CHROMATE PRIMER 0.1mm+STOVE ENAMEL FINISH ON THE FACE - INCLUDE'G ACCESS PANEL - INCLUDING SEISMIC BRACING SYSTEM FOR THE SUSPENSION SYSTEM, IF REQUIRED
J-04 | ALUMINIUM LINEAR CEILING - ALUMINIUM STRIP : 0.5mmx100mm MODULE (W/20mm SHADOW) ALUMINIUM - AL. ALLOY 3005-H26 OR EQUAL - ACOUSTIC BLANKET (25mm LOW-DENSITY BLANKET OF GLASS FIBRE INSULATION) - INCLUDING GRID, HANGER, EDGE - INCLUDING CURTAIN BOX MADE OF COATED STEEL SHEET - EPOXY CHROMATE PRIMER 0.1mm+STOVE ENAMEL FINISH ON THE FACE - INCLUDE'G ACCESS PANEL - INCLUDING SEISMIC BRACING SYSTEM FOR THE SUSPENSION SYSTEM, IF REQUIRED
J-05 | SMC PANEL CEILING - SIZE : 600 x 600 x 1.2mm - SMC(SHEET MOUNDING COMPOUND) - INCLUDING GRID, HANGER, EDGE ANGLE - INCLUDING SCAFFOLDING - INCLUDING CURTAIN BOX MADE OF COATED STEEL SHEET - INCLUDING ACCESS PANEL TO THE CEILING - INCLUDING LIGHT FIXTURE & OPENING REINFORCED WORK - INCLUDING SEISMIC BRACING SYSTEM DETAIL SHALL BE APPLIED FOR THE SUSPENSION SYSTEM, IF REQUIRED
J-06 | GYPSUM PLASTER BOARD PARTITION WALL(BOTH SIDE) - THK. 75mm - BOTH SIDE : THK. 12.5mm GYPSUM PLASTER BOARD - T50 MINERAL FIBRE INSULATION CORE W/ GALVANIZED METAL STUD FRAME - NON-COMBUSTIBLE & NON-INFLAMMABLE TYPE - INCLUDING ALL HARDWARES & CONNECTING/FIXING ACCESSORIES - INCLUDING JOINT TAPING, OPENING WORK & COMPOUND, SEALANT - INCLUDING SLEEVE, DOOR & WINDOW REINFORCING FRAME WORK
J-07 | GYPSUM PLASTER BOARD PARTITION WALL(ONE SIDE) - THK. 63mm - ONE SIDE : THK. 12.5mm GYPSUM PLASTER BOARD - T50 MINERAL FIBRE INSULATION CORE W/ GALVANIZED METAL STUD FRAME - NON-COMBUSTIBLE & NON-INFLAMMABLE TYPE
J-08 | GYPSUM PLASTER BOARD PARTITION WALL (2 HOUR FIRE RATING) - THK. 100mm - BOTH SIDE : THK. 12.5mm x 2PLIES GYPSUM PLASTER BOARD - T50 MINERAL FIBRE INSULATION CORE W/ GALVANIZED METAL STUD FRAME - NON-COMBUSTIBLE & NON-INFLAMMABLE TYPE - INCLUDING UL CERTIFICATION
J-09 | METAL FACED PLASTERBOARD PARTITIONS - THICKNESS : APPROXIMATELY 70mm - HEIGHT : APPROX. 2700mm - FRAME : GALV.STEEL TUBULAR W/ 60mm WOODEN PLINTH - SCREWLESS & INTERLOCKING TYPE - CORE : HIGH DENSITY MINERAL WOOL - ABSORPTION OF AIR BORNE SOUND : 38dBA OVER - DEMOUNTABLE W/ PLASTERBOARD (12.5mm) WRAPPED W/ ENAMELED METAL FACING ON BOTH SIDE OF METAL STUD - 1 HOUR FIRE RESISTANCE - INCLUDING ALL STUDS, HARDWARES & ACCESSORIES - INCLUDING JOINTING WORK - INCLUDING DOOR & WINDOW (DOUBLE GLAZING OF 4mm CLEAR FLOAT GLASS SET IN PVC BEAD) - INCLUDING JOINT TAPING, OPENING WORK & COMPOUND, SEALANT - INCLUDING SLEEVE,DOOR & WINDOW REINFORCING FRAME WORK
J-10 | TOILET PARTITION - HEIGHT : 2000mm - PARTITION : 30mm HIGH DENSITY CHIP BOARD W/ PVC VENEER - FRONT PANEL : 34x15x2mm ANODIZED ALUMINIUM - UNDERPANEL CLEARANCE : 150mm - INCLUDING ALL HARDWARES & ACCESSORIES(LOCKING DEVICE SOWING OCCUPYING INDICATOR) - INCLUDING U-CHANNEL 32x36x2mm - INCLUDING DOOR (W 650mm)
J-11 | URINAL SCREEN - HEIGHT : 1500mm, WIDE : 600mm - PARTITION : 30mm HIGH DENSITY CHIP BOARD W/ PVC VENEER - INCLUDING ALL HARDWARES & ACCESSORIES
J-12 | SHOWER BOOTH PARTITION - HEIGHT : 2100mm - THK. 10mm TEMPERED SAFETY GLASS - INCLUDING STAINLESS STEEL FRAME AROUND GLASS - INCLUDING ALL HARDWARES & ACCESSORIES -INCLUDING JOINTING WORK
J-13 | FIRE RESISTANT GLAZED PARTITION - HEIGHT : 3000mm - SURFACE : FIRE PROOF COATING - PANEL LINING : 90 MINUTES FIRE RESITIVITY GLAZING - HEAT RESISTANCE : 650℃ - INCLUDING GRID, HANGER, EDGE - INCLUDING 90 MINUTES RESISTANT DOOR, WINDOWS & HARDWARES
J-14 | TIMBER WALL PANEL - HEIGHT 2150mm - FOR WALL - INCLUDING ALL HARDWARES & ACCESSORIES - INCLUDING JOINTING WORK - ALL TIMBER SHALL BE OF EITHER GRADE ‘A’ OR GRADE ‘B’ TIMBER
J-15 | GLASS PARTITION WALL -THK. 10mm TEMPERED SAFETY GLASS - INCLUDING STAINLESS STEEL FRAME AROUND GLASS - INCLUDING ALL HARDWARES & ACCESSORIES(LOCKING DEVICE)
K-01 | THERMAL INSULATED TRAPEZOIDAL CLADDING FOR ROOF -EXTERIOR SKIN: TRAPEZOIDAL PROFILE MIN. 0.8T P.V.D.F coating, galvanized steel sheet - CORE: NON-COMBUSTIBLE MATERIAL ACCORDING TO ASTM or EQUIVALENT, MIN thk 200mm. Glass wool, density over 64kg/m3 -INTERIOR SKIN: TRAPEZOIDAL PROFILE MIN. 0.8T P.V.D.F coating, galvanized steel sheet - HEAVY EPOXY BASE COAT AND A HIGH BUILD WEATHER COAT OF POLYURETHANE - AS PER ASTM E1886 AND E1996. - INCLUDING ALL FLASHING(Roof ridge flashing for top & side, Corner & Joint flashing, door & window flashing , Opening flashing , parapet flashing and etc. ) - INCLUDING ACCESSORIES (ANCHOR, PLATE), SEALANT, BACK UP & JOINT FILLING MATERIAL (AROUND OPENING AREA) - INCLUDING SCAFFOLDING - INCLUDING DOOR & WINDOW SUNSHADE - INCLUDING PROTECTION FILM ON SURFACE OF PRODUCTS TILL SITE. - 10 YEAR GUARANTEE - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION - QUANTITIES ARE PROJECTED AREA
K-02 | THERMAL INSULATED TRAPEZOIDAL CLADDING FOR EXT. WALL -EXTERIOR SKIN: TRAPEZOIDAL PROFILE MIN. 0.8mm P.V.D.F coating, galvanized steel sheet - CORE: NON-COMBUSTIBLE MATERIAL ACCORDING TO ASTM or EQUIVALENT, MIN.thk 120mm Glass wool, density over 64kg/m3 -INTERIOR SKIN: TRAPEZOIDAL PROFILE MIN. 0.6mm Silicone coating, galvanized steel sheet - HEAVY EPOXY BASE COAT AND A HIGH BUILD WEATHER COAT OF POLYURETHANE - AS PER ASTM E1886 AND E1996. - INCLUDING ALL FLASHING(Roof ridge flashing for top & side, Corner & Joint flashing, door & window flashing , Opening flashing , parapet flashing and etc. ) - INCLUDING ACCESSORIES (ANCHOR, PLATE), SEALANT, BACK UP & JOINT FILLING MATERIAL (AROUND OPENING AREA) - INCLUDING SCAFFOLDING - INCLUDING DOOR & WINDOW SUNSHADE - INCLUDING PROTECTION FILM ON SURFACE OF PRODUCTS TILL SITE. - 10 YEAR GUARANTEE - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION - QUANTITIES ARE PROJECTED AREA
K-03 | THERMAL INSULATED TRAPEZOIDAL METAL CLADDING (EXTERIOR WALL, 2HR FIRE RATING) -EXTERIOR SKIN: MIN. 0.7mm GALVANIZED AND FACTORY FINISHED STEEL SHEET - CORE: NON-COMBUSTIBLE MATERIAL ACCORDING TO ASTM or EQUIVALENT, MIN.thk 120mm Glass wool, density over 64kg/m3 -INTERIOR SKIN: MIN. 0.7mm GALVANIZED AND FACTORY FINISHED STEEL SHEET - AS PER ASTM E1886 AND E1996. - INCLUDING UL CERTIFICATION - INCLUDING ALL FLASHING(Roof ridge flashing for top & side, Corner & Joint flashing, door & window flashing , Opening flashing , parapet flashing and etc. ) - INCLUDING ACCESSORIES (ANCHOR, PLATE), SEALANT, BACK UP & JOINT FILLING MATERIAL (AROUND OPENING AREA) - INCLUDING SCAFFOLDING - INCLUDING DOOR & WINDOW SUNSHADE - INCLUDING PROTECTION FILM ON SURFACE OF PRODUCTS TILL SITE. - 10 YEAR GUARANTEE - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION - QUANTITIES ARE PROJECTED AREA
K-04 | SINGLE TRAPEZOIDAL CLADDING FOR ROOF - MIN. THK. 0.6mm GALVANIZED STEEL SHEETS, 35/180 TRAPEZOIDAL PROFILE W/ FACTORY APPLIED FINISH FLUROPOLYMER KYNAR-500(19μm) - INCLUDING ALL FLASHING(Roof ridge flashing for top & side, Corner & Joint flashing, door & window flashing , Opening flashing , parapet flashing and etc. ) - INCLUDING ACCESSORIES (ANCHOR, PLATE), SEALANT, BACK UP & JOINT FILLING MATERIAL (AROUND OPENING AREA) - INCLUDING SCAFFOLDING - INCLUDING DOOR & WINDOW SUNSHADE - INCLUDING PROTECTION FILM ON SURFACE OF PRODUCTS TILL SITE. - 10 YEAR GUARANTEE - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION - QUANTITIES ARE PROJECTED AREA
K-05 | SINGLE TRAPEZOIDAL CLADDING FOR WALL - MIN. THK. 0.6mm GALVANIZED STEEL SHEETS, 35/180 TRAPEZOIDAL PROFILE W/ FACTORY APPLIED FINISH FLUROPOLYMER KYNAR-500(19μm) - INCLUDING ALL FLASHING(Roof ridge flashing for top & side, Corner & Joint flashing, door & window flashing , Opening flashing , parapet flashing and etc. ) - INCLUDING ACCESSORIES (ANCHOR, PLATE), SEALANT, BACK UP & JOINT FILLING MATERIAL (AROUND OPENING AREA) - INCLUDING SCAFFOLDING - INCLUDING DOOR & WINDOW SUNSHADE - INCLUDING PROTECTION FILM ON SURFACE OF PRODUCTS TILL SITE. - 10 YEAR GUARANTEE - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION - QUANTITIES ARE PROJECTED AREA
K-06 | TRANSLUCENT SHEET - GLASS FIBRE SHEET (FRP) THK. 2.0mm - 85% LIGHT TRANSMISSION - UV RESISTANCE - INCLUDING ACCESSORIES, SEALANT, BACK UP & JOINT FILLING MATERIAL - INCLUDING SCAFFOLDING
K-07 | FLASHING - STEEL STEET : GALVANIZED STEEL SHEET (ASTM-A653/A653M G90,275 g/m2) W/ TRAPEZOIDAL PROFILE - COATING : 25 microns POLYVINYLIDENE FLUORIDE
K-08 | GUTTER - THK. 1.2mm GALVANIZED STEEL SHEET - W230mm x H250mm - INCLUDING INSULATION, GUTTER HANGER, ANCHOR & SEALANT - INDLUD'G FIXING & JOINTING - INCLUDING SCAFFOLDING - INCLUDING ALL FLASHING
K-09 | PARAPET/TOP CAPPING FLASHING - 0.75mm GALVANIZED STEEL SHEET - W600mm - INDLUD'G FIXING & JOINTING - INCLUDING SCAFFOLDING
K-10 | ROOF RIDGE FLASHING (TOP & SIDE) - 0.75mm GALVANIZED STEEL SHEET - W500mm
K-11 | CORNER/JOINT FLASHING - 0.75mm GALVANIZED STEEL SHEET - W400mm
K-12 | DOOR & WINDOW FLASHING - 0.75mm GALVANIZED STEEL SHEET - W230mm
K-13 | BASE FLASHING - 1.2mm GALVANIZED STEEL SHEET - W200mm
K-14 | OPENING FLASHING - 0.75mm GALVANIZED STEEL SHEET - W200mm
K-15 | ROOF DRAIN Φ100 / CAST IRON - Φ100 / CAST IRON
K-16 | ROOF DRAIN Φ150 / CAST IRON - Φ150 / CAST IRON
K-17 | ROOF DRAIN Φ100 / UPVC - Φ100 / UPVC
K-18 | ROOF DRAIN Φ150 / UPVC - Φ150 / UPVC
K-19 | DOWN SPOUT Φ100 / GALV. STL - Φ100 / GALV. STL. W/ FACTORY COAT OR ALUMINIUM TYPE - □100 / ALUMINIUM x MIN. 0.75 mm - INCLUDING DOWN SPOUT HANGER & ANCHOR - INCLUDING EPOXY PAINT
K-20 | DOWN SPOUT Φ150 / GALV. STL - Φ150 / GALV. STL. W/ FACTORY COAT OR ALUMINIUM TYPE - □150 / ALUMINIUM x MIN. 0.75 mm - INCLUDING DOWN SPOUT HANGER & ANCHOR - INCLUDING EPOXY PAINT
K-21 | DOWN SPOUT Φ100 / UPVC - Φ100 / UPVC W/ FACTORY COAT OR ALUMINIUM TYPE - INCLUDING DOWN SPOUT HANGER & ANCHOR
K-22 | DOWN SPOUT Φ150 / UPVC - Φ150 / UPVC W/ FACTORY COAT OR ALUMINIUM TYPE - INCLUDING DOWN SPOUT HANGER & ANCHOR
K-23 | DOWN SPOUT HEAD GALV. STL. - GALV. STL. FOR DOWN SPOUT OR ALUMINIUM TYPE
K-24 | DOWN SPOUT HEAD UPVC - UPVC FOR DOWN SPOUT
K-25 | SPLASH BLOCK - PC BLOCK
K-26 | NORMAL WEIGHT CONCRETE PRECAST INSULATED SANDWICH PANEL - THK. 325 MM - DEEP SAND BLASTING FINISH W/ WHITE CEMENT (EXT) - SMOOTH FINISH W/ GREY CEMENT (INT) - STEEL PLATE INSERTS EMBEDDED FOR INSTALLATION TO STEEL COLUMN ON SIDES - INCLUDING ACCESSORIES, ANCHORING & GROUT - INCLUDING LABOR & EQUIPMENT FOR ERECTION
K-27 | LIGHT WEIGHT CONCRETE PRECAST INSULATED SANDWICH PANELS (SIPOREX PANEL) - 600(H) X 1200(L) THK. 250mm - 2 COATS OF TEXTURED WATERPROOF PAINT (EXT) - 2 COATS OF PAINT (INT)
L-01 | FIRE RESIST. STEEL DOOR - 0.5 HOUR FIRE DOOR - INCLUDING UL CERTIFICATION - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT. - INCLUDING SIGN PLATE OF ANODIZED ALUMINIUM OR STAINLESS STEEL - HYDRAULIC DOOR CLOSERS SHALL BE FITTED TO ALL DOORS IN AIR- CONDITIONED AREA - DUST PROOF(FOR EXT.DOOR)
L-02 | FIRE RESIST. STEEL DOOR - 1.5 HOUR FIRE DOOR - INCLUDING UL CERTIFICATION - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT. - INCLUDING SIGN PLATE OF ANODIZED ALUMINIUM OR STAINLESS STEEL - HYDRAULIC DOOR CLOSERS SHALL BE FITTED TO ALL DOORS IN AIR- CONDITIONED AREA - DUST PROOF(FOR EXT.DOOR)
L-03 | NORMAL STEEL DOOR - DOOR FRAME : 1.6mm THK GALVANOZED STEEL PLATER - DOOR : 1.2mm THK GALVANIZED STEEL PLATE - INSULATION : 50mm THK GALSS WOOL - COATING : EPOXY PRIMER 75μm + POLYURETHANE PAINT 50 μm - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT. - INCLUDING SIGN PLATE OF ANODIZED ALUMINIUM OR STAINLESS STEEL - HYDRAULIC DOOR CLOSERS SHALL BE FITTED TO ALL DOORS IN AIR- CONDITIONED AREA - DUST PROOF(FOR EXT.DOOR)
L-04 | ROLL-UP SHUTTER DOOR - ELECTRICALLY OPERATED TYPE W/ MANUAL OPERATION - MIN. 1.2T ANODIZED ALUMINUM OR GALVANIZED STEEL SHEET - INCLUDING ALL HARDWARE - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING SIDE GUIDE RAIL AND BOTTOM RAIL AND OTHER ACCESSARIES INCLUDING ESCAPE DOOR AND WIND LOCK IF REQUIRED - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING SHUTTER BOX
L-05 | FOLDING DOOR - TOP HUNG FOLDING HEAVY DUTY TYPE - THK. 1.5mm STEEL SHEET W/ INSULATED DOUBLE SKIN - THK. 60mm (MIN.) - GALAVINIZED - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT, PANIC LATCH. ETC.) - INCLUDING PEDESTRIAN DOOR INTERGRADED IN THE FOLDING DOOR
L-06 | AUTOMATIC SLIDING DOOR -THK. 10mm TEMPERED SAFETY GLASS - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT, PANIC LATCH. ETC.) - INCLUDING STAINLESS STEEL FRAME AT TOP & BOTTOM ONLY - INCLUDING AUTOMATIC SYSTEM
L-07 | STAINLESS STEEL DOOR (GLASS SWING DOOR) - DOOR : THK. 12mm TEMPERED SAFETY GLASS - FIXED GLASS : THK. 8mm TEMPERED SAFETY GLASS - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT, PANIC LATCH. ETC.) - INCLUDING STAINLESS STEEL FRAME - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME
L-08 | TIMBER FLUSH DOOR - THK. 42mm (9 PLIES) - FACE VENEER : 12 mm DRIED WOOD, 5 mm PLYWOOD - INSIDE VENEER : 3 PLY PANEL W/ EACH 1.4mm THK. - WOOD LEAF FRAME : 65x32mm, 25x45mm - DOOR FRAME : STEEL FRAME W/THK. 40mm W/ RUBBER SEALING - SOUND INSULATION : 35~40 Db - INCLUDING ALL HARDWARES AND ACCESSARIES REQUIRED ACCORDING to ITB OR PROJECT REQUIREMENT (SUCH as PANIC BAR, LOCKSET, HINGES, DOOR CLOSER, ETC.) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - ALL TIMBER SHALL BE OF EITHER GRADE ‘A’ OR GRADE ‘B’ TIMBER
L-09 | PLYWOOD DOOR - THK. 42mm (9 PLIES) - FACE VENEER : 12 mm DRIED WOOD, 5 mm PLYWOOD - INSIDE VENEER : 3 PLY PANEL W/ EACH 1.4mm THK. - WOOD LEAF FRAME : 65x32mm, 25x45mm - DOOR FRAME : STEEL FRAME W/THK. 40mm W/ RUBBER SEALING - SOUND INSULATION : 35~40 Db - INCLUDING ALL HARDWARES AND ACCESSARIES REQUIRED ACCORDING to ITB OR PROJECT REQUIREMENT (SUCH as PANIC BAR, LOCKSET, HINGES, DOOR CLOSER, ETC.) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME
L-10 | HANGER DOOR - INCLUDING ALL HARDWARES - INCLUDING RAIL
L-11 | MASTER- KEY SYSTEM - GRAND MASTER KEYS : 10 NOS - MASTER KEYS ; 10 NOS. PER EACH GROUP - SUB-MASTER KEYS ; 5 NOS. PER EACH BLDG - SINGLE KEYS ; 3 NOS. PER EACH DOOR - BLANK KEYS : 4 NOS. PER EACH BLDG - FOR WHOLE PLANT - INCLUDING PROFILE CYLINDER - MASTER KEY SYSTEM SHALL BE SUBJECT TO CONTRACTOR'S APPROVAL
M-01 | ALUMINUM WINDOW - ANODIZED HEAVY DUTY COATING - DOUBLE SOLAR REFLECTIVE GLASS (THK. 6mm) W/ 12mm AIR SPACE - INCLUDING ALL HARDWARES STAINLESS STEEL (SUCH AS LOCKSET AND CRESENT) - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING MORTAR FILLING INTO WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY ) - INCLUDING AL.SUB-FRAME & NYLON COATED INSECT SCREEN AT OPEN AREA ONLY( EXT. WINDOW ONLY )
M-02 | ALUMINUM WINDOW - ANODIZED HEAVY DUTY COATING - DOUBLE GLASS (THK. 6mm) W/ 12mm AIR SPACE - INCLUDING ALUMINUM ACCORDION SHUTER FOR COVERING OF WINDOW - INCLUDING ALL HARDWARES STAINLESS STEEL (SUCH AS LOCKSET AND CRESENT) - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING MORTAR FILLING INTO WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY ) - INCLUDING AL.SUB-FRAME & NYLON COATED INSECT SCREEN AT OPEN AREA ONLY( EXT. WINDOW ONLY )
M-03 | ALUMINUM WINDOW - ANODIZED HEAVY DUTY COATING - SINGLE GLASS (THK. 6mm) - INCLUDING ALL HARDWARES STAINLESS STEEL (SUCH AS LOCKSET AND CRESENT) - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING MORTAR FILLING INTO WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY ) - INCLUDING AL.SUB-FRAME & NYLON COATED INSECT SCREEN AT OPEN AREA ONLY( EXT. WINDOW ONLY )
M-04 | ALUMINUM WINDOW - SINGLEE GLASS (TEMPERED) - ANODIZED HEAVY DUTY COATING - SINGLE GLASS (THK. 6mm) - SOLARCOOL GRAYLITE® FLOAT GLASS - INCLUDING ALL HARDWARES STAINLESS STEEL (SUCH AS LOCKSET AND CRESENT) - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING MORTAR FILLING INTO WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY ) - INCLUDING AL.SUB-FRAME & NYLON COATED INSECT SCREEN AT OPEN AREA ONLY( EXT. WINDOW ONLY )
M-05 | FIRE RESIST. WINDOW - ANODIZED HEAVY DUTY COATING - GLAZING AS PER TECH. SPEC. - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING MORTAR FILLING INTO WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY ) - INCLUDING AL.SUB-FRAME & NYLON COATED INSECT SCREEN AT OPEN AREA ONLY( EXT. WINDOW ONLY )
M-06 | ALUMINIUM GLAZED WALL - ANODIZED HEAVY DUTY COATING - HARDWARE : STAINLESS STEEL, DOUBLE GLASS (THK. 6mm) W/ 12mm AIR SPACE - INCLUDING ALL GLAZING & HARDWARES - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY )
M-07 | ALUMINIUM LOUVER - ANODIZED HEAVY DUTY COATING - W/ ENCLOSING FRAME - STAINLESS STEEL FLY SCREENS - BIRD GUARD ON THE INSIDE - AS PER AMCA 540 & AMCA 550 - MIN. & MAX. OPENING SIZE IN ANY DIRECTION: > 1/4 INCH AND NOT > 1 INCH
M-08 | ALUMINUM SUNSHADE LOUVER - ANODIZED HEAVY DUTY COATING - SUNSHADE LOUVER - THK.2x200 BLADE - AL. ANODIZED FRAME SLAT & FLASHING - ALL ACCESSORIES INCLUDING AL. BRACKET, SUPPORT, FLASHING, ETC. - LOUVER TO BE INSTALLED AT 40 cm IN FRONT OF WINDOW
M-09 | ALUMINIUM STRIP WINDOW FOR U-SHAPE GLAZING - INCLUDING U-SHAPE PUTTYLESS DOUBLE GLAZING - INCLUDING ALUMINIUM WINDOW SILL - INCLUDING AL. WINDOW FRAME AND SEALANT AT ALL JOINTS
N-01 | MISC. STEEL WORK (GALVANIZED) - FOR EMBEDDED PLATE(FOR PIT COVER), SLEEVE, CORNER ANGLE FOR TRENCH COVER AND CHK'D PLATE - HOT DIP GALVANIZED (4 MILS, 100 MICRONS) - STEEL : ASTM A36, ASTM A572 GRADE 50 / KS D 3515 SM355 - INCLUDING ERECTION & SHOP DWG. - INCLUDING ERECTION MATERIAL, EQUIPMENT (HIGH STRENGTH BOLT/NUT/WASHER, ACCESSORIES) - INCLUDING PAINTING, TOUCH-UP PAINTING & GRINDING, SCAFFOLDING WORK (IF NECESSARY) - INCLUDING TESTING AS PER TECH.SPEC. - INCLUDING FIXING ANGLE AT MISC STEEL WORK
N-02 | MISC. STEEL WORK (PAINTED) - FOR EMBEDDED PLATE(FOR PIT COVER), SLEEVE, CORNER ANGLE FOR TRENCH COVER AND CHK'D PLATE - STEEL : ASTM A36, ASTM A572 GRADE 50 - PAINT : BLASTING SIS SA 2 1/2 OR EQUIVALENT, 1 COAT ZINC EPOXY PRIMER (80㎛) 1 COAT EPOXY HIGH SOLID (80㎛) - DFT : TOTAL 160㎛
N-03 | GALV. STEEL GRATING - FOR TRENCH COVER, PLATFORM, STAIR LANDING & TREAD ETC. - HOT DIP GALVANIZED (4 MILS, 100 MICRONS) - BEARING BAR : DEPTH 32 OR 40mm x 5mm AT 30 MM C/C - CROSS BAR : 6mm Square Bar AT 100 MM C/C - STEEL : KS D 3503 SS275 - INCLUDING TOE PLATE, STAIR TREAD, BOLT OR CLIP - INCLUDING 4 NOS. GRATING CLAMP PER PANEL - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING FIXING ANGLE, ANCHOR BOLT FOR FIXING ANGLE - INCLUDING AS PER APPROVED SHOP DRAWING
N-04 | CHECKERED PLATE - FOR TRENCH COVER, PLATFORM, ETC. - HOT DIP GALVANIZED (4 MILS, 100 MICRONS) - THK. 6mm - RAISED DIAMOND PATTERN - INCLUDING FIXING BY COUNTERSUNK, FLAT HEAD BOLT OR SCREW - INCLUDING DRAIN & LIFTING HOLE AS PER APPROVED SHOP DRAWING - INCLUDING FIXING ANGLE, ANCHOR BOLT FOR FIXING ANGLE - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-05 | GALV. EXPANDED METAL LATH - FOR ROOF WALKWAY - HOT DIP GALVANIZED (4 MILS, 100 MICRONS) - FACTORY APPLIED FINISH COATING - INCLUDING EDGE FRAME,FIXING CLAMP - INCLUDING FIXING ANGLE, ANCHOR BOLT FOR FIXING ANGLE - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-06 | GALV. MESH SCREEN & DOOR - FOR CABLE ROOM, TR AREA - HOT DIP GALVANIZED (4 MILS, 100 MICRONS) - FACTORY APPLIED FINISH COATING - REMOVABLE TYPE - INCLUDING GALV. MESH DOOR, BIRD SCREEN, MESH PANEL FRAMES, - INCLUDING ALL FIXING, ACCESSORIES, HARDWARE AND PAD LOCK - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-07 | ALUMINIUM SHEET - THK. 3 mm AL. SHEET - DOUBLE PROFILE THK. 75mm - INCLUDING ALL ACCESSORIES FOR FIXING, SEALANT, ETC. - INDLUD'G FIXING & JOINTING - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-08 | STEEL PIPE HANDRAIL (STAND TYPE) - RAILING PIPE : INTERNAL DIA. Φ32mm, THK.4 mm - TOP RAIL HEIGHT : WALKWAY & PLATFORM - 1100 mm : STAIR - 900 mm - 2 INTEMEDIATE HORIZONTAL RAILS - PIPE POST SPACING @ 1200 mm - HOT DIP GALVANIZED AND INORGANIC ETHYL ZINC SILICATE(1COAT) - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING TOE PLATE OR CHANNEL - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-09 | STEEL PIPE HANDRAIL (REMOVABLE TYPE) - RAILING PIPE : INTERNAL DIA. Φ32mm, THK.4 mm - PIPE POST SPACING @ 1200 mm - HOT DIP GALVANIZED AND INORGANIC ETHYL ZINC SILICATE(1COAT) - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING
N-10 | STAINLESS STEEL HANDRAIL - AS PER ASTM A500-01a & ASTM A53/A53M-01 - ROUND OR SQUARE : POST - DIA. Φ32mm / SQUARE □40, THK.4 mm : INTERMEDIATE RAIL-DIA. Φ32mm, SQUARE□30 - TOP RAIL HEIGHT : 900mm - 2 INTERMEDIATE HORIZONTAL RAILS - PIPE POST SPACING @ 1200 mm - INCLUDING FIXING AND ACCESSORIES - INCLUDING TOE PLATE OR CHANNEL - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-11 | STAINLESS STEEL HANDRAIL (WOODEN GRIP) - AS PER ASTM A500-01a & ASTM A53/A53M-01 - ROUND OR SQUARE : POST - DIA. Φ32mm / SQUARE □40, THK.4 mm : INTERMEDIATE RAIL-DIA. Φ32mm, SQUARE□30 - TOP RAIL HEIGHT : 900mm - 2 INTERMEDIATE HORIZONTAL RAILS - PIPE POST SPACING @ 1200 mm - 45x150mm, HARDWOOD GRIP
N-12 | LADDER (H ≤ 2.5m) - LADDER : WIDTH - 400 mm : SIDE RAIL - ANGLE L60/8 or L75/10 : RUNG - Φ25 RIBBED BAR @280 - HOT DIP GALVANIZED AND INORGANIC ETHYL ZINC SILICATE(1COAT) - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-13 | CAGE LADDER (2.5m < H ≤ 10m) - LADDER : WIDTH - 400 mm : SIDE RAIL - ANGLE L60/8 or L75/10 : RUNG - Φ25 RIBBED BAR @280 - CAGE : DIAMETER 700 mm : CAGES STARTING 2.5m ABOVE G.L OR F.L : HORIZONTAL HOOP - F.B 55x6 mm @1.5m : VERTICAL HOOP - 5 EQUALLY SPACED - HOT DIP GALVANIZED AND INORGANIC ETHYL ZINC SILICATE(1COAT) - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-14 | CAGE LADDER (10.0m < H) - LADDER : WIDTH - 400 mm : SIDE RAIL - ANGLE L60/8 or L75/10 : RUNG - Φ25 RIBBED BAR @280 - CAGE : DIAMETER 700 mm : CAGES STARTING 2.5m ABOVE G.L OR F.L : HORIZONTAL HOOP - F.B 55x6 mm @1.5m : VERTICAL HOOP - 5 EQUALLY SPACED - HOT DIP GALVANIZED AND INORGANIC ETHYL ZINC SILICATE(1COAT) - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-15 | BOLLARD - REMOVABLE(DE-MOUNTED) - STEEL PIPE H 1000MM Φ 150 MM & REMOVAL - STEEL PIPE FILLIED CONCRETE & FOUNDATION - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-16 | BOLLARD -FIXED - STEEL PIPE H 1000MM Φ 150 MM & REMOVAL - STEEL PIPE FILLIED CONCRETE & FOUNDATION - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-17 | DOWEL BAR - PLAIN STEEL DOWEL ROUND BARS DIA. 20mm, L 600mm, @300 - FOR SEPARATION JOINT - INCLUDING DOWEL CAP FILLED WITH COMPRESSIBLE MATERIAL FOR SLIP PURPOSE
N-18 | STEEL FORM - FOR CEP(Condensate Extraction Pump) STEEL PIPE CAN STRUCTURE FOR STEAM TURBINE BUILDING - STEEL PIPE DIA 1000mm x 10t, L=9m - STEEL PLATE 1000 x 1000 x 10t WITH ANCHOR BOLT - INCLUDING ANCHORING - INCLUDING TAR EPOXY COATING (250 micron) - INCLUDING FRAME AND ACCESSORIES - INCLUDING WEDLING STEEL PIPE ON STEEL PLATE
O-01 | ISOLATION JOINT - FOR AROUND TG FDN. - THK. 50 x 50 OIL RESISTANT SEALANT W/ BACKING ROD FORM - AS PER BS 6093 - INCLUDING PREMOULDED FILLER
O-02 | EXPANSION JOINT - FOR EXT. / INT. FLOOR AND WALL - THK. 25 x 25 OIL RESISTANT SEALANT W/ BACKING ROD FORM - AS PER BS 6093 - INCLUDING PREMOULDED FILLER
O-03 | EXP. JOINT COVER W=200 - FOR 25mm FLOOR EXP. JOINT COVER - INCLUDING FIXING BY NON-CORRODING & HEAVY DUTY ALUMINUM PROFILE WITH RUBBER INSERT - INCLUDING PREMOULDED FILLER
O-04 | SEPARATION JOINT - FOR AROUND GRADE SLAB - THK. 12 x 12 / SEALANT W/ BACKING ROD FORM - AS PER BS 6093 - INCLUDING PREMOULDED FILLER
O-05 | CONTRACTION JOINT (FOR FLOOR) - FOR FLOOR OF HEAVY DUTY TRAFFIC - THK. 6 x 6, OIL RESISTANT SEALANT W/ BACKING ROD FORM - INCLUDING SAW CUTTING OF CONC.
O-06 | CONTRACTION JOINT (FOR WALL) - FOR VERTICAL & HOR. WALL JOINT - THK.10 x 10, 2-PART POLYSULPHIDE BASED SEALANT W/ BACKING ROD FORM
O-07 | PREMOULDED FILLER - THK. 50mm - FOR ISOLATION JOINT
O-08 | PREMOULDED FILLER - THK. 25mm - FOR EXPANSION JOINT
O-09 | PREMOULDED FILLER - THK. 12mm - FOR SEPARATION JOINT
O-10 | EMERGENCY MANHOLE COVER - POWER OPERATED - SIZE 800 x 800 - INCLUDING FRAME & ALL ACCESSORIES
O-11 | FIRE RATED MANHOLE COVER - 1.5 HOURS FIRE RESISTANCE - SIZE 800 x 800
O-12 | CORNER PROTECTION H=1.2M - PLASTIC OR ALUMINUM - PROTECTION OF EXPOSED EDGE OF CONC./ PLASTER UP TO 1.2M FROM FLOOR LEVEL
O-13 | STAIR NOSING - AL W/ PLASTIC OR RUBBER INSERT - W=50mm - INCLUDING ALL ANCHORS
O-14 | BLIND - INCLUDING BLIND BOX AND ALL HARDWARES
O-15 | ROOM DESIGNATION SIGN - INTERNAL / EXTERNAL - SIZE : 260 x 100 x 4mm - ALUMINIUM ANODIZED PLATE W/ SPECIALLY TREATED SURFACE - 4 HORIZONTAL GROOVES, 10mm WIDE AT LOWER END OF PLATE TO TAKE PLASTIC STRIP - DESIGNATION PRINTED IN ENGLISH & LOCAL LANGUAGE - ROOM NUMBER ENGRAVED AT UPPER PORT - INCLUDING FIXING BY NON-CORRODING SCREW ON WALL
O-16 | SHOWER TRAY - ACRYLIC, SIZE : 900x900x150, FOR SHOWER - INCLUDING FIXING & ACCESSORIES
O-17 | VANITY TOP - L=750MM (1 BOWL) - ACRYLIC, 4" FRONT/BACK SPLASH - FOR TOILET, WITHOUT BOWL - INCLUDING FIXING & ACCESSORIES
O-18 | VANITY TOP - L=1500MM (2 BOWL) - ACRYLIC, 4" FRONT/BACK SPLASH - FOR TOILET, WITHOUT BOWL
O-19 | MIRROR - 750Wx800Hx5T - FOR TOILET - INCLUDING FIXING & ACCESSORIES
O-20 | MIRROR - 1500Wx800Hx5T - FOR TOILET - INCLUDING FIXING & ACCESSORIES
O-21 | TOWEL BAR - STAINLESS STEEL - INCLUDING FIXING & ACCESSORIES
O-22 | SOAP DISPENSER - STAINLESS STEEL - INCLUDING FIXING & ACCESSORIES
O-23 | ROLLER PAPER HOLDER - STAINLESS STEEL - BALL-JOINT TYPE - INCLUDING FIXING & ACCESSORIES
O-24 | NON-SLIP NOSING - STAINLESS STEEL NON-SLIP NOSING - FOR COVERING OF EXPOSED EDGE FOR P.V.C. TILE - INCLUDING FIXING BY SCREW
O-25 | SST'L DIVIDING STRIP - GRADE 316L OR BETTER - EMBEDDED ITEMS SUCH AS PLATE, BENT PLATE, ANCHOR BOLTS & NUTS, ANGLE, SLEEVE, FIXING ELEMENTS, ETC. - FOR OUTSIDE CONDITION - FOR INSIDE CONDITION W/ SEA WATER WETTING, CHEMICALS, ETC. - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
P-01 | RCC PAVE PLINTH PROTECTION (FOOTWAY) - THK. 100MM, CONCRETE WIDE 1500MM - SURROUNDING THE BUILDING - INCLUDING ONE LAYER OF WIRE MESH REINFORCEMENT
P-02 | INTERLOCKING PAVING - BLOCK THK. 80mm (MIN.) - SAND BEDDING THK. 50mm - COMPACTION THK. 300mm - COMPACTION OF FORMATION SAME AS ROAD - INCLUDING CONCRETE KERB AT EDGE - CONFORMING TO ASTM C 936, HEAVY/MEDIUM DUTY TYPE - LEVELING BASE WITH SOIL STERILIZER - LAYING ON SAND BEDDING OVER AN AGGREGATE BASE/SUB-BASE MATERIAL - COLOUR MATCHING WITH ADJACENT BUILDINGS
P-03 | CHAIN LINK FENCE - 2.4M HIGH GALVANIZED STEEL WIRE PVC - INCLUDING APPROXIMATELY 50mm DIAMOND MESH PATTERN AND 45 DEGREE TO VERTICAL - MIN. BREAKING STRENGTH OF MESH WIRE : 585kg - MIN. THICKNESS OF PVC : 0.38mm - TO KEEP COLOUR WITH GREEN - INCLUDING FOUNDATION
P-04 | CHAIN LINK GATE - HEIGHT 2.4m / WIDTH 6.0m - FOR GPRS AREA, OUTDOOR STORAGE AREA - DOUBLE WING GATE - PLASTIC COATED GALVANIZED CHAIN LINK MESH ON A PLASTIC COATED GALVANIZED STEEL FRAME - INCLUDING THREE STRANDS OF GALVANIZED BARBED WIRE ACROSS THE TOP ON CRANKED GALVANZIED EXTENSION POSTS. - INCLUDING A VERTICAL DROP BOLT ON EACH LEAF - INCLUDING ALL HARDWARE AND PAD LOCK (GALVANIZED) - INCLUDING FOUNDATION
Q-01 | DRIVEN PC PILE - SQUARE 400 X 400 mm, L =20m - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE V - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK
Q-02 | DRIVEN PHC PILE (D400) - 말뚝길이 : 본당 40m - PHC 말뚝 자재비, 천공, 항타, 두부보강, 두부정리, 말뚝이음, 하차비 (Φ400x65t) 포함 - 시멘트 페이스트 채움 (W/C=83%) 포함 - 케이싱 자재비 (강관 457.2x9t, 99.5kg/m) 포함 - 고재처리 (케이싱) 포함 - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE V - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK
Q-03 | DRIVEN PHC PILE (D500) - 말뚝길이 : 본당 40m - PHC 말뚝 자재비, 천공, 항타, 두부보강, 두부정리, 말뚝이음, 하차비 (Φ500x80t) 포함 - 시멘트 페이스트 채움 (W/C=83%) 포함 - 케이싱 자재비 (강관 558.8x9t, 122.0kg/m) 포함 - 고재처리 (케이싱) 포함 - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE V - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK
Q-04 | DRIVEN PHC PILE (D600) - 말뚝길이 : 본당 40m - PHC 말뚝 자재비, 천공, 항타, 두부보강, 두부정리, 말뚝이음, 하차비 (Φ600x90t) 포함 - 시멘트 페이스트 채움 (W/C=83%) 포함 - 케이싱 자재비 (강관 700.0x9t, 153.0kg/m) 포함 - 고재처리 (케이싱) 포함 - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE V - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK
Q-05 | DRIVEN STEEL PILE - STEEL PILE DIA 609.6 x T12MM, L=20m - INSTALLATION TYPE FOR PILE : DRIVING - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE JONTS, TOES, HEAD REINFORCEMENT IF REQUIRED - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK
Q-06 | BORING PC PILE - DIA 400mm, L =20m - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE I - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK - INCULDING PRE-BORING AND ALL ACCESSORY WORK
Q-07 | BORED CAST IN-SITU PILE - 말뚝길이 : 본당 40m - DIA 600mm (STRUCTURAL PROPERTIES : GRADE 80 AND CLASS C) - 현장타설 말뚝 천공 / 말뚝 조성(철근망 근입, 콘크리트 타설) / 말뚝 두부보강 / 말뚝 두부정리 포함 - SLURY 공급설비, SLIME처리, CASING설치 및 인발 등 부대공사 포함 - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE I - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK - INCULDING PRE-BORING AND ALL ACCESSORY WORK
Q-08 | BORED CAST IN-SITU PILE - DIA 400mm, L =20m - INCLUDING MOBILIZATION, SHIFTING AND DEMOBILIZATION OF AUGER / PILE RIG / CRANE / ANY RELATED MACHINE FOR THE PILING WORK. - SOCKETING INTO ROCK LAYER - INCLUDING MATERIAL LOADING / UNLOADING / CONTROL / HANDLING - INCLUDING LEADING. LIFTING, INSTALLATION OF MATERIALS - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING ALL NECESSARY TESTS / CERTIFICATES - ALL MATERIALS AND WORKS INCLUDING DRILLING, CONCRETING AND REINFORCEMENT WORKS AND ETC - INCLUDING THE FABRICATION AND INSTALLATION OF REINFORCEMENT CAGE - TEMPORARY STEEL CASING TO STABILIZE THE BOREHOLE - INCLUDING VERTICALITY CHECK FOR ALL PILES - INCLUDING TREATMENT AND DISPOSAL OF SLIME, MUCK AND SOIL DURING DRILLING - SONIC LOGGING TUBES : FOUR (4) STEEL PIPES OF INTERNAL DIA. NOT LESS THAN 50mm FOR ENTIRE LENGTH OF PILE TO BE INSTALLED IN ALL PILES - INCLUDING PILE HEAD CUTTING AT PILE CUT OFF LEVEL AND CONNECTION WITH PILE CAP - CONCRETE ASTM C150 TYPE V, f'c = 35MPa - RE-BAR ASTM A615 GRADE 60 - INCLUDING PVC PIPE FOR CAPPING RE-BAR TO SERVE PILE HEAD CUTTING'S CONVENIENCE - INCLUDING ANY TEMPORARY ASSOCIATED WORK
Q-09 | BORED CAST IN-SITU PILE - 말뚝길이 : 본당 40m - DIA 800mm (STRUCTURAL PROPERTIES : GRADE 80 AND CLASS C) - 현장타설 말뚝 천공 / 말뚝 조성(철근망 근입, 콘크리트 타설) / 말뚝 두부보강 / 말뚝 두부정리 포함 - SLURY 공급설비, SLIME처리, CASING설치 및 인발 등 부대공사 포함 - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE I - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK - INCULDING PRE-BORING AND ALL ACCESSORY WORK
Q-10 | BORED CAST IN-SITU PILE - 말뚝길이 : 본당 40m - DIA 1000mm, (STRUCTURAL PROPERTIES : GRADE 80 AND CLASS C) - 현장타설 말뚝 천공 / 말뚝 조성(철근망 근입, 콘크리트 타설) / 말뚝 두부보강 / 말뚝 두부정리 포함 - SLURY 공급설비, SLIME처리, CASING설치 및 인발 등 부대공사 포함 - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE I - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK - INCULDING PRE-BORING AND ALL ACCESSORY WORK
Q-11 | SHEET PILE - INSTALLATION TYPE FOR PILE : DRIVEN - U-TYPE SHEET PILE (SP-IV 400 X 170 X15.5) - L=8M - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING EQUIPMENT ASSEMBLING & DISMANTLING COST - INCLUDING ANY TEMPORARY ASSOCIATED WORK - REPLACEMENT OF REJECTION PILES AT NO EXTRA - INCLUDING WALE, STRUT, POST PILE, JACK
R-01 | HARD WOOD DESK - 1600 x 700 x 800 mm - COMMON DESK - INCLUDING DRAWERS (MATCHING THE DESK) & GLASS TOP
R-02 | HARD WOOD DESK - 1300 x 1300 x 800 mm - CANTEEN TABLE
R-03 | SIDE TABLE - 1600 x 500 mm - INCLUDING DRAWERS (MATCHING THE DESK) & GLASS TOP
R-04 | CHAIR - HIGH BACKED EXECUTIVE - ADJUSTABLE SWIVEL
R-05 | CHAIR - ADJUSTABLE SWIVEL
R-06 | CANTEEN CHAIR - NON-SWIVEL
R-07 | COUCH - REST ROOM
R-08 | VISITOR - NON-SWIVEL
R-09 | SMALL FOR COMPUTER TABLE -SWIVEL
R-10 | CORRESPONDENCE TRAY
R-11 | WASTE BIN
R-12 | WALL BOARD
R-13 | SECRETARIAL WORK STATION
R-14 | COMPUTER TABLE - 700 x 1600 x 800 mm
R-15 | SIDE STORAGE UNIT - 800 x 425 x 725 mm
R-16 | CONFERENCE ROOM PACKAGE - TABLE, CHAIRS, WHITE BOARD - LAMINATED OR WOOD VENEER - HIGH QUALITY - LARGE TABLE FOR 20 PERSON + 20 SEATING - 1 BEAM PROJECTOR & 1 SCREEN - SIZE TO SUIT THE CONFERENCE ROOM
R-17 | MANAGEMENT OFFICE PACKAGE - PLANT MANAGER OFFICE - TABLE, SIDE TABLE, STDE STORAGE UNIT & HIGH BACKED CHAIR - SPECIAL SELECTION OF HIGHER QUALITY MODERN OFFICE PACKAGE
R-18 | TRAINING ROOM PACKAGE - CHAIR WITH FOLDING TABLE, WHITE BOARD - SEATING FOR 40 PERSONS - TO SUIT THE TRAINING ROOM
R-19 | OFFICE STORAGE ROOM PACKAGE - FILING CABINETS, STORAGE SHELVES, DRAWING HOLDERS - TO SUIT THE STORAGE ROOM
R-20 | COFFEE SHOP & KITCHEN - 2 GAS STOVE W/ 4 BURNER & 1 OVEN - 3 SECTIONAL WASHING TANK WITH RACK - 1 REFRIDGERATING CABINET (1600 x 725 x 1950 mm) - 4 PROCESS TABLE (1300 x 800 x 860 mm) - STATIONARY RACK (1500 x 500 x 1200 mm) - COUNTER FOR SERVER & TRAY
R-21 | RECEPTION AREA - RECEPTION DESK, SOFA SEATS & COFFEE TABLE - FOR 6~10 PERSONS -TO SUIT DESIGNATED AREAS
R-22 | BUILT-IN CUPBOARD - FOR OFFICE - HEIGHT : UP TO CEILING (≒CUPBOARD 2.3m+COVER STRIP 0.5m) - SIZE : 500 x 2600 x 1800 mm - COMPONENTS : CUPBOARDS, WARDROBES, SHELVES & DRAWS -COMPONENT DESIGN BY VENDOR
R-23 | TEA KITCHENS - COOKTOP & HOOD - CUPBOARD W/STAINLESS STEEL SINK
R-24 | OTHERS(FURNITURE) - WOOD LOCKER (500 x 500 x 1800 mm)

## Spec Comparison
7.4.3 BOQ
C. MATERIAL BRIEF SPECIFICATION
[P-현대차CCPP] 현대자동차 울산공장 복합화력 발전소, Rev. No : 6 ]
Discipline : Architecture | [8 empty] | 2021-07-29
No. | WBS Name | Brief Spec. | 금액Ratio | 현대차 Spec (2021.5월 최종금액, 건축BM Rev.3 - Rev.8과 동일) |  |  |  | 안동 Spec (안동 복합화력 발전사업) | 대구 Spec (대구 친환경에너지 개선사업 주기기 구매사업)
[5 empty] | 영문 Proposal Spec. (2021.01) | 한글 기술기준서 (2021.11) PT파일 | 현대차 자체 Spec |  |  | 회의결과
B-01 | EXCAVATION | COMMON SOIL BELOW 2M DEPTH | 0.04% | EXCAVATION COMMON SOIL - REGARDLESS of EXCAVATION DEPTH AND METHOD (MACHINERY OR HAND DIGGING) - INCLUDING SURVEY, MARKING & LEVELING - INCLUDING DEWATERING WITH a PROVISION of SUMP AND PUMP, IF REQUIRED - INCLUDING SAFETY PRECAUTION SUCH as STRUTTING, SHEETING AND BRACING - INCLUDING PROTECTION MEASURES to EXISTING & NEW STRUCTURE / UTILITIES ENCOUNTERED DURING THE WORK - INCLUDING COMPACTION AT EXCAVATED LEVEL - INCLUDING TEST(PLATE LOAD TEST) BENEATH FOUNDATION, IF REQUIRED | Compaction of sub grades and structural granular backfill materials shall be carried out within the range of  2% of the optimum moisture content to attain a maximum dry density of not less than 90~95%. |  |  | - | -
B-02 | BACKFILL (GENERAL FILL) | SELECTED EXCAVATED SOIL | 0.11% | BACK FILL -FILL MATERIALS - COMPACTION AT A LAYER OF 15cm MAX. - TO KEEP 95% OF MAX. DRY DENSITY IN ACCORDANCE WITH AASHTO T-180 METHOD D - BOTH SELECTED SOIL - INCLUDING ALL ACCESSARY EQUIPMENT SUCH AS VIBRATING ROLLER. RAMMER AND WATER SPRING WHEN REQUIRED |  |  | BACK FILL - COMPACTION AT A LAYER OF 20cm MAX. - TO KEEP 95% OF MAX. DRY DENSITY IN ACCORDANCE WITH KS F 2312 | BACK FILL - COMPACTION AT A LAYER OF 30cm MAX. - TO KEEP 95% OF MAX. DRY DENSITY IN ACCORDANCE WITH KS F 2312, ASTM D 1557 | BACK FILL - COMPACTION AT A LAYER OF 20cm MAX. - TO KEEP 95% OF MAX. DRY DENSITY IN ACCORDANCE WITH KS F 2312
B-03 |  |  |  | BACK FILL - IMPORTED SOIL (반입토) - MAX. SOIL PARTICLE SIZE : 50mm - COURSE-GRAINED SOIL - 다짐도 95% 이상(MODIFIED PROCTOR TEST)
B-04 | DISPOSAL | 부지내부사토 | 0.71% | DISPOSAL - 부지 내부 사토 (굴착토 재사용 목적) - DISPOSAL DISTANCE : 약 1.0km |  |  | - | - | -
B-05 |  |  |  | DISPOSAL - TO BE DISPOSED OUTSIDE THE PLANT BOUNDARY LIMIT(AT THE MUNICIPAL CORPORATION DESIGNATED DUMPING AREA) 부지 외부 사토 - DISPOSAL DISTANCE ( KM), 토취장, 사토장 위치 및 거리 확인 및 관련 인허가 획득은 계약자 역무임
B-06 |  |  |  | CRUSHED STONE W/ SAND FILL - INCLUDING COMPACTION, GRADING & TEST
B-07 |  |  |  | SOIL REPLACEMENT - SELECTED EXCAVATED AND SCREENED LIMESTONE ROCK MAX. SIEVE SIZE : 50mm - FOR BENEATH FOUNDATION - COMPACTION ONE LAYER OF MAX. 150mm AND MAX. 95% OF DRY DENSITY IN ACCORDANCE WITH ASTM D1557 - INCLUDING NECESSARY TEST AS PER SPEC. - THIS SHALL BE GOOD HARD WELL GRADED MATERIAL SCREENED AND CRUSHED AS NECESSARY TO LIE WITHIN THE GRADING ENVELOPE GIVEN BELOW WHEN TESTED IN ACCORDANCE WITH ASTM.
B-08 |  |  |  | COMPACTED SUB-BASE- STRUCTURE COMPACTION - FOR BENEATH SHALLOW FOUNDATION - THK. 0.5m ~ 1.0m -THE VALUE OF CBR NOT LESS THAN 35% (ASTM D 1883) -COMPACTION AT A LAYER OF 15cm MAX. AND 95% OF MAX. DRY DENSITY IN ACCORDANCE WITH ASTM D1557.
B-09 |  |  |  | GRAVEL LAYER - FOR COAL STORAGE SHED - DIA 100
B-10 |  |  |  | P.P. MAT - FOR COAL STORAGE SHED - THK. 5MM - POLYPROPYLENE MAT
B-11 |  |  |  | GRAVEL PAVING - FOR COAL STORAGE SHED - THK. 200MM - SUB-GRADE TO BE COMPACTED TO 95% OF MAX. DRY DENSITY AS PER ASTM D1557 - SPREADING MAX. Φ40 mm CRUSHED ROCKS OR GRAVELS - INCLUDING EXCAVATION & DISPOSAL
C-01 | LEAN CONCRETE | [UG] F'C = 18 MPA, W/CONSTRUCTION JOINT | 0.72% | LEAN CONCRETE - f'c=18 MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I - FOR LEAN CONC., BLINDING, SCREED, BACKFILL - INCLUDING MARKING, LEVELING, SCAFFOLDING, STAGING, CURING & TESTING - INCLUDING POURING & VIBRATING WORK - INCLUDING SMOOTH CONCRETE FINISHING - INCLUDING ALL CONSTRUCTION AND JOINTS WORK - INCLUDING LABOR & EQUIPMENT FOR ERECTION - INCLUDING CRACKED REPAIR & REQUIRED DAMAGED SURFACE - INCLUDING EMBEDDING MATERIALS IN CONCRETE AND TEMPLATE - INCLUDING TESTING, SUPERVISION, INSPECTION AT SITE - INCLUDING CONVEY OF CONCRETE FROM BATCH PLANT TO THE PLACE OF FINAL DEPOSIT - INCLUDING STORAGE/MAINTENANCE/PRESERVATION OF ALL CONCRETE MATERIALS AT SUBCONTRACTOR'S WAREHOUSE OR STORAGE AREA | F'C = 18 MPA | F'C = 18 MPA | LEAN CONCRETE(버림) - 공사 사양 설계 표준화 Spec. 없음 무근콘크리트 강도 18MPa > 21MPa | LEAN CONCRETE - f'c=14MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH KS L 5201, 1종 | LEAN CONCRETE - f'c=18MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH / Spec.없으나 국내 KS L 5201, 1종 적용 예상 | 14MPa적용검토
C-02 |  |  |  | LEAN CONCRETE - f'c=20 MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I - FOR LEAN CONC., BLINDING, SCREED, BACKFILL
C-03 |  |  |  | REINF. CONCRETE - f'c=25MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I - FOR GENERAL USE SUB STRUCTURE (ABOVE GROUND LEVEL)
C-04 |  |  |  | REINF. CONCRETE - f'c=25MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I - FOR GENERAL USE SUB STRUCTURE (UNDER GROUND LEVEL)
C-05 | CONCRETE | [AG] F'C = 24 MPA, W/CONSTRUCTION JOINT | 3.43% | REINF. CONCRETE - f'c=24MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I / KS L 5201, TYPE I - FOR GENERAL USE SUPER STRUCTURE (ABOVE GROUND LEVEL) | F'C = 24 MPA | F'C = 24 MPA | REINF. CONCRETE - f'c=24MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH KS L 5201, 1종~5종 *콘크리트 강도는 별도의 지침이 없는 한 fck=24MPa 강도 적용 (자동차 표준) | REINF. CONCRETE - f'c=24MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH KS L 5201, 1종 | REINF. CONCRETE - f'c=27MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH / Spec.없으나 국내 KS L 5201, 1종 적용 예상
C-06 | CONCRETE | [UG] F'C = 24 MPA, W/CONSTRUCTION JOINT | 2.89% | REINF. CONCRETE - f'c=24MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I / KS L 5201, TYPE I - FOR GENERAL USE SUB STRUCTURE (UNDER GROUND LEVEL) | F'C = 24 MPA | F'C = 24 MPA | REINF. CONCRETE - f'c=24MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH KS L 5201, 1종~5종 *콘크리트 강도는 별도의 지침이 없는 한 fck=24MPa 강도 적용 (자동차 표준) | REINF. CONCRETE - f'c=24MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH KS L 5201, 1종 | REINF. CONCRETE - f'c=27MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH / Spec.없으나 국내 KS L 5201, 1종 적용 예상
C-07 | CONCRETE (FOR MAJOR EQUIPMENT FDN) | [AG] F'C = 30 MPA, W/CONSTRUCTION JOINT (for TG) | 0.34% | REINF. CONCRETE - f'c=30MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I / KS L 5201, TYPE I - FOR TG FOUNDATION (ABOVE GROUND LEVEL) |  |  | REINF. CONCRETE - f'c=30MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH KS L 5201, 1종~5종 *콘크리트 강도는 별도의 지침이 없는 한 fck=24MPa 강도 적용 (자동차 표준) | REINF. CONCRETE - f'c=24MPa(MAT), 35MPa(Topping) (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH KS L 5201, 1종 | REINF. CONCRETE - f'c=30MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH / Spec.없으나 국내 KS L 5201, 1종 적용 예상 | 30MPa 적용
C-08 | CONCRETE (FOR MAJOR EQUIPMENT FDN) | [UG] F'C = 30 MPA, W/CONSTRUCTION JOINT (for TG, HRSG) | 1.38% | REINF. CONCRETE - f'c=30MPa(CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH ASTM C150, TYPE I / KS L 5201, TYPE I - FOR TG FOUNDATION & HRSG BUILDING & HRSG FOUNDATION (UNDER GROUND LEVEL) | F'C = 30 MPA | F'C = 30 MPA | REINF. CONCRETE - f'c=30MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH KS L 5201, 1종~5종 *콘크리트 강도는 별도의 지침이 없는 한 fck=24MPa 강도 적용 (자동차 표준) | REINF. CONCRETE - f'c=24MPa(MAT), 35MPa(Topping) (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH KS L 5201, 1종 | REINF. CONCRETE - f'c=30MPa (CYLINDER SPECIMEN) - ORDINARY PORTLAND CEMENT COMPLYING WITH / Spec.없으나 국내 KS L 5201, 1종 적용 예상
C-09 | TEMPERATURE CONTROL MONITORING | FOR MASS CONCRETE | 0.03% | TEMPERATURE CONTROL MONITORING - FOR MASS CONCRETE STRUCTURE(T=800mm OVER) & TG FOUNDATION - INCLUDING THERMO COUPLER, MONITORING & RECORD ACC. TO APPROVED MS |  |  | - | - | -
C-10 |  |  |  | HIGH YIELD DEFORMED BAR (EPOXY COATED) - ASTM A615 GRADE 60 (Fy=420MPa) - FUSION BONDED EPOXY COATED REINFORCING BAR(ASTM A775) - INCLUDING PRESSURE WELDED JOINT WORK WHERE NECESSARY & STRENGTH TEST - INCLUDING BAR SUPPORTS, TIE WIRES, SPACER, FABRICATED BAR MESH - INCLUDING RE-BAR SHOP DRAWING & BAR BENDING SCHEDULE - INCLUDING BAR BENDING & CUTTING - INCLUDING SLIP ROUND BAR AT SEPARATION JOINT - INCLUDING LABOR & EQUIPMENT - INCLUDING SITE INSPECTION
C-11 | REINFORCEMENT | HIGH YIELD DEFORMED BAR WORK (BLACK DEFORMED BARS) | 12.5% | HIGH YIELD DEFORMED BAR (BLACK DEFORMED BARS) - KS D 3504 SD400 - ASTM A615 GRADE 60 (Fy=420MPa) - BS 4449 : 2005 GRADE 500 - INCLUDING PRESSURE WELDED JOINT WORK WHERE NECESSARY & STRENGTH TEST - INCLUDING BAR SUPPORTS, TIE WIRES, SPACER, FABRICATED BAR MESH - INCLUDING RE-BAR SHOP DRAWING & BAR BENDING SCHEDULE - INCLUDING BAR BENDING & CUTTING - INCLUDING SLIP ROUND BAR AT SEPARATION JOINT | D10 to D16 : ASTM A615 G40 / KS D 3504, SD30A Over D 19 : ASTM A615 G60 / KS D 3504, SD40 | 400MPa, KS D 3504 | HIGH YIELD DEFORMED BAR (BLACK DEFORMED BARS) - KS D 3504 SD400 *기본 철근 강도는 fy=400 MPa 사용 (자동차 표준) | HIGH YIELD DEFORMED BAR (BLACK DEFORMED BARS) - KS D 3504 SD400 (D19 이상) - KS D 3504 SD300 (D10~D16) | HIGH YIELD DEFORMED BAR (BLACK DEFORMED BARS) - KS D 3504 SD400
C-12 | FORM WORKS(Fair faced form) | 1 TIMES, FAIR FACE FOR ABOVE GROUND | 10.95% | FAIR FACED FORM - FOR EXPOSED SUPERSTRUCTURE FORM FACE / PAINTED CONCRETE FORM FACE - FOR EQUIPMENT PLINTH AND FLOOR OPENING - COATED PLYWOOD THK. 18MM, 3 USE - INCLUDING, FORM TIE, ALL ACCESSORIES, SEALING OF FORM TIE HOLE, SEPARATOR & ANCHOR BOX OUT. - INCLUDING CHAMFER FOR EXPOSED EDGE - INCLUDING FLOOR AND WALL OPENING WORK & SLEEVE - INCLUDING BOXOUT FOR EQUIPMENT ANCHOR BOLT - INCLUDING LABOR & EQUIPMENT - INCLUDING FABRICATION / FORM INSTALL & REMOVAL - INCLUDING SHORING, SCAFFORDING AND SAFETY MEASURES - INCLUDING FORMWORK CALCULATION FOR STG PEDESTAL & TOP DECK (INCLUDING SHOP DRAWING) |  |  | FAIR FACED FORM - 공사 사양 설계 표준화 Spec. 없음 - KSF 3110(콘크리트 거푸집용 라왕합판), 12mm 내수합판 | 합판거푸집 - KS F 3110(콘크리트 거푸집용 합판)의 규정에 적합한 것이어야 함 | 합판거푸집 - 노출 치장콘크리트 부위, 원형 구조물 (2회) - 보 , 슬라브, 소형 구조물, 옥내기기기초(소형) (3회) | 거푸집 두께 12mm 적용
C-13 | FORM WORKS(Normal faced form) | 3 TIMES, GENERAL FOR UNDERGROUND | 1.49% | NORMAL FACED FORM - FOR UNDERGROUND CONCRETE - FOR HIDDEN SURFACE & APPLIED FINISHING CONCRETE FORM FACE (EXCLUDE PAINTED CONCRETE FORM FACE) - NORMAL PLYWOOD THK. 18MM, 6 USE |  |  | NORMAL FACED FORM - 공사 사양 설계 표준화 Spec. 없음 - KSF 3110(콘크리트 거푸집용 라왕합판), 12mm 내수합판 | 합판거푸집 - KS F 3110(콘크리트 거푸집용 합판)의 규정에 적합한 것이어야 함 | 합판거푸집 - 노출 치장콘크리트 부위, 원형 구조물 (2회) - 보 , 슬라브, 소형 구조물, 옥내기기기초(소형) (3회)
C-14 | SYSTEM FORM | FOR STEAM TURBINE GENERATOR FOUNATION TOP TABLE | 0.9% | SYSTEM FORM - FOR STEAM TURBINE GENERATOR FOUNATION TOP TABLE - HEAVY-DUTY FORMS, METAL FRAMED PLAYWOOD FORMS |  |  | SYSTEM FORM - 공사 사양 설계 표준화 Spec. 없음 | SYSTEM FORM - 기술기준서 Spec. 없음 | 시스템거푸집 - STG 기초
C-15 |  |  |  | FAIR FACED ROUND FORM FOR EXPOSED TO VIEW - INCLUDING, FORM TIE, ALL ACCESSORIES, SEALING OF FORM TIE HOLE, SEPARATOR & ANCHOR BOX OUT. - INCLUDING CHAMFER FOR EXPOSED EDGE - INCLUDING FLOOR AND WALL OPENING WORK & SLEEVE - INCLUDING BOXOUT FOR EQUIPMENT ANCHOR BOLT - INCLUDING LABOR & EQUIPMENT - INCLUDING FABRICATION / FORM INSTALL & REMOVAL - INCLUDING SHORING, SCAFFORDING AND SAFETY MEASURES
C-16 |  |  |  | NORMAL FACED ROUND FORM FOR HIDDEN SURFACE
C-17 |  |  |  | PRECAST CONC. COVER - THK.100 (SINGLE FABRIC) - FOR PIPE & CABLE TRENCH - INCLUDING LIFTING HANDLE, CORNER ANGLE
C-18 |  |  |  | PRECAST CONC. COVER - THK.150 (SINGLE FABRIC) - FOR PIPE & CABLE TRENCH - INCLUDING LIFTING HANDLE, CORNER ANGLE
C-19 |  |  |  | PRECAST CONC. COVER - THK.200 (DOUBLE FABRIC) '- FOR PIPE & CABLE TRENCH - INCLUDING LIFTING HANDLE, CORNER ANGLE
C-20 | PRECAST CONCRETE (THK.250) | FOR MISC PART SUCH AS PIT COVER, EQUIPEMENT PAD, ETC | 0.02% | PRECAST CONC. COVER - THK.250 (DOUBLE FABRIC) '- FOR PIPE & CABLE TRENCH - INCLUDING LIFTING HANDLE, CORNER ANGLE |  |  |  | - | -
D-01 | STEEL(KS D 3530 SSC275) | (FOR PURLIN & GIRTH) | 1.193% | STRUCTURAL STEEL (INDOOR STEEL / ROLL MEMBER) - KS D 3530 SSC275 - ASTM A36 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 or ISO 8501-1 Sa 2.5 Primer : Inorganic Zinc 75㎛ 2nd : High Build Polyamide Epoxy 100㎛ - DFT : TOTAL 175㎛ 􀁹 Common bolts : KS B 1002 or ASTM A307 􀁹 Nuts : KS B 1012 or ASTM A563 􀁹 Washer : KS B 1326 or ASTM F436 􀁹 Hot dip galvanized | 1) Structural Steel Surface (Indoor) : ISO 12944 Category C3 System A3.11 • Surface preparation : Sa 2½ (ISO 8501-1:1988)/SSPC-SP10 • Coat 1: Inorganic Zinc-rich Primer Single Coat System, DFT : min 75㎛ • Coat 2: High Build Epoxy Polyamide with satin or semi-gloss finish, DFT : min 100㎛ • Total DFT: Min 175㎛ | KS D 3530 SSC275 | STRUCTURAL STEEL * 일반적인 경우 공장건물은 지진력 저항시스템으로 “강구조 기준의 일반규정만을 만족하는 철골구조시스템“을 적용하여 설계되므로 반드시 내진 강재를 적용할 필요는 없음. * H-형강은 일반 구조용 압연강재인 SS275(구SS400)와 건축구조용 압연강재인 SN275(구SN400), 건축구조용 열간압연형강 SHN275(구SHN400)를 적용하고 기둥부재나 보 부재 중 H-500X200 이상인 경우 SM355, SN355, SHN355 강종 사용이 경제적임. - PAINT : 공사 사양 설계 표준화 Spec. 없음 | STRUCTURAL STEEL (INDOOR STEEL / ROLL MEMBER) - KS D 3530 SSC400 - PAINT : Surface Preparation : SSPC-SP-10 Primer : Inorganic Zinc 75㎛ 2nd : High Build Polyamide Epoxy 100㎛ - DFT : TOTAL 175㎛ 􀁹 Common bolts : KS B 1002 􀁹 Nuts : KS B 1012 􀁹 Washer : KS B 1326 􀁹 Hot dip galvanized | STRUCTURAL STEEL (INDOOR STEEL / ROLL MEMBER) - KS D 3530 SSC275 - PAINT : Surface Preparation : SSPC-SP-10 Primer : 방청페인트 1회 (KS M 6030 1종) 2nd : 조합페인트 2회 이상 (KS M 6020 1종) (보수도장포함) - DFT : - 􀁹 Common bolts : KS B 1002 􀁹 Nuts : KS B 1012 􀁹 Washer : KS B 1326 􀁹 Hot dip galvanized
D-02 |  |  |  | STRUCTURAL STEEL (INDOOR STEEL / ROLL MEMBER) - KS D 3515 SM355 - ASTM A572 G50 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-6 Primer : Inorganic Zinc 80㎛ 2nd : High Build Epoxy 80㎛ Finish : High Build Epoxy 80㎛ - DFT : TOTAL 240㎛ 􀁹- High-strength bolts : KS B 1010 F10T or ASTM A325(DACRO) 􀁹 Nuts : KS B 1010 or ASTM A563(DACRO) 􀁹 Washer : KS B 1326 or ASTM F436 (DACRO) 􀁹 Detail Description FABRICATION work includes followings but not limited to; - Shop drawings with Master member list. - Supply of Raw materials consisting of steel structures like Main members(roll or built up), Purlin & Girth, Stair, Canopy, Fasteners and Stud Shear Connector(Stud bolt) - Supply of Paints for touch up painting at the site. - Fabrication of Steel structures including Painting. - Transportation of the Materials to Construction Site(FOT). - Submissions : Certificate of Raw materials,Factory Test Report. ERECTION Work includes followings but not limited to; - Erection, Bolting, Welding, Touch up Painting and Grouting work for Column base. - Supply of Equipment for Material Handling and Lifting , Scaffolding, Tools and Consumables. - Submissions : Test and Inspection Report. In case of the seismic resistant frame in steel structure, the welding procedure shall be done in accordance with the requirements of AWS D1.8. The specific details will be indicated in the detail drawings of the engineering design stage
D-03 |  |  |  | STRUCTURAL STEEL (OUTDOOR STEEL / ROLL MEMBER) - KS D 3515 SM355 - ASTM A572 G50 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-6 Primer : Inorganic Zinc 80㎛ 2nd : High Build Epoxy 80㎛ Finish : Polyurethane 80㎛ - DFT : TOTAL 240㎛ 􀁹 High-strength bolts : KS B 1010 F10T or ASTM A325 (DACRO) 􀁹 Nuts : KS B 1010 or ASTM A563 ( DACRO) 􀁹 Washer : KS B 1326 or ASTM F436 (DACRO)
D-04 | STEEL(KS D 3866 SHN355) | (INDOOR STEEL / ROLL MEMBER) | 12.37% | STRUCTURAL STEEL (INDOOR STEEL / ROLL MEMBER) - KS D 3866 SHN355 - ASTM A992 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 or ISO 8501-1 Sa 2.5 Primer : Inorganic Zinc 75㎛ 2nd : High Build Polyamide Epoxy 100㎛ - DFT : TOTAL 175㎛ 􀁹 High-strength bolts : KS B 1010 F10T or ASTM A325 (DACRO) 􀁹 Nuts : KS B 1010 or ASTM A563 (DACRO) 􀁹 Washer : KS B 1326 or ASTM F436 (DACRO) |  | 용접구조용 압연강재 KS D 3515 SM355 건축구조용 열간압연형강 KS D 3866 SHN355 건축구조용 탄소강관 KS D 3632 SNT275/355 고력볼트 KS B 1010 일반볼트 KS B 1002 | STRUCTURAL STEEL * 일반적인 경우 공장건물은 지진력 저항시스템으로 “강구조 기준의 일반규정만을 만족하는 철골구조시스템“을 적용하여 설계되므로 반드시 내진 강재를 적용할 필요는 없음. * H-형강은 일반 구조용 압연강재인 SS275(구SS400)와 건축구조용 압연강재인 SN275(구SN400), 건축구조용 열간압연형강 SHN275(구SHN400)를 적용하고 기둥부재나 보 부재 중 H-500X200 이상인 경우 SM355, SN355, SHN355 강종 사용이 경제적임. * 고력볼트는 F10T TS볼트사용을 기본으로 함. - PAINT : 공사 사양 설계 표준화 Spec. 없음 | STRUCTURAL STEEL (INDOOR STEEL / ROLL MEMBER) - KS D 3515 SM490 - ASTM A992 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 Primer : Inorganic Zinc 75㎛ 2nd : High Build Polyamide Epoxy 100㎛ - DFT : TOTAL 175㎛ 􀁹 High-strength bolts : KS B 1010 F10T (DACRO) 􀁹 Nuts : KS B 1010 (DACRO) 􀁹 Washer : KS B 1326 (DACRO) | STRUCTURAL STEEL (INDOOR STEEL / ROLL MEMBER) - KS D 3866 SHN355 / SHN275 - ASTM A992 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 Primer : 방청페인트 1회 (KS M 6030 1종) 2nd : 조합페인트 2회 이상 (KS M 6020 1종) (보수도장포함) - DFT : - 􀁹 High-strength bolts : KS B 1010 F10T (DACRO) 􀁹 Nuts : KS B 1010 (DACRO) 􀁹 Washer : KS B 1326 (DACRO) | 내진강재 적용X(단가차이 클 경우) SM355 적용가능 HNCC SHN 적용 대산 SM 적용 Shelter SS275 SHN275 적용 (단가검토 후)
D-05 | STEEL(KS D 3866 SHN355) | (INDOOR STEEL / BUILT-UP MEMBER) | 0.6529% | STRUCTURAL STEEL (INDOOR STEEL / BUILT-UP MEMBER) - KS D 3866 SHN355 - ASTM A992 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 or ISO 8501-1 Sa 2.5 Primer : Inorganic Zinc 75㎛ 2nd : High Build Polyamide Epoxy 100㎛ - DFT : TOTAL 175㎛ 􀁹 High-strength bolts : KS B 1010 F10T or ASTM A325 (DACRO) 􀁹 Nuts : KS B 1010 or ASTM A563 (DACRO) 􀁹 Washer : KS B 1326 or ASTM F436 (DACRO) |  |  | STRUCTURAL STEEL * 일반적인 경우 공장건물은 지진력 저항시스템으로 “강구조 기준의 일반규정만을 만족하는 철골구조시스템“을 적용하여 설계되므로 반드시 내진 강재를 적용할 필요는 없음. * H-형강은 일반 구조용 압연강재인 SS275(구SS400)와 건축구조용 압연강재인 SN275(구SN400), 건축구조용 열간압연형강 SHN275(구SHN400)를 적용하고 기둥부재나 보 부재 중 H-500X200 이상인 경우 SM355, SN355, SHN355 강종 사용이 경제적임. * 고력볼트는 F10T TS볼트사용을 기본으로 함. | STRUCTURAL STEEL (INDOOR STEEL / ROLL MEMBER) - KS D 3515 SM490 - ASTM A992 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 Primer : Inorganic Zinc 75㎛ 2nd : High Build Polyamide Epoxy 100㎛ - DFT : TOTAL 175㎛ 􀁹 High-strength bolts : KS B 1010 F10T (DACRO) 􀁹 Nuts : KS B 1010 (DACRO) 􀁹 Washer : KS B 1326 (DACRO) | STRUCTURAL STEEL (INDOOR STEEL / ROLL MEMBER) - KS D 3866 SHN355 / SHN275 - ASTM A992 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 Primer : 방청페인트 1회 (KS M 6030 1종) 2nd : 조합페인트 2회 이상 (KS M 6020 1종) (보수도장포함) - DFT : - 􀁹 High-strength bolts : KS B 1010 F10T (DACRO) 􀁹 Nuts : KS B 1010 (DACRO) 􀁹 Washer : KS B 1326 (DACRO) | 안동사양 적용
D-06 | STEEL(KS D 3866 SHN355) | (OUTDOOR STEEL / ROLL MEMBER) | 0.3615% | STRUCTURAL STEEL (OUTDOOR STEEL / ROLL MEMBER) - KS D 3866 SHN355 - ASTM A992 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 or ISO 8501-1 Sa 2.5 Primer : Inorganic Zinc 75㎛ 2nd : High Build Polyamide Epoxy 125㎛ Finish : Polyurethane 40㎛ - DFT : TOTAL 240㎛ 􀁹 High-strength bolts : KS B 1010 F10T or ASTM A325 (DACRO) 􀁹 Nuts : KS B 1010 or ASTM A563 (DACRO) 􀁹 Washer : KS B 1326 or ASTM F436 (DACRO) | 2) Structural Steel Surface (Outdoor) : ISO 12944 Category C4 System A4.15 • Surface preparation : : Sa 2½ (ISO 8501-1:1988)/SSPC-SP10 • Coat 1 : Inorganic Zinc-rich Primer Single Coat System, DFT : min 75㎛ • Coat 2 : High Build Epoxy Polyamide with satin or semi-gloss finish, DFT : min 125㎛ • Coat 3 : Apliphatic Polyurethane - High Build, DFT : min 50㎛ • Total DFT 250μm |  | STRUCTURAL STEEL * 일반적인 경우 공장건물은 지진력 저항시스템으로 “강구조 기준의 일반규정만을 만족하는 철골구조시스템“을 적용하여 설계되므로 반드시 내진 강재를 적용할 필요는 없음. * H-형강은 일반 구조용 압연강재인 SS275(구SS400)와 건축구조용 압연강재인 SN275(구SN400), 건축구조용 열간압연형강 SHN275(구SHN400)를 적용하고 기둥부재나 보 부재 중 H-500X200 이상인 경우 SM355, SN355, SHN355 강종 사용이 경제적임. → SHN275 적용 (for Outdoor Steel, Shelter) * 고력볼트는 F10T TS볼트사용을 기본으로 함. - PAINT : 공사 사양 설계 표준화 Spec. 없음 | STRUCTURAL STEEL (OUTDOOR STEEL / ROLL MEMBER) - KS D 3503 SS400 - ASTM A992 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 Primer : Inorganic Zinc 75㎛ 2nd : High Build Polyamide Epoxy 125㎛ Finish : Polyurethane 40㎛ - DFT : TOTAL 240㎛ 􀁹 High-strength bolts : KS B 1010 F10T (DACRO) 􀁹 Nuts : KS B 1010 (DACRO) 􀁹 Washer : KS B 1326 (DACRO) | STRUCTURAL STEEL (OUTDOOR STEEL / ROLL MEMBER) - KS D 3866 SHN275 - ASTM A992 OR EQUIVALENT - PAINT : Surface Preparation : SSPC-SP-10 Primer : 방청페인트 1회 (KS M 6030 1종) 2nd : 조합페인트 2회 이상 (KS M 6020 1종) (보수도장포함) - DFT : - 􀁹 High-strength bolts : KS B 1010 F10T (DACRO) 􀁹 Nuts : KS B 1010 (DACRO) 􀁹 Washer : KS B 1326 (DACRO)
D-07 | ANCHOR BOLT | DIA 24MM, L=800 | 0.3654% | ANCHOR BOLT - KS B 1016 or ASTM F 1554 - Nuts : KS B 1012 or ASTM A563 - Washer : KS B 1326 or ASTM F436 - Hot dip galvanized - FOR STEEL COLUMN BASE - INCLUDING INSTALLATION & ALIGNMENT FOR ANCHOR FRAMES & TEMPLATES |  | KS B 1016 | ANCHOR BOLT - KS B 1016 | ANCHOR BOLT - KS B 1016 | ANCHOR BOLT - KS B 1016
D-08 | GROUTING | NON-SHRINK CEMENT BASED GROUT. | 0.08969% | NON-SHRINKAGE GROUT - Fcu= 50 MPa AT 28 DAYS - CEMENTIOUS - FOR STEEL COLUMN BASE - INCLUDING FORM WORK |  |  | NON-SHRINKAGE GROUT - 공사 사양 설계 표준화 Spec. 없음 | NON-SHRINKAGE GROUT - Fcu= 50 MPa | NON-SHRINKAGE GROUT - Fcu= 50 MPa
D-09 | DECK PLATE | GALVANIZED. 1.6 t | 0.863% | DECK PLATE - KS D 3602 - THK. 1.6mm GALVANIZED STEEL - HOT DIPPED GALVANIZED AS PER ASTM A653-01a ZINC WEIGHT OF NOT LESS THAN 0.275kg/m2 ON EACH SIDE OF SHEET - INCLUDING ALL SUBSIDIARY WORK SUCH AS OPENING ARRANGEMENT, INSTALLATION OF END PLATE & ENCLOSURE, CONC. STOPPER, WELDING, etc. - AS PER TECH SPEC. - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION |  | KS D 3602 | DECK PLATE * 데크 슬래브는 철근 트러스형 데크를 사용하며 다른 데크 슬래브를 사용하는 경우 시설담당자와 협의하여 결정할 것. | DECK PLATE - KS D 3602 - THK. 1.6mm GALVANIZED STEEL | DECK PLATE - 철근트러스형 시스템데크 - 아연도강판 : 0.5 mm 용융아연도강판 상단/하단 주근: D10~D13 래티스재 : 원형철선 ø5~6 스터드 볼트 포함(SS275) End Plate, End Closer 포함 | 현대차 에너지관리팀 Clarification item
D-10 |  |  |  | DECK PLATE - KS D 3602 - THK. 1.2mm GALVANIZED STEEL - HOT DIPPED GALVANIZED AS PER ASTM A653-01a ZINC WEIGHT OF NOT LESS THAN 0.275kg/m2 ON EACH SIDE OF SHEET - INCLUDING ALL SUBSIDIARY WORK SUCH AS OPENING ARRANGEMENT, INSTALLATION OF END PLATE & ENCLOSURE, CONC. STOPPER, WELDING, etc. - AS PER TECH SPEC. - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION
D-11 |  |  |  | FIRE PROOFING COATING 2.0 HOUR (INDOOR STEEL) - 2.0 HOUR FIRE PROOFING COATING - INTUMESCENT FIREPROOF PAINT - 한국공인인증기관 인증제품 - INCLUDING SCAFFOLDING WORK - INCLUDING PROTECTION FOR EQUIPMENT AND FACILITY - INCLUDING REACTIFICATION OF DAMAGED PARTS ON SITE - INCLUDING CERTIFICATION
D-12 | STEEL PAINTING | FOR-FIRE-PROOFED, PAINT TYPE (2HOUR) | 0% | FIRE PROOFING COATING 2.0 HOUR (INDOOR STEEL) - 2.0 HOUR FIRE PROOFING COATING - INTUMESCENT FIREPROOF PAINT - 한국공인인증기관 인증제품 - INCLUDING SCAFFOLDING WORK - INCLUDING PROTECTION FOR EQUIPMENT AND FACILITY - INCLUDING REACTIFICATION OF DAMAGED PARTS ON SITE - INCLUDING CERTIFICATION |  |  |  | - | -
D-13 |  |  |  | STRUCTURAL STEEL (ELECTION ONLY) - BRIEF SPEC.: SEE ITEM NO. 4.1 & 4.2 - INCLUDING TOUCH-UP PAINTING & GRINDING, WELDING, SCAFFOLDING WORK (IF NECESSARY) - INCLUDING WELDING OF STUD SHEAR CONNECTOR (STUD BOLTS) - INCLUDING TESTING AS PER TECH.SPEC.
E-01 | INSULATION | ONLY FOR BRICK WALL INSULATION(THK.100) | 0.4127% | INSULATION FOR CAVITY WALL - THK.100 GLASS WOOL (64kg/m3 DENSITY) - INCLUDING FIXING ACCESSORIES - INCLUDING SCAFFOLDING | • Outside Wall Thermal Transmittance ≤ 0.45 W/m2K |  |  | INSULATION FOR CAVITY WALL - GLASS WOOL (64kg/m3 DENSITY) - Thermal Transmittance ≤ 0.45 W/m2K (열관류율) | INSULATION FOR CAVITY WALL - KS L 9102 그라스울 보온판 48K, 64K, 80K, 96K, 120K - 열전도율 : 0.034 W/mK 이하
E-02 | BRICK(T=115) | [0.5B] CEMENT BRICK W/LINTEL FOR OPENING | 1.824% | T115 CLAY/CEMENT BRICK - KS F4004 2nd grade, Min. Compressive strength >= 8.2N/mm2 (시멘트 벽돌은 KS F 4004 C종 2급으로 압축강도는 8.2 N/mm2 이상) - INCLUDING TIES & GALV. ANCHOR TO BE WELDED TO STEEL - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING SEISMIC REINFORCEMENT BAR (VERTICAL, HORIZONTAL) - INCLUDING HEADER, STIFF COLUMN, LINTEL, CONC. FRAME FOR LARGE OPENING | (b) Cement brick shall conform to KS F 4004, Type B or ASTM C55, and Portland cement shall conform to KS L 5201. Design minimum compressive strength shall be 82kg/cm2. |  | 화장실, 샤워실 및 기계실 등에 사용 | CEMENT BRICK - KS F 4004, 8.2 N/mm2 | CEMENT BRICK - KS F 4004, 8.0 N/mm2 # 대구 : BRICK & BLOCK 미적용
E-03 | BRICK(T=230) | [1.0B] CEMENT BRICK W/LINTEL FOR OPENING | 3.299% | T230 CLAY/CEMENT BRICK - KS F4004 2nd grade, Min. Compressive strength >= 8.2N/mm2 (시멘트 벽돌은 KS F 4004 C종 2급으로 압축강도는 8.2 N/mm2 이상) - INCLUDING TIES & GALV. ANCHOR TO BE WELDED TO STEEL - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING SEISMIC REINFORCEMENT BAR (VERTICAL, HORIZONTAL) - INCLUDING HEADER, STIFF COLUMN, LINTEL, CONC. FRAME FOR LARGE OPENING | (b) Cement brick shall conform to KS F 4004, Type B or ASTM C55, and Portland cement shall conform to KS L 5201. Design minimum compressive strength shall be 82kg/cm2. |  | 화장실 및 기계실 등에 사용 공장동-사무동 경계벽은 차음검토 | CEMENT BRICK - KS F 4004, 8.2 N/mm2 | CEMENT BRICK - KS F 4004, 8.0 N/mm2 # 대구 : BRICK & BLOCK 미적용 | STB-CCB 내벽 차음성능 검토 후 재료변경 ALC? Gypsum?
E-04 |  |  |  | 4" SAND-LIME BRICK - ASTM C55 - COMPRESSIVE STRENGTH : 20 N/mm2 - SIZE 222x108x67 Detail Description -INCLUDING TIES & GALV. ANCHOR TO BE WELDED TO STEEL - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING SEISMIC REINFORCEMENT BAR (VERTICAL, HORIZONTAL) - INCLUDING HEADER, STIFF COLUMN, LINTEL, CONC. FRAME FOR LARGE OPENING
E-05 |  |  |  | HOLLOW CONC. BLOCK - TYPE I AS PER ASTM C90 - WALL TIE : GALVANIZED STEEL, ASTM A153 CLASS B2 OR EQUIVALANT : FISHTAILED TYPE (150 mm x 75mm) : Max. @450mm (VERTICAL) : Max. @900mm (HORIZONTAL) - WALL LUG : BUTTERFLY TYPE : Max. @450mm (VERTICAL) - INCLUDING GALV. ANCHOR, TIES, LUGS - INCLUDING METAL LATH (Min.300mm Wide) - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING VERTICAL JOINTS POINTED FLUSH AND HORIZONTAL JOINTS POINTED STRUCK FOR FAIR FACED CONC. BLOCK ONLY - INCLUDING GALV. ANCHOR STRIP TO BE WELDED TO STEEL - INCLUDING SOLID CONC. BLOCK FOR END BLOCKS - INCLUDING HEADER, STIFF COLUMN, LINTEL, CONC. FRAME FOR LARGE OPENING - INCLUDING SEISMIC REINFORCEMENT BAR (VERTICAL, HORIZONTAL)
E-06 |  |  |  | 8" HOLLOW CONC. BLOCK
E-07 |  |  |  | 6" HOLLOW CONC. BLOCK
E-08 |  |  |  | 4" HOLLOW CONC. BLOCK
E-09 |  |  |  | 8" FAIR FACED CONC. BLOCK
E-10 |  |  |  | 6" FAIR FACED CONC. BLOCK
E-11 |  |  |  | 4" FAIR FACED CONC. BLOCK
E-12 |  |  |  | CAVITY WALL W/INSULATION (8" BLOCK+ INSULATION+ 4"HOLLOW BLCOK or 4'' SAND-LIME BRICK)
E-13 |  |  |  | CAVITY WALL W/INSULATION (4" BLOCK+ INSULATION+ 4"HOLLOW BLCOK or 4'' SAND-LIME BRICK)
E-14 |  |  |  | 8" HOLLOW CONC. BLOCK (SWYD) - GRADE N, TYPE II AS PER ASTM C90 - WALL TIE : GALVANIZED STEEL, ASTM A153 CLASS B2 OR EQUIVALANT : FISHTAILED TYPE (150 mm x 75mm) : Max. @450mm (VERTICAL) : Max. @900mm (HORIZONTAL) - WALL LUG : BUTTERFLY TYPE : Max. @450mm (VERTICAL) - INCLUDING GALV. ANCHOR, TIES, LUGS - INCLUDING METAL LATH (Min.300mm Wide) - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING VERTICAL JOINTS POINTED FLUSH AND HORIZONTAL JOINTS POINTED STRUCK FOR FAIR FACED CONC. BLOCK ONLY - INCLUDING GALV. ANCHOR STRIP TO BE WELDED TO STEEL - INCLUDING SOLID CONC. BLOCK FOR END BLOCKS - INCLUDING HEADER, STIFF COLUMN, LINTEL, CONC. FRAME FOR LARGE OPENING - INCLUDING SEISMIC REINFORCEMENT BAR (VERTICAL, HORIZONTAL)
E-15 |  |  |  | 4" HOLLOW CONC. BLOCK (SWYD)
E-16 |  |  |  | 8" U-CONC. BLOCK - TYPE I AS PER ASTM C90 - 4-D12 REINFORCING BARS TO BE USED AND TO BE FILLED W/ CONC - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING GALV. ANCHOR STRIP TO BE WELDED TO STEEL
E-17 |  |  |  | 6" U-CONC. BLOCK - TYPE I AS PER ASTM C90 - 4-D12 REINFORCING BARS TO BE USED AND TO BE FILLED W/ CONC - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING GALV. ANCHOR STRIP TO BE WELDED TO STEEL
E-18 |  |  |  | 4" U-CONC. BLOCK - TYPE I AS PER ASTM C90 - 2-D12 REINFORCING BARS TO BE USED AND TO BE FILLED W/ CONC - INCLUDING SCAFFOLDING - INCLUDING VERT./ HORIZONTAL JOINT WORK - INCLUDING GALV. ANCHOR STRIP TO BE WELDED TO STEEL
E-19 |  |  |  | HOLLOW GLASS BLOCK - 200mm x 200mm x thk.90 - COMFORMING TO BS1207 & CP122 - INCLUDNG SCAFFOLDING - INCLUDNG FIXING MATERIAL
E-20 | DAMP-PROOF COURSE | For masonry work | 0.1107% | DAMP-PROOF COURSE - ALUMINUM CORED BITUMENISED HESSIAN COVERED SHEET : BS6398 : 1983, BS743, W=350mm - HORIZONTAL: BOTTOM OF ALL BLOCKWORK INCLUDING 12MM THICK CEMENT MORTAR - VERTICAL: ALL DOOR & WINDOW REVEALS - THE DAMP PROOF MEMBRANE SHALL BE LAPPED AND BE FULLY BONDED TO A DAMP PROOF COURSE IN THE PLINTH WALL. |  |  |  | DAMP-PROOF COURSE - 기술기준서 Spec. 없음 | DAMP-PROOF COURSE - 기술기준서 Spec. 없음
F-01 |  |  |  | BONDED CEMENT SCREED - THK. MIN. 40mm - INCLUDING CONTROL JOINT WORK WITH ALL RELATED MATERIAL - INCLUDING STEEL TROWEL FINISHING AND/ OR MECHANICAL PLACING & FINISHING - INCLUDING ADHESIVE AND APPROPRIATE SLOPE
F-02 | EXTERNAL PLASTER | WALL | 0.5872% | EXTERIOR CEMENT PLASTER FOR WALL - THK. 21 / 3 COATS (8+8+5)mm - INCLUDING SCAFFOLDING - INCLUDING VERT. /HORIZONTAL CONTROL JOINT WORK - INCLUDING GALV. CORNER & CASING BEAD & PLASTER STOP & LATH WORK - INCLUDING PREPARETION OF SURFACE & MOIST CURING |  |  |  | EXTERIOR CEMENT PLASTER FOR WALL - 기술기준서 Spec. 없음 | EXTERIOR CEMENT PLASTER FOR WALL - THK. 24
F-03 | INTERNAL PLASTER | WALL | 1.092% | INTERIOR CEMENT PLASTER FOR WALL - THK. 18mm / 3 COATS (7+7+4)mm - INCLUDING SCAFFOLDING - INCLUDING VERT. /HORIZONTAL CONTROL JOINT WORK - INCLUDING GALV. CORNER & CASING BEAD & PLASTER STOP & LATH WORK - INCLUDING PREPARETION OF SURFACE & MOIST CURING |  |  |  | INTERIOR CEMENT PLASTER FOR WALL - 기술기준서 Spec. 없음 | INTERIOR CEMENT PLASTER FOR WALL - THK. 18
F-04 |  |  |  | INTERIOR CEMENT PLASTER FOR CEILING - THK. 9mm / 2 COATS (4.5+4.5)mm
F-05 | STEEL TROWEL FINISH | FOR CONCRETE SURFACE | 0.1451% | STEEL TROWEL FINISH - FOR CONCRETE FLOOR FACE UNDER THE HARDENER FINISHING, PAINTING AND PVC TILE, CARPET TILE, ETC. |  |  |  | STEEL TROWEL FINISH - 기술기준서 Spec. 없음 | 쇠흙손마감 - 별도의 마감이 없는 바닥부분 (도장제외) - 기계실, 중량물창고, 공작 및 정비실 등
G-01 |  |  |  | EMULSION PAINT (EXT.) - FOR EXT. WALL - Surface Prep - Prime Coat Latex Emulsion - Minimum dry thickness 2 mils. Koppers "600 - Interior, Exterior", Tnemec "6 Tneme - Cryl", or Amerguard 335 Epoxy Acrylic. - Second Coat Latex Emulsion - Minimum dry thickness 2 mils. Koppers "600 - Interior, Exterior", Tnemec "6 Tneme - Cryl", or Amerguard 335 Epoxy Acrylic. - Third Coat Copolymer - Minimum dry thickness 2 mils. Rainguard Products Company "Vandl Guard". - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-02 |  |  |  | ACRYLIC EMULSION PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT OF ALKALI-RESISTING SEALER 30 ~ 35㎛ - 2 COATS EMULSION PAINT 50~60㎛ '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PAINT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-03 | ACRYLIC EMULSION PAINT (AEP) | EXTERNAL WALL | 0.1913% | ACRYLIC EMULSION PAINT (EXT.) - FOR EXT. WALL - 1 COAT OF ALKALI-RESISTING SEALER 30 ~ 35㎛ - 2 COATS ACRYLIC PAINT - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION |  |  | 하도1회 중도1회 상도1회 (총 60micron) Color Scheme : 별도 기준 참조 | ACRYLIC EMULSION PAINT (EXT.) - 1회도장: Acrylic Emulsion 30 ㎛ 2회도장: Acrylic Emulsion 30 ㎛ 3회도장: Acrylic Emulsion 30 ㎛ | 수성페인트 - KS M 6010 1종 (외부) - 1회도장: Acrylic Emulsion 40 ㎛ 2회도장: Acrylic Emulsion 40 ㎛ 3회도장: Acrylic Emulsion 40 ㎛
G-04 |  |  |  | ACRYLIC PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT OF ALKALI-RESISTING SEALER 30 ~ 35㎛ - 2 COATS ACRYLIC PAINT '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-05 |  |  |  | ACRYLIC PAINT (BASE) - FOR BASE PAINT H=100mm - 1 COAT OF ALKALI-RESISTING SEALER 30 ~ 35㎛ - 2 COATS ACRYLIC PAINT '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-06 |  |  |  | ALKYD ENAMEL PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT PRIMER - 2 COATS OF ALKYD ENAMEL PAINT - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-07 | EPOXY PAINT | FLOOR | 0.2644% | EPOXY PAINT (FLOOR) - FOR INTERIOR FLOOR - 1 COAT PRIMER - 2 COATS EPOXY POLYAMIDE, SEAL COAT TYPE - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION |  |  | 프라이머 0.05mm + 에폭시 0.1mm | EPOXY PAINT (FLOOR) - 1회도장 : Epoxy Primer 50 ㎛ 2회도장 : Polyamide Epoxy 100 ㎛ 3회도장 : Polyamide Epoxy 50 ㎛ | 에폭시 페인트 - 에폭시 아민수지계 - 1회도장(하도): Epoxy Primer 40 ㎛ 2회도장(상도): Amine Epoxy 80 ㎛ | 두께명시
G-08 | ANTI-DUST PAINT | FLOOR | 0.01225% | EPOXY PAINT (DUST PROOF) - FOR BENEATH OF FALSE FLOOR - 1 COAT PRIMER - 1 COATS EPOXY POLYAMIDE '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION |  |  |  | EPOXY PAINT (DUST PROOF) - 1회도장 : Epoxy Primer/Sealer 50 ㎛ 2회도장 : Phenolic Epoxy 125 ㎛ 3회도장 : Phenolic Epoxy 125 ㎛ | EPOXY PAINT (DUST PROOF) - 기술기준서 Spec. 없음
G-09 |  |  |  | EPOXY PAINT (EXT.) - FOR EXT. WALL - 1 COAT PRIMER - 2 COATS EPOXY POLYAMIDE '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-10 |  |  |  | EPOXY PAINT (INT.) - FOR INT. WALL & CEILING - Surface Prep - Prime Coat Acrylic Emulsion - Kopper "Surfacer", Tnemec 51 792 "Vinacryl Primer-sealer", or Amerguard 149. - Second Coat Epoxy - Minimum dry thickness 1.75 mils. Koppers "Glamorglass 200 Epoxy", or Amerguard 335 "Epoxy Acrylic". - Third Coat Epoxy - Minimum dry thickness 1.75 mils. Koppers "Glamorglass 200 Epoxy", or Amerguard 335 "Epoxy Acrylic". '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-11 | EPOXY PAINT | SKIRT, H=100MM | 0.02041% | EPOXY PAINT (BASE) - FOR BASE PAINT H=100mm - 1 COAT PRIMER - 2 COATS EPOXY POLYAMIDE '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION |  |  |  | EPOXY PAINT (BASE) - 1회도장 : Epoxy Primer 50 ㎛ 2회도장 : Polyamide Epoxy 100 ㎛ 3회도장 : Polyamide Epoxy 50 ㎛ | 걸레받이용페인트 - 아크릴계 - 하도: 아크릴 프라이머 상도: 3회이상 도장 (45 ㎛ 이상 확보)
G-12 | ACID RESISTANT PAINT | FLOOR | 0.009041% | ACID RESISTANT PAINT (FLOOR) - FOR INTERIOR FLOOR - 1 COAT CHLORINATED RUBBER PRIMER - 2 COATS CHLORINATED RUBBER HIGH BUILD - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION |  |  |  | ACID RESISTANT PAINT (FLOOR) - 1회도장 : Epoxy Primer/Sealer 50 ㎛ 2회도장 : Polyamide Epoxy 125 ㎛ 3회도장 : Polyamide Epoxy 125 ㎛ | 내산 페인트 - 에폭시계 - 축전지실 콘크리트 또는 미장면 - 하도 : Epoxy Primer / Sealer 40 ㎛ 중도 : Polyamide Epoxy 40 ㎛ 상도 : Polyamide Epoxy 40 ㎛
G-13 | ACID RESISTANT PAINT | INTERNAL WALL | 0.002954% | ACID RESISTANT PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT CHLORINATED RUBBER PRIMER - 2 COATS CHLORINATED RUBBER HIGH BUILD - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION |  |  |  | ACID RESISTANT PAINT (INT.) - 1회도장 : Epoxy Primer/Sealer 40 ㎛ 2회도장 : Polyamide Epoxy 40 ㎛ 3회도장 : Polyamide Epoxy 40 ㎛ | 내산 페인트 - 에폭시계 - 축전지실 콘크리트 또는 미장면 - 하도 : Epoxy Primer / Sealer 40 ㎛ 중도 : Polyamide Epoxy 40 ㎛ 상도 : Polyamide Epoxy 40 ㎛
G-14 | CHEMICAL RESISTANT PAINT | FLOOR | 0.06577% | CHEMICAL RESISTANT EPOXY PAINT (FLOOR) - FOR INTERIOR FLOOR - 1 COAT EPOXY PRIMER / SEALER - 2 COATS PHENOLIC EPOXY - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION |  |  |  | CHEMICAL RESISTANT EPOXY PAINT (FLOOR) - 1회도장 : Epoxy Primer/Sealer 50 ㎛ 2회도장 : Phenolic Epoxy 125 ㎛ 3회도장 : Phenolic Epoxy 125 ㎛ | 내화학 에폭시 페인트 - 에폭시계 - 내산, 내알칼리성이 요구되는 바닥면 - 하도 : 크린폭시 상도 : 내산 에폭시 황산70 %, 질산30 %, 염산30 %, 과산화수소22 %, 인산70 %, 아세트산20 %, 수산화나트륨, 수산화칼슘, 엔진오일에도 변형이 없는 제품 건조도막두께 2~3 mm
G-15 | CHEMICAL RESISTANT PAINT | INTERNAL WALL | 0.1235% | CHEMICAL RESISTANT EPOXY PAINT (INT.) - FOR INT. WALL & CEILING - 1 COAT EPOXY PRIMER / SEALER - 2 COATS PHENOLIC EPOXY '- INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION |  |  |  | CHEMICAL RESISTANT EPOXY PAINT (INT.) - 1회도장 : Epoxy Primer/Sealer 50 ㎛ 2회도장 : Phenolic Epoxy 125 ㎛ 3회도장 : Phenolic Epoxy 125 ㎛ | 내화학 에폭시 페인트 - 에폭시계 - 내산, 내알칼리성이 요구되는 바닥면 - 하도 : 크린폭시 상도 : 내산 에폭시 황산70 %, 질산30 %, 염산30 %, 과산화수소22 %, 인산70 %, 아세트산20 %, 수산화나트륨, 수산화칼슘, 엔진오일에도 변형이 없는 제품 건조도막두께 2~3 mm
G-16 |  |  |  | COLORLESS WATER REPELLENT PAINT - FOR EXT. WALL (4" SAND-LIME BRICK) -1 COAT - INCLUDING SCAFFOLDING
G-17 |  |  |  | THK.5mm EPOXY SCREED & SEAL COAT (FLOOR) - FOR INTERIOR FLOOR - 1 COAT EPOXY PRIMER & SEALER - 1 COAT EPOXY MORTAR SCREED VARIABLE MIN. 5mm THK - 1 COAT EPOXY SEAL COAT ON TOP OF EPOXY SCREED - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-18 |  |  |  | THK.3mm HEAVY DUTY SELF LEVELLING EPOXY PAINT (FLOOR) - FOR INTERIOR FLOOR - 1 COAT EPOXY PRIMER - 1 COAT HIGH BUILT SELF LEVELLING EPOXY SCREED COATING VARIABLE MIN. 3mm THK - INCLUDING SURFACE TREATMENT & PANIT PUTTY - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-19 |  |  |  | TEXTURED PAINT (EXT.) - FOR EXT. WALL - 1 COAT PRIMER, - 2 COATS TEXTURED PAINT - 1 COAT DIRT RESISTANCE FINISH COAT - INCLUDING SCAFFOLDING - INCLUDING SURFACE TREATMENT & PANIT PUTTY - WATER RESISTANCE ,ANTI-CONTAMINATION,EASY CLEANING - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION
G-20 | SURFACE HARDENER | HEAVY DUTY FLOOR CHEMICAL SURFACE HARDENER ANTI-DUST FINISH | 0.2141% | SURFACE HARDENER - FOR INTERIOR FLOOR - HEAVY DUTY FLOOR CHEMICAL SURFACE HARDENER ANTI-DUST FINISH - GRANOLITE® NON-METALLIC FLOOR HARDENER - INCLUDING STEEL TROWEL FINISHING AND/OR MECHANICAL PLACING & FINISHING - INCLUDING JOINT GROUTING - TO EXECUTE AS PER MANUFACTURER'S INSTRUCTION - USAGE RATE 5 KG/M2. - INCLUDING ONE COAT OF ‘SEALBOND GR’ CURING COMPOUND. |  |  |  | SURFACE HARDENER - T/G Hall - 1회도장 : Epoxy Primer/Sealer 50 ㎛ 2회도장 : Self Levelling Epoxy 2,000 ㎛ 3회도장 : Polyamide Epoxy 50 ㎛ | SURFACE HARDENER - 기술기준서 Spec. 없음
H-01 | RIGID INSULATION FOR ROOF | THK. 200mm Rigid Extruded Polystyrene Insulation | 0.3671% | RIGID INSULATION FOR ROOF - FOR ROOF SLAB - THK. 200mm Rigid Extruded Polystyrene Insulation OR EQUIVALENT - COMPRESSIVE STRENGTH : Min. 250 KPa - INCLUDING JOINT TAPE | • Roof Thermal Transmittance ≤ 0.24 W/m2K |  | <바닥 단열> 바닥부위가 지표면으로 2m 이내 위치할 경우, 최하층 거실의 단열기준을 적용. 건물물의 내표면까지 수평거리 10m이내 바닥부위는 단열조치 <에너지절약설계 기준> 최하층 거실바닥 : 최소 135mm 적용 (관류율0.35 W/m2K 이하) 지붕단열재 : 단열재등급 가 기준 180mm 이상 (0.18 W/m2K이하) | RIGID INSULATION FOR ROOF - 기술기준서 Spec. 없음 (철근 Con'c + 복합방수 + 단열재 + P.E 필름 + 누름 Con'c THK.60mm) | RIGID INSULATION FOR ROOF - 압출발포 폴리스티렌 / KS M 3808 압출법 보온판 특호, 1호, 2호, 3호 - 열전도율 : 0.034 W/mK 이하 | 매트슬라브 밑에 단열재 설치불가 바닥단열재 관련 법규검토 요망
H-02 | WATERPROOFING MEMBRANE | FOR ROOF AREA ONLY | 1.175% | MEMBRANE WATERPROOFING - BUILT-UP ROOFING - FOR ROOF SLAB & PARAPET WALL - INCLUDING COLD WORKED PRIME COAT & 4mm THK. BITUMINUOUS ROOFING FELT - INCLUDING GALV. STEEL FLASHING TO SEAL/COVER THE END OF WATERPROOFING AT PARAPET/UPSTAND - INCLUDING BITUMEN SEALANT AT GROOVE TO END WATERPROOFING MEMBRANE AT UPSTAND - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK |  |  |  | MEMBRANE WATERPROOFING - 기술기준서 Spec. 없음 (철근 Con'c + 복합방수 + 단열재 + P.E 필름 + 누름 Con'c THK.60mm) | 신기술복합방수적용(지붕) | 지하외벽 멤브레인 물량 별도 항목으로 추가검토 지붕 : EPDM멤브레인 복합방수 화장실 : 우레탄/액체방수
H-03 |  |  |  | MEMBRANE WATERPROOFING - BUILT-UP ROOFING - FOR ROOF SLAB & PARAPET WALL - a. Primer: Shall be MIP-067 epoxy-polyamide, low viscosity, two-component primer sealer. - b. Base Membrane: Shall be "Multi-l-Thane 4000" single-component, high-adhesion, moisture cured, liquid polyurethane membrane, 85% weight solids. - c. Second Coat Membrane: Shall be "Multi-l-Thane 5000" single component, high tensile strength, liquid applied elastomeric polyurethane, 85% weight solids. - d. Aggregate: Equal to or finer than 20 mesh flint shot silica, ground glass, or Monterey sand. Aggregate shall be hard and stable to atmospheric conditions, clean and free of any other material, chemicals or salt. - e. Top Coat: Shall be "Multi-l-Thane 6000" single component, high tensile strength, abrasion resistant and weather-resistant aliphatic polyurethane membrane 53% solids. - f. Caulking: "Multi-l-Seal 1000", one component polyurethane compound. - INCLUDING GALV. STEEL FLASHING TO SEAL/COVER THE END OF WATERPROOFING AT PARAPET/UPSTAND - INCLUDING BITUMEN SEALANT AT GROOVE TO END WATERPROOFING MEMBRANE AT UPSTAND - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK
H-04 |  |  |  | ELATOMERIC COATING - FOR ROOF SLAB & PARAPET WALL - INCLUDING GALV. STEEL FLASHING TO SEAL/COVER THE END OF WATERPROOFING AT PARAPET/UPSTAND - INCLUDING BITUMEN SEALANT AT GROOVE TO END WATERPROOFING MEMBRANE AT UPSTAND - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK
H-05 |  |  |  | EPDM WATERROOFING MEMBRANE - CONTINUOUS SHEET ETHYLENE PROPYLENE DIENE MONOMER (EPDM) ROOFING SYSTEM - FULLY ADHERED EPDM SYSTEM TO MECHANICALLY ATTACHED - INCLUDING ADHESIVE, SHEET, RUBBER FLASHING, SEALANTS - TAPER RIGID INSULATION TO ROOF DRAIN - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK
H-06 | LIQUID WATERPROOFING | INTERNAL FLOOR AREA | 0.0606% | CEMENTITIOUS WATERPROOFING - FOR FLOOR & WALL OF WET ROOM - 2 COAT CEMENT BASE - ACRYLIC-POLYMER EMULSION MIXED WITH CEMENT MORTARS - INCLUDING ALL ACCESSORIES NEEDED FOR THE WORK - INCLUDING SURFACE TREATMENT WORK |  |  | <화장실 방수> 바닥 : 우레탄방수 벽 : 액체방수 위 우레탄방수 (H=1200) <생산장비 Pit 방수적용기준> 지수판, 구체방수/액체방수, 자착식시트 등 깊이 등 조건에 따라 상이 | CEMENTITIOUS WATERPROOFING - 기술기준서 Spec. 없음 | 우레탄도막방수 - 3mm, 주방, 화장실 및 샤워실 | 현대차 Clarification 사항
H-07 |  |  |  | P.E FILM - THK. 0.1mm, 2 LAYERS FOR ROOF - AS PER SPECIFICATION
H-08 | LIGHT-WEIGHT CONCRETE SCREED | W/ TROWELING, WITHOUT WIREMESH (for SLOPE,1/100) | 0.178% | LIGHT WEIGHT CONCRETE ( ROOF ) - LIGHTWEIGHT CELLULAR CONCRETE FILL PORTLAND CEMENT AND FOAMING AGENT - MIN.THK. 60 mm, 1/150 SLOPE - INCLUDING ALL MATERIALS FOR EXPANSION JOINT : @2.0m x 2.0m - INCLUDING WIRE MESH FOR CRACK CONTROL |  |  |  | LIGHT WEIGHT CONCRETE ( ROOF ) - 기술기준서 Spec. 없음 | 신기술복합방수적용(지붕)
H-09 |  |  |  | CON'C ROOF TILE - PRECASTE CONC. TILE SIZE : 400x400xT40mm - INCLUDING SEPARATION JOINT OF 15mm FILLED W/ APPROVED SEALANT - INCLUDING CRACK CONTROL JOINT : 8mmx12~15mm(H) @1.25x 1.25M FILLED W/APPROVED SEALANT - INCLUDING SEMI-DRY TYPE CEMENT MORTAR - INCLUDING CONTROL JOINT WORK WITH ALL RELATED MATERIAL - INCLUDING STEEL TROWEL FINISHING AND/ OR MECHANICAL PLACING & FINISHING
H-10 |  |  |  | ROOF AGGREGATE - THK. 50 mm / PROTECTION FOR WATER PROOFING - WASHED AGGREGATE MAX. @ 19MM
H-11 | BITUMINOUS COATING | FOR UNDERGROUND CONCRETE PROTECTION | 1.282% | UNDERGROUND BITUMEN EMULSION PAINT - MASTER SEAL 420 OR EQUIVALENT - 2 COATS - NORMAL DRY CONDITION |  |  |  | UNDERGROUND BITUMEN EMULSION PAINT - 기술기준서 Spec. 없음 | 규산질계 분말형 도포방수 - KS F 4918, 2회 - 지하 바닥 및 외벽부분
H-12 | WATER STOP | PVC WATERSTOP | 0.01739% | PVC WATERSTOP - W = 150, THK 9mm FOR FLAT DUMBBELL - INTERNAL TYPE , HEAVY DUTY, FLEXIBLE P.V.C. WITH A CENTRAL EXPANSION BULB |  |  |  | PVC WATERSTOP - 연질 염화비닐수지 지수판, KS M 3805 | 지수판(PVC WATERSTOP) - W = 200, THK 5mm
H-13 |  |  |  | HYDROPHILIC POLYMER RUBBER WATERSTOP - BENTONITE CLAY & MICROSCOPIC PLATELETS WATERSTOP - INCLUDING INSTALL
H-14 |  |  |  | UNDERGROUND BITUMEN MEMBRANE - FLEXIBLE MULTY LAYERED COMPOSITE SHEET - FELT MEMBRANE BONDED TO BITUMEN/POLYMER ADHESIVE - FOR ALL UNDERGROUND CONCRETE SURFACE - INCLUDING SEALING JOINT WORK ; RAKING OUT OF WALL & FILLING W/ BITUMEN SEALING COMPOUND - FOR WRAPPING ALL UNDERGROUND FOUNDATION / CONC. STRUCTURE - INCLUDING AEROFOIL OR SIMILAR - INCLUDE'G ALUMINUM FLASHING ACCORDING TO SPEC. - REFER TO TECHNICAL SPEC.
H-15 |  |  |  | CEMENT SCREED FOR WATER PROOFING - THK. 25MM / PROTECTION FOR WATER PROOFING - FOR BOTTOM - INCLUDING CONTROL JOINT WORK WITH ALL RELATED MATERIAL - INCLUDING STEEL TROWEL FINISHING AND/ OR MECHANICAL PLACING & FINISHING
H-16 |  |  |  | PROTECTION BOARD - BITUMEN IMPREGNATED FIBRE BOARD - THK. 6mm - FOR SIDE & TOP SIDE - FOR WALL & VERTICAL SIDE
H-17 | PE SHEET (VAPOR BARRIER) | THK. 0.15mm, 2 LAYERS | 0% | VAPOUR BARRIER - THK. 0.15mm, P.E FILM 2 PLIES - FOR BELOW GROUND SLAB & ROOF |  |  |  | VAPOUR BARRIER - Aluminum Foil 7㎛과 P.V.C Film 80㎛ 사이에 Fiber Yarn을 넣어 접착제로 접착시킨 제품이어야 한다 | 방습재 - THK. 0.1mm, P.E FILM 2 PLIES | 0.1mm 적용
I-01 |  |  |  | RUBBER SKIRTING - H100 x 2T - FOR WALL
I-02 |  |  |  | ANTI-STATIC VINYL SKIRTING - H100 x 15 mm
I-03 |  |  |  | SKIRT PAINTING - EPOXY PAINT - FOR FLOOR SKIRTING - H=100 - INCLUDING SURFACE TREATMENT & PANIT PUTTY
I-04 |  |  |  | VINYL SHEET THK.3mm - INCLUDING ADHESIVE, WELDING - INCLUDING POLISHING WORK
I-05 |  |  |  | ANTI-STATIC VINYL TILE 400 x 400 x 3mm - INCLUDING ADHESIVE, WELDING - INCLUDING POLISHING WORK
I-06 | HEAVY DUTY PVC TILE | FLOOR W/ BEDDING, WIREMESH IF NECESSARY | 0.2319% | HEAVY DUTY P.V.C TILE 400 x 400 x 3mm - INCLUDING ADHESIVE, WELDING - INCLUDING POLISHING WORK |  |  | <사무공간 회의실 휴게실 바닥> 비닐계타일 (데코급 or 디럭스급 ) <복도 계단실 바닥> 비닐계타일(데코급 or 디럭스급) 에폭시코팅 or 에폭시페인트 | 비닐 바닥 타일 - 300 x 300 x 3mm | 고급 PVC 타일 - 450 x 450 x 3mm
I-07 | HEAVY DUTY PVC TILE | SKIRTS W/ BEDDING, WIREMESH IF NECESSARY | 0.1092% | P.V.C SKIRTING H100 x 2T - INCLUDING ADHESIVE, WELDING |  |  |  | P.V.C SKIRTING - H100 x 3T | 비닐걸레받이 - H100 x 2T
I-08 |  |  |  | ACCESS FLOOR SYSTEM - 600 x 600 H:300 - 600mm x 600mm x Min.35mm ANTI-STATIC PVC TILE - HIGH DENSITY CHIPBOARD CORE(675 kg/m3) WRAPPED W/ 0.9mm GALV. SHEET Detail Description - INCLUDING STEPS, SUPPORTING MATERIAL & ACCESSORIES - INCLUDING ADHESIVE OR ANCHOR & POLISHING - INCLUDING SEISMIC BRACING SYSTEM FOR SUPPORT STRUCTURE INCLUDING CALCULATION
I-09 | RAISED FLOOR W/ VINYL TILE | 600 x 600 H:600 | 0.1668% | ACCESS FLOOR SYSTEM - 600 x 600 H:600 - 600mm x 600mm x Min.35mm ANTI-STATIC PVC TILE - HIGH DENSITY CHIPBOARD CORE(675 kg/m3) WRAPPED W/ 0.9mm GALV. SHEET |  |  |  | ACCESS FLOOR SYSTEM - 600 x 600 H:600 - 600mm x 600mm x 3mm ANTI-STATIC LAMINATE TILE | ACCESS FLOOR SYSTEM - 600 x 600 H:600 - 전도성 비닐타일 : 600mm x 600mm x 3mm | Tile (3mm)
I-10 |  |  |  | ACCESS FLOOR SYSTEM - 600 x 600 H:800 - 600mm x 600mm x Min.35mm ANTI-STATIC PVC TILE - HIGH DENSITY CHIPBOARD CORE(675 kg/m3) WRAPPED W/ 0.9mm GALV. SHEET
I-11 |  |  |  | ACCESS FLOOR SYSTEM - 1200 x 1200 H:1200 - 1200mm x 1200mm x Min.35mm ANTI-STATIC PVC TILE - HIGH DENSITY CHIPBOARD CORE(675 kg/m3) WRAPPED W/ 0.9mm GALV. SHEET
I-12 | NON-SLIP CERAMIC TILE | FLOOR W/ BEDDING, WIREMESH IF NECESSARY | 0.309% | UNGLAZED NON-SLIP CERAMIC TILE - FOR FLOOR - THK. 10mm / NON-SLIP TYPE - INCLUDING NON-SLIP NOSING TILE - INCLUDING BEDDING MORTAR & JOINT GROUTING & SEALANT - INCLUDING ADHESIVE & POLISHING |  |  | THK.7 논슬립자기질타일(300X300) | UNGLAZED NON-SLIP CERAMIC TILE - 기술기준서 Spec. 없음 | 논스립 바닥 타일 - 300 x 300 x 9mm
I-13 | GLAZED CERAMIC TILE | WALL W/ BEDDING, WIREMESH IF NECESSARY | 0.05539% | GLAZED CERAMIC TILE - FOR WALL - THK. 6mm - INCLUDING BEDDING MORTAR & JOINT GROUTING - INCLUDING 3mm THICK REAL CEMENT PASTE OR ADHESIVE & JOINT GROUTING & SEALANT - INCLUDING SCAFFOLDING - INCLUDING ADHESIVE & POLISHING |  |  | THK.7 도기질벽타일(300X600) | GLAZED CERAMIC TILE - 기술기준서 Spec. 없음 | 내장벽 타일 - 600 x 600 x 10mm
I-14 |  |  |  | ACID RESISTANT TILE - FOR FLOOR & BASE - THK. 300 x 300 x 16mm - INCLUDING ACID PROOF MEMBRANE, BEDDING, EPOXY BASED ADHESIVE & JOINT GROUTING - INCLUDING POLISHING
I-15 |  |  |  | ACID RESISTANT TILE - FOR WALL - THK. 300 x 300 x 16mm '- INCLUDING ACID PROOF MEMBRANE, BEDDING, EPOXY BASED ADHESIVE & JOINT GROUTING - INCLUDING POLISHING
I-16 |  |  |  | TERRAZZO TILE - FOR FLOOR - THK. 30mm - INCLUDING BEDDING & JOINT GROUTING - INCLUDING POLISHING - INCLUDING ADHESIVE - INCLUDING GRINDING WORK
I-17 |  |  |  | TERRAZZO STAIR TREAD & RISER THK. 30mm - INCLUDING ANTI-SLIP GROOVE ON TREAD - INCLUDING BEDDING & JOINT GROUTING - INCLUDING ADHESIVE - INCLUDING POLISHING
I-18 |  |  |  | TERRAZZO SKIRTING H100 x 20 mm - INCLUDING BEDDING & JOINT GROUTING - INCLUDING GRINDING WORK - INCLUDING ADHESIVE & JOINT GROUTING
I-19 |  |  |  | GRANITE STAIR TREAD & RISER THK. 20mm - INCLUDING ANTI-SLIP GROOVE - INCLUDING BEDDING & JOINT GROUTING - INCLUDING ADHESIVE - INCLUDING GRINDING & POLISHING
I-20 |  |  |  | MARBLE STAIR TREAD & RISER THK. 20mm - INCLUDING ANTI-SLIP GROOVE - INCLUDING BEDDING & JOINT GROUTING - INCLUDING ADHESIVE - INCLUDING GRINDING & POLISHING
I-21 |  |  |  | GRANITE TILE - FOR FLOOR - THK. 30mm - INCLUDING BEDDING & JOINT GROUTING - INCLUDING GRINDING WORK & POLISHING - INCLUDING ADHESIVE
I-22 |  |  |  | GRANITE TILE - FOR WALL - THK. 20mm - INCLUDING 3mm THICK REAL CEMENT PASTE OR ADHESIVE & JOINT GROUTING - INCLUDING STEEL ANCHORING & ACCESSARIES & SEALANT - INCLUDING ADHESIVE & JOINT GROUTING - INCLUDING SCAFFOLDING - INCLUDING GRANITE SKIRTING (H=100)
I-23 |  |  |  | MARBLE TILE - FOR FLOOR - THK. 30mm - INCLUDING BEDDING & JOINT GROUTING - INCLUDING GRINDING WORK & POLISHING - INCLUDING ADHESIVE
I-24 |  |  |  | MARBLE TILE - FOR WALL - THK. 20mm - INCLUDING 3mm THICK REAL CEMENT PASTE OR ADHESIVE & JOINT GROUTING - INCLUDING STEEL ANCHORING & ACCESSARIES & SEALANT - INCLUDING ADHESIVE & JOINT GROUTING - INCLUDING SCAFFOLDING - INCLUDING GRANITE SKIRTING (H=100)
I-25 |  |  |  | GRANITE / MARBLE SILL - THK. 30mm - FOR WINDOW SILL OR DIVIDING STRIP - INCLUDING BEDDING & JOINT GROUTING
I-26 |  |  |  | MARBLE COUNTER - THK. 50mm x 600mm - FOR GUARD HOUSE / COUNTER - INCLUDING BEDDING & JOINT GROUTING
I-27 |  |  |  | CARPET TILE - THK. 7mm - POLYPROPYLENE YARN IN LOOP-PILE (1/10") - ANTISTATIC - INCLUDING ADHESIVE & SURFACE TREATMENT
I-28 |  |  |  | MOSAIC TILE - FOR EXTERIOR & INT. WALL - INCLUDING BEDDING & JOINT GROUTING - INCLUDING SCAFFOLDING - INCLUDING 3mm THICK REAL CEMENT PASTE OR ADHESIVE & JOINT GROUTING
I-29 |  |  |  | WOODEN SKIRTING - H100 x 15 mm - INCLUDING ADHESIVE
J-01 | SUSPENDED ACOUSTIC CEILING SYSTEM | 600x600xTHK.15mm, NON COMBUSTIBLE | 0.7899% | ACOUSTIC MINERAL BOARD CEILING - SIZE : THK.15mm x 600 x 600mm or 300X1200mm - NON-COMBUSTIBLE CLASS B TO EN13501-1 - INCLUDING GRID, HANGER, EDGE ANGLE - INCLUDING SCAFFOLDING - INCLUDING CURTAIN BOX MADE OF COATED STEEL SHEET - INCLUDING ACCESS PANEL TO THE CEILING - INCLUDING LIGHT FIXTURE & OPENING REINFORCED WORK - INCLUDING SEISMIC BRACING SYSTEMFOR THE SUSPENSION SYSTEM INCLUDING CALCULATION |  |  | <표준시방서> M-bar 구성 : Double M-bar, Carrying Channel, Minor Channel, Hanger bolt 피스공법 석고보드하지공법 <사무공간 천정> T bar 및 압면흡음텍스 <복도 천정> M-bar + 석고보드 2ply 수성페인트 or 압면흡음텍스 | 흡음천정판 - SIZE : THK.12mm or 15mm - 불연성 무기질 섬유판, 미네랄울 흡음 천정판, KS L 9105 | 불연천장재 (미네랄울계) - SIZE : THK.12mm x 300 x 600mm | 두께 12mm 적용 T bar 적용
J-02 |  |  |  | PVC STRIP CEILING - 100mm WIDE x 15mm DEEP WTHI 25mm RECESSED - FOR TOILETS, SHOWERS CEILING
J-03 | PVC STRIP CEILING | FOR TOILET & SHOWER ROOM | 0.07412% | ALUMINIUM PANEL CEILING - SIZE : 600x600x0.5mm OR 600x1200x0.5mm - NON DIRECTIONAL PERFORATED ALUMINIUM - ACOUSTIC BLANKET (25mm LOW-DENSITY BLANKET OF GLASS FIBRE INSULATION) - INCLUDING GRID SYSTEM : GALVANIZED STEEL (MOLDING, LOCKING CLIP ETC.) - INCLUDING SUSPENSION SYSTEM : HOT DIP GAL. MILD STEEL FLATS AND/OR RODS (ROD HANGER : GAL. STEEL OF 4mm DIA.) - FIRE RESISTANCE RATING : 1/2 HOUR - INCLUDING CURTAIN BOX - EPOXY CHROMATE PRIMER 0.1mm+STOVE ENAMEL FINISH ON THE FACE - INCLUDE'G ACCESS PANEL - INCLUDING SEISMIC BRACING SYSTEM FOR THE SUSPENSION SYSTEM, IF REQUIRED |  |  | <화장실 천정재 마감기준> 1. 경량철골천정틀(M-bar) + 석고보드(2ply) 비닐페인트 or 유공흡음텍스 2. 경량철골천정틀(Clip-bar) + 열경화성수지천정판 or 알루미늄천장타일 <샤워실 천정재 마감기준> 경량철골천정틀(Clip-bar) + 열경화성수지천정판 or 알루미늄천장타일 | 알루미늄 천정판 - SIZE : THK.0.5mm or 0.6mm | AL. 천정판 - SIZE : 600x600x0.7mm | 락커룸 화장실 흡음텍스 적용검토
J-04 |  |  |  | ALUMINIUM LINEAR CEILING - ALUMINIUM STRIP : 0.5mmx100mm MODULE (W/20mm SHADOW) ALUMINIUM - AL. ALLOY 3005-H26 OR EQUAL - ACOUSTIC BLANKET (25mm LOW-DENSITY BLANKET OF GLASS FIBRE INSULATION) - INCLUDING GRID, HANGER, EDGE - INCLUDING CURTAIN BOX MADE OF COATED STEEL SHEET - EPOXY CHROMATE PRIMER 0.1mm+STOVE ENAMEL FINISH ON THE FACE - INCLUDE'G ACCESS PANEL - INCLUDING SEISMIC BRACING SYSTEM FOR THE SUSPENSION SYSTEM, IF REQUIRED
J-05 |  |  |  | SMC PANEL CEILING - SIZE : 600 x 600 x 1.2mm - SMC(SHEET MOUNDING COMPOUND) - INCLUDING GRID, HANGER, EDGE ANGLE - INCLUDING SCAFFOLDING - INCLUDING CURTAIN BOX MADE OF COATED STEEL SHEET - INCLUDING ACCESS PANEL TO THE CEILING - INCLUDING LIGHT FIXTURE & OPENING REINFORCED WORK - INCLUDING SEISMIC BRACING SYSTEM DETAIL SHALL BE APPLIED FOR THE SUSPENSION SYSTEM, IF REQUIRED
J-06 | GYPSUM BOARD | WALL, (both side) | 0.5909% | GYPSUM PLASTER BOARD PARTITION WALL(BOTH SIDE) - THK. 75mm - BOTH SIDE : THK. 12.5mm GYPSUM PLASTER BOARD - T50 MINERAL FIBRE INSULATION CORE W/ GALVANIZED METAL STUD FRAME - NON-COMBUSTIBLE & NON-INFLAMMABLE TYPE - INCLUDING ALL HARDWARES & CONNECTING/FIXING ACCESSORIES - INCLUDING JOINT TAPING, OPENING WORK & COMPOUND, SEALANT - INCLUDING SLEEVE, DOOR & WINDOW REINFORCING FRAME WORK |  |  |  | 경량 칸막이 - THK. 12.5mm | 경량 칸막이 - THK. 9.5mm
J-07 | GYPSUM BOARD | WALL (one side) | 0% | GYPSUM PLASTER BOARD PARTITION WALL(ONE SIDE) - THK. 63mm - ONE SIDE : THK. 12.5mm GYPSUM PLASTER BOARD - T50 MINERAL FIBRE INSULATION CORE W/ GALVANIZED METAL STUD FRAME - NON-COMBUSTIBLE & NON-INFLAMMABLE TYPE |  |  |  | 경량 칸막이 - THK. 12.5mm | 경량 칸막이 - THK. 9.5mm
J-08 | GYPSUM BOARD | WALL, 2HR FIRE-RATING. | 0.995% | GYPSUM PLASTER BOARD PARTITION WALL (2 HOUR FIRE RATING) - THK. 100mm - BOTH SIDE : THK. 12.5mm x 2PLIES GYPSUM PLASTER BOARD - T50 MINERAL FIBRE INSULATION CORE W/ GALVANIZED METAL STUD FRAME - NON-COMBUSTIBLE & NON-INFLAMMABLE TYPE - INCLUDING UL CERTIFICATION |  |  | T 12.5 방화석고보드 2겹 그라스울 T50 설치가능 (시험성적에 따름) | 경량 칸막이 - THK. 12.5mm | 경량 칸막이 - THK. 9.5mm | 단열재 적용예외 검토
J-09 |  |  |  | METAL FACED PLASTERBOARD PARTITIONS - THICKNESS : APPROXIMATELY 70mm - HEIGHT : APPROX. 2700mm - FRAME : GALV.STEEL TUBULAR W/ 60mm WOODEN PLINTH - SCREWLESS & INTERLOCKING TYPE - CORE : HIGH DENSITY MINERAL WOOL - ABSORPTION OF AIR BORNE SOUND : 38dBA OVER - DEMOUNTABLE W/ PLASTERBOARD (12.5mm) WRAPPED W/ ENAMELED METAL FACING ON BOTH SIDE OF METAL STUD - 1 HOUR FIRE RESISTANCE - INCLUDING ALL STUDS, HARDWARES & ACCESSORIES - INCLUDING JOINTING WORK - INCLUDING DOOR & WINDOW (DOUBLE GLAZING OF 4mm CLEAR FLOAT GLASS SET IN PVC BEAD) - INCLUDING JOINT TAPING, OPENING WORK & COMPOUND, SEALANT - INCLUDING SLEEVE,DOOR & WINDOW REINFORCING FRAME WORK
J-10 | CUBICLE PARTITION | FOR TOILET, | 0.4459% | TOILET PARTITION - HEIGHT : 2000mm - PARTITION : 30mm HIGH DENSITY CHIP BOARD W/ PVC VENEER - FRONT PANEL : 34x15x2mm ANODIZED ALUMINIUM - UNDERPANEL CLEARANCE : 150mm - INCLUDING ALL HARDWARES & ACCESSORIES(LOCKING DEVICE SOWING OCCUPYING INDICATOR) - INCLUDING U-CHANNEL 32x36x2mm - INCLUDING DOOR (W 650mm) |  |  | H=2,300 | 화장실칸막이 - 프레임 : 1.0mm STS | 화장실칸막이 - 프레임 : 1.2mm STS | 2300 적용
J-11 |  |  |  | URINAL SCREEN - HEIGHT : 1500mm, WIDE : 600mm - PARTITION : 30mm HIGH DENSITY CHIP BOARD W/ PVC VENEER - INCLUDING ALL HARDWARES & ACCESSORIES
J-12 |  |  |  | SHOWER BOOTH PARTITION - HEIGHT : 2100mm - THK. 10mm TEMPERED SAFETY GLASS - INCLUDING STAINLESS STEEL FRAME AROUND GLASS - INCLUDING ALL HARDWARES & ACCESSORIES -INCLUDING JOINTING WORK
J-13 |  |  |  | FIRE RESISTANT GLAZED PARTITION - HEIGHT : 3000mm - SURFACE : FIRE PROOF COATING - PANEL LINING : 90 MINUTES FIRE RESITIVITY GLAZING - HEAT RESISTANCE : 650℃ - INCLUDING GRID, HANGER, EDGE - INCLUDING 90 MINUTES RESISTANT DOOR, WINDOWS & HARDWARES
J-14 |  |  |  | TIMBER WALL PANEL - HEIGHT 2150mm - FOR WALL - INCLUDING ALL HARDWARES & ACCESSORIES - INCLUDING JOINTING WORK - ALL TIMBER SHALL BE OF EITHER GRADE ‘A’ OR GRADE ‘B’ TIMBER
J-15 |  |  |  | GLASS PARTITION WALL -THK. 10mm TEMPERED SAFETY GLASS - INCLUDING STAINLESS STEEL FRAME AROUND GLASS - INCLUDING ALL HARDWARES & ACCESSORIES(LOCKING DEVICE)
K-01 | SANDWICH PANEL W/FLASHING IF NECESSORY | ROOF | 1.057% | THERMAL INSULATED TRAPEZOIDAL CLADDING FOR ROOF -EXTERIOR SKIN: TRAPEZOIDAL PROFILE MIN. 0.8T P.V.D.F coating, galvanized steel sheet - CORE: NON-COMBUSTIBLE MATERIAL ACCORDING TO ASTM or EQUIVALENT, MIN thk 200mm. Glass wool, density over 64kg/m3 -INTERIOR SKIN: TRAPEZOIDAL PROFILE MIN. 0.8T P.V.D.F coating, galvanized steel sheet - HEAVY EPOXY BASE COAT AND A HIGH BUILD WEATHER COAT OF POLYURETHANE - AS PER ASTM E1886 AND E1996. - INCLUDING ALL FLASHING(Roof ridge flashing for top & side, Corner & Joint flashing, door & window flashing , Opening flashing , parapet flashing and etc. ) - INCLUDING ACCESSORIES (ANCHOR, PLATE), SEALANT, BACK UP & JOINT FILLING MATERIAL (AROUND OPENING AREA) - INCLUDING SCAFFOLDING - INCLUDING DOOR & WINDOW SUNSHADE - INCLUDING PROTECTION FILM ON SURFACE OF PRODUCTS TILL SITE. - 10 YEAR GUARANTEE - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION - QUANTITIES ARE PROJECTED AREA | • The thermal conductivity value of wall panel must below 0.24 W/m2.K. • Metal sandwich panel shall have sufficient strength to resist the site environmental conditions especially the salt laden atmosphere and wind pressure. • The roof panel shall have strength to withstand the dead load of 100 kg/m2 • Metal sandwich panel shall be of hot-dipped galvanized steel, according to KS D 3506 or ASTM A653/653M, coated polyvinylidene fluoride (PVDF) on exposed surface at shop. The coating shall consist of epoxy primer coat of 5 micron thick and PVDF coat of 20 micron thick. • Metal sandwich panel shall consist of the following: - Exterior sheet : 0.8T P.V.D.F coating, galvanized steel sheet - Interior sheet : 0.8T P.V.D.F coating, galvanized steel sheet - Insulation : Glass wool, density over 64kg/m3 • Color shall be submitted to the KOSPO for approval. • The accessories shall be the same as metal sandwich panel. • Roof Thermal Transmittance ≤ 0.24 W/m2K |  | 강판 : 0.6T 코팅 : 불소 25±5 mic, 실리콘 20±5 mic. 단열 : 그라스울 64K, THK. 50 / 75/ 100 (도면에 따라) 규격 : w=1.0, L=최대 15m 색상 : 3.6PB 4.2/6.2 (RAL5000) | Metal Sandwich Panel for Roof - Exterior sheet : 0.8T P.V.D.F coating, galvanized steel sheet - Interior sheet : 0.8T P.V.D.F coating, galvanized steel sheet - Insulation : Glass wool, density over 64kg/m3 | 샌드위치 패널 - 상하표면재 : 0.5mm, 착색아연도강판(실리콘폴리에스터) 중간단열재(그라스울), 100mm, 0.034 W/mK 이하 (48k이상) | 강판두께 조정으로 절감가능한지 검토
K-02 | SANDWICH PANEL W/FLASHING IF NECESSORY | WALL | 1.702% | THERMAL INSULATED TRAPEZOIDAL CLADDING FOR EXT. WALL -EXTERIOR SKIN: TRAPEZOIDAL PROFILE MIN. 0.8mm P.V.D.F coating, galvanized steel sheet - CORE: NON-COMBUSTIBLE MATERIAL ACCORDING TO ASTM or EQUIVALENT, MIN.thk 120mm Glass wool, density over 64kg/m3 -INTERIOR SKIN: TRAPEZOIDAL PROFILE MIN. 0.6mm Silicone coating, galvanized steel sheet - HEAVY EPOXY BASE COAT AND A HIGH BUILD WEATHER COAT OF POLYURETHANE - AS PER ASTM E1886 AND E1996. - INCLUDING ALL FLASHING(Roof ridge flashing for top & side, Corner & Joint flashing, door & window flashing , Opening flashing , parapet flashing and etc. ) - INCLUDING ACCESSORIES (ANCHOR, PLATE), SEALANT, BACK UP & JOINT FILLING MATERIAL (AROUND OPENING AREA) - INCLUDING SCAFFOLDING - INCLUDING DOOR & WINDOW SUNSHADE - INCLUDING PROTECTION FILM ON SURFACE OF PRODUCTS TILL SITE. - 10 YEAR GUARANTEE - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION - QUANTITIES ARE PROJECTED AREA | • The thermal conductivity value of wall panel must below 0.45 W/m2.K. • Metal sandwich panel shall have sufficient strength to resist the site environmental conditions especially the salt laden atmosphere and wind pressure. • Metal sandwich panel shall be of hot-dipped galvanized steel, according to KS D 3506 or ASTM A653/653M, coated polyvinylidene fluoride (PVDF) on exposed surface at shop. The coating shall consist of epoxy primer coat of 5 micron thick and PVDF coat of 20 micron thick. • Metal sandwich panel shall consist of the following: - Exterior sheet : 0.8T P.V.D.F coating, galvanized steel sheet - Interior sheet : 0.6T Silicone coating, galvanized steel sheet - Insulation : Glass wool, density over 64kg/m3 • Color shall be submitted to the Owner for approval. • The metal flashing shall be the minimum thickness of 0.8 mm and the coating shall be applied the same as the mentioned above. Main fasteners (Hilti, hook bolt, self tapping of self drilling/self tapping screws, blind rivets) are applied to the external side of the sheet through the center of every other through, at every girt. Fasteners should be placed in every through at end laps and sheet ends. Fasteners should have neoprene washer sealer or sealing flange. • Outside Wall Thermal Transmittance ≤ 0.45 W/m2K |  | 강판 : 0.6T(외부) 0.5T(내부) 코팅 : 불소 25±5 mic, 실리콘 20±5 mic. 단열 : 그라스울 64K, THK. 50 / 75/ 100 (도면에 따라) (0.034W/mK) 규격 : w=1.0, L=최대 15m 색상 : RAL 7035 (8.5GY 8.3/0.8) | Metal Sandwich Panel for Wall - Exterior sheet : 0.8T P.V.D.F coating, galvanized steel sheet - Interior sheet : 0.6T Silicone coating, galvanized steel sheet - Insulation : Glass wool, density over 64kg/m3 | 샌드위치 패널 - 상하표면재 : 0.5mm, 착색아연도강판(실리콘폴리에스터) 중간단열재(그라스울), 50mm, 0.034 W/mK 이하 (48k이상) | 단가검토 후 상세변경 내부 가드 확인
K-03 | SANDWICH PANEL W/FLASHING IF NECESSORY | WALL, 2HOUR FIRE RATING | 0% | THERMAL INSULATED TRAPEZOIDAL METAL CLADDING (EXTERIOR WALL, 2HR FIRE RATING) -EXTERIOR SKIN: MIN. 0.7mm GALVANIZED AND FACTORY FINISHED STEEL SHEET - CORE: NON-COMBUSTIBLE MATERIAL ACCORDING TO ASTM or EQUIVALENT, MIN.thk 120mm Glass wool, density over 64kg/m3 -INTERIOR SKIN: MIN. 0.7mm GALVANIZED AND FACTORY FINISHED STEEL SHEET - AS PER ASTM E1886 AND E1996. - INCLUDING UL CERTIFICATION - INCLUDING ALL FLASHING(Roof ridge flashing for top & side, Corner & Joint flashing, door & window flashing , Opening flashing , parapet flashing and etc. ) - INCLUDING ACCESSORIES (ANCHOR, PLATE), SEALANT, BACK UP & JOINT FILLING MATERIAL (AROUND OPENING AREA) - INCLUDING SCAFFOLDING - INCLUDING DOOR & WINDOW SUNSHADE - INCLUDING PROTECTION FILM ON SURFACE OF PRODUCTS TILL SITE. - 10 YEAR GUARANTEE - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION - QUANTITIES ARE PROJECTED AREA |  |  |  | - | -
K-04 | GALVANIZED STEEL SHEET W/FLASHING IF NECESSORY | ROOF | 0.06632% | SINGLE TRAPEZOIDAL CLADDING FOR ROOF - MIN. THK. 0.6mm GALVANIZED STEEL SHEETS, 35/180 TRAPEZOIDAL PROFILE W/ FACTORY APPLIED FINISH FLUROPOLYMER KYNAR-500(19μm) - INCLUDING ALL FLASHING(Roof ridge flashing for top & side, Corner & Joint flashing, door & window flashing , Opening flashing , parapet flashing and etc. ) - INCLUDING ACCESSORIES (ANCHOR, PLATE), SEALANT, BACK UP & JOINT FILLING MATERIAL (AROUND OPENING AREA) - INCLUDING SCAFFOLDING - INCLUDING DOOR & WINDOW SUNSHADE - INCLUDING PROTECTION FILM ON SURFACE OF PRODUCTS TILL SITE. - 10 YEAR GUARANTEE - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION - QUANTITIES ARE PROJECTED AREA |  | THK. 0.6mm SINGLE TRAPEZOIDAL METAL CLADDING | 강판 : 0.6T, 칼라강판 홑겹(V-115) 코팅 : 불소 25±5 mic, 실리콘 20±5 mic. | SINGLE TRAPEZOIDAL CLADDING FOR ROOF - 기술기준서 Spec. 없음 | SINGLE TRAPEZOIDAL CLADDING FOR ROOF - 기술기준서 Spec. 없음
K-05 | GALVANIZED STEEL SHEET W/FLASHING IF NECESSORY | Wall | 0.03306% | SINGLE TRAPEZOIDAL CLADDING FOR WALL - MIN. THK. 0.6mm GALVANIZED STEEL SHEETS, 35/180 TRAPEZOIDAL PROFILE W/ FACTORY APPLIED FINISH FLUROPOLYMER KYNAR-500(19μm) - INCLUDING ALL FLASHING(Roof ridge flashing for top & side, Corner & Joint flashing, door & window flashing , Opening flashing , parapet flashing and etc. ) - INCLUDING ACCESSORIES (ANCHOR, PLATE), SEALANT, BACK UP & JOINT FILLING MATERIAL (AROUND OPENING AREA) - INCLUDING SCAFFOLDING - INCLUDING DOOR & WINDOW SUNSHADE - INCLUDING PROTECTION FILM ON SURFACE OF PRODUCTS TILL SITE. - 10 YEAR GUARANTEE - QUANTITIES OF LAP SPLICE TO BE CONSIDERED FOR QUOTATION - QUANTITIES ARE PROJECTED AREA |  |  | 하단부 몰딩은 알미늄(2T) 재질로하여 하부에 10mm구멍을 1m 간격으로 설치 벽체고정은 STS 후크 볼트 | SINGLE TRAPEZOIDAL CLADDING FOR WALL - 기술기준서 Spec. 없음 | SINGLE TRAPEZOIDAL CLADDING FOR ROOF - 기술기준서 Spec. 없음
K-06 |  |  |  | TRANSLUCENT SHEET - GLASS FIBRE SHEET (FRP) THK. 2.0mm - 85% LIGHT TRANSMISSION - UV RESISTANCE - INCLUDING ACCESSORIES, SEALANT, BACK UP & JOINT FILLING MATERIAL - INCLUDING SCAFFOLDING
K-07 |  |  |  | FLASHING - STEEL STEET : GALVANIZED STEEL SHEET (ASTM-A653/A653M G90,275 g/m2) W/ TRAPEZOIDAL PROFILE - COATING : 25 microns POLYVINYLIDENE FLUORIDE
K-08 | GUTTER | EAVE GUTTER. | 0.3238% | GUTTER - THK. 1.2mm GALVANIZED STEEL SHEET - W230mm x H250mm - INCLUDING INSULATION, GUTTER HANGER, ANCHOR & SEALANT - INDLUD'G FIXING & JOINTING - INCLUDING SCAFFOLDING - INCLUDING ALL FLASHING |  |  | <우수홈통 TPO 시트 덧씌우기 공사> KS F 4911 합성고분자계방수시트 중 보강복합형 방수시트 사용 기존 지붕강판과 같거나 유사한 색상 | GUTTER - 기술기준서 Spec. 없음 | GUTTER - THK. 1.5mm, 스테인리스강 / 마감코킹 포함 | TPO 시트 항목추가 TPO 시트 자료 조사
K-09 |  |  |  | PARAPET/TOP CAPPING FLASHING - 0.75mm GALVANIZED STEEL SHEET - W600mm - INDLUD'G FIXING & JOINTING - INCLUDING SCAFFOLDING
K-10 |  |  |  | ROOF RIDGE FLASHING (TOP & SIDE) - 0.75mm GALVANIZED STEEL SHEET - W500mm
K-11 |  |  |  | CORNER/JOINT FLASHING - 0.75mm GALVANIZED STEEL SHEET - W400mm
K-12 |  |  |  | DOOR & WINDOW FLASHING - 0.75mm GALVANIZED STEEL SHEET - W230mm
K-13 |  |  |  | BASE FLASHING - 1.2mm GALVANIZED STEEL SHEET - W200mm
K-14 |  |  |  | OPENING FLASHING - 0.75mm GALVANIZED STEEL SHEET - W200mm
K-15 | ROOF DRAIN (Φ100 / CAST IRON) | FOR BUILDING | 0% | ROOF DRAIN Φ100 / CAST IRON - Φ100 / CAST IRON |  |  | <사이포닉 우수배관 사용하는 경우> GEBERIT HDPE(열처리 거친제품) 또는 동등이상 신축팽창률 1% 이하 GEBERIT에서 제시한 규격 사용 | ROOF DRAIN - 기술기준서 Spec. 없음 | 루프드레인 - 주철제, Φ75~Φ250 - STS, Φ75~Φ250
K-16 | ROOF DRAIN (Φ150 / CAST IRON) | FOR BUILDING | 0.03699% | ROOF DRAIN Φ150 / CAST IRON - Φ150 / CAST IRON |  |  |  | ROOF DRAIN - 기술기준서 Spec. 없음 | 루프드레인 - 주철제, Φ75~Φ250 - STS, Φ75~Φ250
K-17 |  |  |  | ROOF DRAIN Φ100 / UPVC - Φ100 / UPVC
K-18 |  |  |  | ROOF DRAIN Φ150 / UPVC - Φ150 / UPVC
K-19 | DOWNSPOUT(Φ100 / GALV. STL) | FOR BUILDING, GALV. STEEL. | 0.01816% | DOWN SPOUT Φ100 / GALV. STL - Φ100 / GALV. STL. W/ FACTORY COAT OR ALUMINIUM TYPE - □100 / ALUMINIUM x MIN. 0.75 mm - INCLUDING DOWN SPOUT HANGER & ANCHOR - INCLUDING EPOXY PAINT |  |  |  | 선홈통 - STS (건물의 외부에 노출되는 선홈통은 스테인레스 제품) | 선홈통 - STS, 1.5mm, Φ75~Φ250
K-20 | DOWNSPOUT(Φ150 / GALV. STL) | FOR BUILDING, GALV. STEEL. | 0.5069% | DOWN SPOUT Φ150 / GALV. STL - Φ150 / GALV. STL. W/ FACTORY COAT OR ALUMINIUM TYPE - □150 / ALUMINIUM x MIN. 0.75 mm - INCLUDING DOWN SPOUT HANGER & ANCHOR - INCLUDING EPOXY PAINT |  |  |  | 선홈통 - STS (건물의 외부에 노출되는 선홈통은 스테인레스 제품) | 선홈통 - STS, 1.5mm, Φ75~Φ250
K-21 |  |  |  | DOWN SPOUT Φ100 / UPVC - Φ100 / UPVC W/ FACTORY COAT OR ALUMINIUM TYPE - INCLUDING DOWN SPOUT HANGER & ANCHOR
K-22 |  |  |  | DOWN SPOUT Φ150 / UPVC - Φ150 / UPVC W/ FACTORY COAT OR ALUMINIUM TYPE - INCLUDING DOWN SPOUT HANGER & ANCHOR
K-23 | WATER COLLECTION BOX | GALV. STEEL DOWN SPOUT HEAD | 0.04623% | DOWN SPOUT HEAD GALV. STL. - GALV. STL. FOR DOWN SPOUT OR ALUMINIUM TYPE |  |  |  | 선홈통 - STS (건물의 외부에 노출되는 선홈통은 스테인레스 제품) | DOWN SPOUT HEAD - 기술기준서 Spec. 없음
K-24 |  |  |  | DOWN SPOUT HEAD UPVC - UPVC FOR DOWN SPOUT
K-25 |  |  |  | SPLASH BLOCK - PC BLOCK
K-26 |  |  |  | NORMAL WEIGHT CONCRETE PRECAST INSULATED SANDWICH PANEL - THK. 325 MM - DEEP SAND BLASTING FINISH W/ WHITE CEMENT (EXT) - SMOOTH FINISH W/ GREY CEMENT (INT) - STEEL PLATE INSERTS EMBEDDED FOR INSTALLATION TO STEEL COLUMN ON SIDES - INCLUDING ACCESSORIES, ANCHORING & GROUT - INCLUDING LABOR & EQUIPMENT FOR ERECTION
K-27 |  |  |  | LIGHT WEIGHT CONCRETE PRECAST INSULATED SANDWICH PANELS (SIPOREX PANEL) - 600(H) X 1200(L) THK. 250mm - 2 COATS OF TEXTURED WATERPROOF PAINT (EXT) - 2 COATS OF PAINT (INT)
L-01 |  |  |  | FIRE RESIST. STEEL DOOR - 0.5 HOUR FIRE DOOR - INCLUDING UL CERTIFICATION - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT. - INCLUDING SIGN PLATE OF ANODIZED ALUMINIUM OR STAINLESS STEEL - HYDRAULIC DOOR CLOSERS SHALL BE FITTED TO ALL DOORS IN AIR- CONDITIONED AREA - DUST PROOF(FOR EXT.DOOR)
L-02 | FIRE RESIST. STEEL DOOR W/90 MIN (1.0 x2.1) | SINGLE DOOR W/HARDWARE | 0.69% | FIRE RESIST. STEEL DOOR - 1.5 HOUR FIRE DOOR - INCLUDING UL CERTIFICATION - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT. - INCLUDING SIGN PLATE OF ANODIZED ALUMINIUM OR STAINLESS STEEL - HYDRAULIC DOOR CLOSERS SHALL BE FITTED TO ALL DOORS IN AIR- CONDITIONED AREA - DUST PROOF(FOR EXT.DOOR) |  |  | <맨도어, 창고 등 스틸도어> 문틀 : 1.6T STL PLATE 문짝 : T1.2 STL PLATE 충진 : GLASS WOOL 50K 도장 : 방청도료 후 정전분체 도장 (외부 : 방청페인트 위 조합페인트) 관시창 : 필요시 T5 투명유리 (외부 : T16 복층유리) | - | -
L-03 | NORMAL STEEL DOOR (1.0 x2.1) (2.0x 2.1) | SINGLE DOOR W/HARDWARE | 0.53% | NORMAL STEEL DOOR - DOOR FRAME : 1.6mm THK GALVANOZED STEEL PLATER - DOOR : 1.2mm THK GALVANIZED STEEL PLATE - INSULATION : 50mm THK GALSS WOOL - COATING : EPOXY PRIMER 75μm + POLYURETHANE PAINT 50 μm - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT ETC.) - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING PANIC BARS FOR DOORS ON ESCAPE ROUTE - INCLUDING WEATHER STRIP FOR EXT. - INCLUDING SIGN PLATE OF ANODIZED ALUMINIUM OR STAINLESS STEEL - HYDRAULIC DOOR CLOSERS SHALL BE FITTED TO ALL DOORS IN AIR- CONDITIONED AREA - DUST PROOF(FOR EXT.DOOR) |  |  | <변전실 장비반입구> 양개문 사이즈 : 도어 3,000 x 2,500 <맨도어, 창고 등 스틸도어> 문틀 : 1.6T STL PLATE 문짝 : T1.2 STL PLATE 충진 : 내부 : PAPER HONEY COMB (외부: GLASS WOOL 50K) 도장 : 방청도료 후 정전분체 도장 (외부 : 방청페인트 위 조합페인트) 관시창 : 필요시 T5 투명유리 (외부 : T16 복층유리) <사무실 및 공용공간> 강화유리도어 (T12) 문틀 : T1.2 STL PLATE 문짝 : T12 강화유리 내부 : 재료분리대 외부 : 외부경사로 (빗물차단) 도장 : 헤어라인 미러/수퍼미러 등 추가 : 시선차단용 필름 내면 : 2면프레임/코너힌지 외부 : 4면프레임 플로어힌지 <사무동 주출입구, VIP 출입구> 오토슬라이딩도어 재질 : STS/강화유리 자동개폐형 난방공간에 면할 경우 방풍고려 FRAME : THK.1.5 50X100 STS FRAME 마감 : 헤어라인, 미러마감 유리 : THK.12 강화유리, 고정창 : THK10 강화유리 철물 : 기타부속철물 일체 개구부유효폭 : 1.4m 이상 | NORMAL STEEL DOOR - DOOR FRAME : 1.6mm THK GALVANOZED STEEL PLATE - DOOR : 1.2mm THK GALVANIZED STEEL PLATE - INSULATION : 50mm THK GALSS WOOL - COATING : EPOXY PRIMER 75μm + POLYURETHANE PAINT 50 μm | 철문 - 문틀 : 1.6mm THK / 녹막이페인트, 조합페인트 3회 - 문 : 1.2mm THK / 녹막이페인트, 조합페인트 2회 - 충진단열재 : 그라스울 (48K) | CCB 주출입문 유리문 반영 도어개수추가(RISK 대비차원)
L-04 | SHUTTER (6.0 x 6.0) | W/HARDWARE | 0.42% | ROLL-UP SHUTTER DOOR - ELECTRICALLY OPERATED TYPE W/ MANUAL OPERATION - MIN. 1.2T ANODIZED ALUMINUM OR GALVANIZED STEEL SHEET - INCLUDING ALL HARDWARE - INCLUDING ALL FRAME AND ACCESSORIES - INCLUDING SIDE GUIDE RAIL AND BOTTOM RAIL AND OTHER ACCESSARIES INCLUDING ESCAPE DOOR AND WIND LOCK IF REQUIRED - INCLUDING PAINT WORK(2 COATS SEMI-GLOSS ENAMEL ON METAL PRIMER) - INCLUDING SHUTTER BOX |  |  | 변전실 장비반입구 셔터 : 3,000 x 3,700 <기계,전기실 등 장비반입구> SLAT: 철판두께 1.2T, 알루미늄 1.0T 개폐속도 : 2.5m/min 이상 문틀재질 : E.G.I / STS / STL / AL | ROLL-UP SHUTTER DOOR - ELECTRICALLY OPERATED TYPE W/ MANUAL OPERATION - MIN. 1.2T ANODIZED ALUMINUM OR GALVANIZED STEEL SHEET | 알루미늄 내풍압 셔터 - 1.3mm 이중알루미늄(압출 이중단열, 방음, 내풍압) | 전기사양 추가필요
L-05 |  |  |  | FOLDING DOOR - TOP HUNG FOLDING HEAVY DUTY TYPE - THK. 1.5mm STEEL SHEET W/ INSULATED DOUBLE SKIN - THK. 60mm (MIN.) - GALAVINIZED - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT, PANIC LATCH. ETC.) - INCLUDING PEDESTRIAN DOOR INTERGRADED IN THE FOLDING DOOR
L-06 |  |  |  | AUTOMATIC SLIDING DOOR -THK. 10mm TEMPERED SAFETY GLASS - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT, PANIC LATCH. ETC.) - INCLUDING STAINLESS STEEL FRAME AT TOP & BOTTOM ONLY - INCLUDING AUTOMATIC SYSTEM
L-07 |  |  |  | STAINLESS STEEL DOOR (GLASS SWING DOOR) - DOOR : THK. 12mm TEMPERED SAFETY GLASS - FIXED GLASS : THK. 8mm TEMPERED SAFETY GLASS - INCLUDING ALL HARDWARES (HINGE, LOCK, DOOR CLOSER, DOOR STOPPER, FLUSH BOLT, PANIC LATCH. ETC.) - INCLUDING STAINLESS STEEL FRAME - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME
L-08 |  |  |  | TIMBER FLUSH DOOR - THK. 42mm (9 PLIES) - FACE VENEER : 12 mm DRIED WOOD, 5 mm PLYWOOD - INSIDE VENEER : 3 PLY PANEL W/ EACH 1.4mm THK. - WOOD LEAF FRAME : 65x32mm, 25x45mm - DOOR FRAME : STEEL FRAME W/THK. 40mm W/ RUBBER SEALING - SOUND INSULATION : 35~40 Db - INCLUDING ALL HARDWARES AND ACCESSARIES REQUIRED ACCORDING to ITB OR PROJECT REQUIREMENT (SUCH as PANIC BAR, LOCKSET, HINGES, DOOR CLOSER, ETC.) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME - ALL TIMBER SHALL BE OF EITHER GRADE ‘A’ OR GRADE ‘B’ TIMBER
L-09 |  |  |  | PLYWOOD DOOR - THK. 42mm (9 PLIES) - FACE VENEER : 12 mm DRIED WOOD, 5 mm PLYWOOD - INSIDE VENEER : 3 PLY PANEL W/ EACH 1.4mm THK. - WOOD LEAF FRAME : 65x32mm, 25x45mm - DOOR FRAME : STEEL FRAME W/THK. 40mm W/ RUBBER SEALING - SOUND INSULATION : 35~40 Db - INCLUDING ALL HARDWARES AND ACCESSARIES REQUIRED ACCORDING to ITB OR PROJECT REQUIREMENT (SUCH as PANIC BAR, LOCKSET, HINGES, DOOR CLOSER, ETC.) - INCLUDING MORTAR FILLING INTO DOOR FRAME & SEALANT AROUND DOOR FRAME
L-10 |  |  |  | HANGER DOOR - INCLUDING ALL HARDWARES - INCLUDING RAIL
L-11 | MASTER KEY SYSTEM |  | 0.002055% | MASTER- KEY SYSTEM - GRAND MASTER KEYS : 10 NOS - MASTER KEYS ; 10 NOS. PER EACH GROUP - SUB-MASTER KEYS ; 5 NOS. PER EACH BLDG - SINGLE KEYS ; 3 NOS. PER EACH DOOR - BLANK KEYS : 4 NOS. PER EACH BLDG - FOR WHOLE PLANT - INCLUDING PROFILE CYLINDER - MASTER KEY SYSTEM SHALL BE SUBJECT TO CONTRACTOR'S APPROVAL |  |  |  | - | -
M-01 | ALUMINUM WINDOW (1.2 x 1.2) | DOUBLE GLASS / W/HARDWARE | 0.27% | ALUMINUM WINDOW - ANODIZED HEAVY DUTY COATING - DOUBLE SOLAR REFLECTIVE GLASS (THK. 6mm) W/ 12mm AIR SPACE - INCLUDING ALL HARDWARES STAINLESS STEEL (SUCH AS LOCKSET AND CRESENT) - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING MORTAR FILLING INTO WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY ) - INCLUDING AL.SUB-FRAME & NYLON COATED INSECT SCREEN AT OPEN AREA ONLY( EXT. WINDOW ONLY ) | • Outside Window(except double glassing) Thermal Transmittance ≤ 2.70 W/m2K |  | <알루미늄 합금제 창호> 창호재질 : KS D 6759 또는 동등 이상 창세트 : KS F 3117, KS F 3109에 적합한 제품 알루미늄합금 압출형재 및 판재의 표면처리 : KS D 8301 또는 KS D 8303 부재두께 : 1.35mm <지붕고창> 갤러리창호 적용검토 (투명 폴리카보네이트 4.5T 110mm) 최대 1,800 x 2,000 알루미늄 프로젝트(Top hung)창 고려 (적층형 폴리카보네이트) | ALUMINUM WINDOW - ANODIZED HEAVY DUTY COATING - DOUBLE SOLAR REFLECTIVE GLASS (THK. 6mm) W/ 12mm AIR SPACE | 알루미늄창호 - 불소수지 알루미늄 - 24(6칼라유리+12공기층+6투명유리) | KS F 2229 기밀성 1등급 사양 기재 에너지성능지표 검토결과 반영 - 창 : 로이유리 vs일반유리 - 단열재 PVC창호(18mm 복층유리 적용) 단가확인 후 변경검토 터빈빌딩 창 구분 - PVC - Fixed Window (상부)
M-02 |  |  |  | ALUMINUM WINDOW - ANODIZED HEAVY DUTY COATING - DOUBLE GLASS (THK. 6mm) W/ 12mm AIR SPACE - INCLUDING ALUMINUM ACCORDION SHUTER FOR COVERING OF WINDOW - INCLUDING ALL HARDWARES STAINLESS STEEL (SUCH AS LOCKSET AND CRESENT) - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING MORTAR FILLING INTO WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY ) - INCLUDING AL.SUB-FRAME & NYLON COATED INSECT SCREEN AT OPEN AREA ONLY( EXT. WINDOW ONLY )
M-03 |  |  |  | ALUMINUM WINDOW - ANODIZED HEAVY DUTY COATING - SINGLE GLASS (THK. 6mm) - INCLUDING ALL HARDWARES STAINLESS STEEL (SUCH AS LOCKSET AND CRESENT) - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING MORTAR FILLING INTO WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY ) - INCLUDING AL.SUB-FRAME & NYLON COATED INSECT SCREEN AT OPEN AREA ONLY( EXT. WINDOW ONLY )
M-04 |  |  |  | ALUMINUM WINDOW - SINGLEE GLASS (TEMPERED) - ANODIZED HEAVY DUTY COATING - SINGLE GLASS (THK. 6mm) - SOLARCOOL GRAYLITE® FLOAT GLASS - INCLUDING ALL HARDWARES STAINLESS STEEL (SUCH AS LOCKSET AND CRESENT) - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING MORTAR FILLING INTO WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY ) - INCLUDING AL.SUB-FRAME & NYLON COATED INSECT SCREEN AT OPEN AREA ONLY( EXT. WINDOW ONLY )
M-05 |  |  |  | FIRE RESIST. WINDOW - ANODIZED HEAVY DUTY COATING - GLAZING AS PER TECH. SPEC. - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING MORTAR FILLING INTO WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY ) - INCLUDING AL.SUB-FRAME & NYLON COATED INSECT SCREEN AT OPEN AREA ONLY( EXT. WINDOW ONLY )
M-06 |  |  |  | ALUMINIUM GLAZED WALL - ANODIZED HEAVY DUTY COATING - HARDWARE : STAINLESS STEEL, DOUBLE GLASS (THK. 6mm) W/ 12mm AIR SPACE - INCLUDING ALL GLAZING & HARDWARES - INCLUDING SEALANT AROUND WINDOW FRAME - INCLUDING AL. WINDOW SILL FLASHING ( EXT. WINDOW ONLY )
M-07 | ALUMINUM LOUVER | 1400x1000 | 0.1% | ALUMINIUM LOUVER - ANODIZED HEAVY DUTY COATING - W/ ENCLOSING FRAME - STAINLESS STEEL FLY SCREENS - BIRD GUARD ON THE INSIDE - AS PER AMCA 540 & AMCA 550 - MIN. & MAX. OPENING SIZE IN ANY DIRECTION: > 1/4 INCH AND NOT > 1 INCH |  |  |  | ALUMINIUM LOUVER - ANODIZED HEAVY DUTY COATING - W/ ENCLOSING FRAME - STAINLESS STEEL FLY SCREENS | ALUMINIUM LOUVER - 기술기준서 Spec. 없음
M-08 |  |  |  | ALUMINUM SUNSHADE LOUVER - ANODIZED HEAVY DUTY COATING - SUNSHADE LOUVER - THK.2x200 BLADE - AL. ANODIZED FRAME SLAT & FLASHING - ALL ACCESSORIES INCLUDING AL. BRACKET, SUPPORT, FLASHING, ETC. - LOUVER TO BE INSTALLED AT 40 cm IN FRONT OF WINDOW
M-09 |  |  |  | ALUMINIUM STRIP WINDOW FOR U-SHAPE GLAZING - INCLUDING U-SHAPE PUTTYLESS DOUBLE GLAZING - INCLUDING ALUMINIUM WINDOW SILL - INCLUDING AL. WINDOW FRAME AND SEALANT AT ALL JOINTS
N-01 | MISC STEEL | GALVANIZED. | 0.08% | MISC. STEEL WORK (GALVANIZED) - FOR EMBEDDED PLATE(FOR PIT COVER), SLEEVE, CORNER ANGLE FOR TRENCH COVER AND CHK'D PLATE - HOT DIP GALVANIZED (4 MILS, 100 MICRONS) - STEEL : ASTM A36, ASTM A572 GRADE 50 / KS D 3515 SM355 - INCLUDING ERECTION & SHOP DWG. - INCLUDING ERECTION MATERIAL, EQUIPMENT (HIGH STRENGTH BOLT/NUT/WASHER, ACCESSORIES) - INCLUDING PAINTING, TOUCH-UP PAINTING & GRINDING, SCAFFOLDING WORK (IF NECESSARY) - INCLUDING TESTING AS PER TECH.SPEC. - INCLUDING FIXING ANGLE AT MISC STEEL WORK |  |  |  | - | -
N-02 |  |  |  | MISC. STEEL WORK (PAINTED) - FOR EMBEDDED PLATE(FOR PIT COVER), SLEEVE, CORNER ANGLE FOR TRENCH COVER AND CHK'D PLATE - STEEL : ASTM A36, ASTM A572 GRADE 50 - PAINT : BLASTING SIS SA 2 1/2 OR EQUIVALENT, 1 COAT ZINC EPOXY PRIMER (80㎛) 1 COAT EPOXY HIGH SOLID (80㎛) - DFT : TOTAL 160㎛
N-03 | GRATING | THK.>=32MM, GALVANIZED | 0.9577% | GALV. STEEL GRATING - FOR TRENCH COVER, PLATFORM, STAIR LANDING & TREAD ETC. - HOT DIP GALVANIZED (4 MILS, 100 MICRONS) - BEARING BAR : DEPTH 32 OR 40mm x 5mm AT 30 MM C/C - CROSS BAR : 6mm Square Bar AT 100 MM C/C - STEEL : KS D 3503 SS275 - INCLUDING TOE PLATE, STAIR TREAD, BOLT OR CLIP - INCLUDING 4 NOS. GRATING CLAMP PER PANEL - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING FIXING ANGLE, ANCHOR BOLT FOR FIXING ANGLE - INCLUDING AS PER APPROVED SHOP DRAWING | Steel for grating, banding and stair treads shall conform to ASTM A569. Grating for floor and walkways shall have 5 mm thick, 32 mm deep bearing bars, I type, hot dip galvanized, spaced at 30 mm center to center with 5 mm cross bars spaced at 100 mm center to center. Grating shall span a maximum or 1.6 meters measured center to center of support beam. Stair treads shall have 5 mm thick, 25 mm ~ 32 mm deep bearing, I type, hot dip galvanized, bars spaced at 30 mm center to center with 5 mm cross bars spaced at 100 mm center to center. |  |  | GALV. STEEL GRATING - BEARING BAR : DEPTH 32 OR 40mm x 5mm AT 30 MM C/C - CROSS BAR : 6mm Square Bar AT 100 MM C/C | 그레이팅 - BEARING BAR : DEPTH 32mm x 5mm AT 30 MM C/C - CROSS BAR : 6mm Square Bar AT 100 MM C/C
N-04 | CHECKERED PLATE | GALVANIZED, 6 MM | 0.0602% | CHECKERED PLATE - FOR TRENCH COVER, PLATFORM, ETC. - HOT DIP GALVANIZED (4 MILS, 100 MICRONS) - THK. 6mm - RAISED DIAMOND PATTERN - INCLUDING FIXING BY COUNTERSUNK, FLAT HEAD BOLT OR SCREW - INCLUDING DRAIN & LIFTING HOLE AS PER APPROVED SHOP DRAWING - INCLUDING FIXING ANGLE, ANCHOR BOLT FOR FIXING ANGLE - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING |  |  |  | CHECKERED PLATE (무늬강판) - 기술기준서 Spec. 없음 | CHECKERED PLATE (무늬강판) - 기술기준서 Spec. 없음
N-05 |  |  |  | GALV. EXPANDED METAL LATH - FOR ROOF WALKWAY - HOT DIP GALVANIZED (4 MILS, 100 MICRONS) - FACTORY APPLIED FINISH COATING - INCLUDING EDGE FRAME,FIXING CLAMP - INCLUDING FIXING ANGLE, ANCHOR BOLT FOR FIXING ANGLE - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-06 |  |  |  | GALV. MESH SCREEN & DOOR - FOR CABLE ROOM, TR AREA - HOT DIP GALVANIZED (4 MILS, 100 MICRONS) - FACTORY APPLIED FINISH COATING - REMOVABLE TYPE - INCLUDING GALV. MESH DOOR, BIRD SCREEN, MESH PANEL FRAMES, - INCLUDING ALL FIXING, ACCESSORIES, HARDWARE AND PAD LOCK - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-07 |  |  |  | ALUMINIUM SHEET - THK. 3 mm AL. SHEET - DOUBLE PROFILE THK. 75mm - INCLUDING ALL ACCESSORIES FOR FIXING, SEALANT, ETC. - INDLUD'G FIXING & JOINTING - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-08 | STEEL HANDRAIL | W/ PAINT (OR) HOT DIP GALVANIZED. | 0.9444% | STEEL PIPE HANDRAIL (STAND TYPE) - RAILING PIPE : INTERNAL DIA. Φ32mm, THK.4 mm - TOP RAIL HEIGHT : WALKWAY & PLATFORM - 1100 mm : STAIR - 900 mm - 2 INTEMEDIATE HORIZONTAL RAILS - PIPE POST SPACING @ 1200 mm - HOT DIP GALVANIZED AND INORGANIC ETHYL ZINC SILICATE(1COAT) - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING TOE PLATE OR CHANNEL - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING | • Pipe handrail shall conform to ASTM A53, Type E or S, Grade B. Top rails, mid rails and posts shall be 32 mm nominal diameter standard (schedule 40) pipe. • Platform handrail shall have one intermediate rail with centerline at 550 mm above the finished floor level and a second rail with top elevation at 1100 mm above the finished floor. Handrail posts shall be spaced not more than 1.8 meters center to center. • Handrail shall be of welded construction. Rail and post joints shall be welded and ground smooth. Rails shall be continuous. Exposed ends of pipe shall be closed by welding a 5 mm steel plate in place or using prefabricated fittings. • Toe plate, 100 mm high, shall be furnished with handrail except for stairs and at sides of platforms and walkways where channels extend 100 mm above the top of grating. |  |  | STEEL PIPE HANDRAIL - RAILING PIPE : DIA. Φ42.7mm / 난간(Handrail) 및 난간동자(Baluster) | STEEL PIPE HANDRAIL - RAILING PIPE TOP BAR : DIA. Φ42.7mm, THK.2 mm POST : DIA. Φ34mm, THK.2 mm MID BAR : DIA. Φ27.2mm, THK.2 mm - PIPE POST SPACING @ 1200 mm | Rail 직경 42.7mm 두께검토 후 명시 Post 직경검토
N-09 |  |  |  | STEEL PIPE HANDRAIL (REMOVABLE TYPE) - RAILING PIPE : INTERNAL DIA. Φ32mm, THK.4 mm - PIPE POST SPACING @ 1200 mm - HOT DIP GALVANIZED AND INORGANIC ETHYL ZINC SILICATE(1COAT) - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING
N-10 |  |  |  | STAINLESS STEEL HANDRAIL - AS PER ASTM A500-01a & ASTM A53/A53M-01 - ROUND OR SQUARE : POST - DIA. Φ32mm / SQUARE □40, THK.4 mm : INTERMEDIATE RAIL-DIA. Φ32mm, SQUARE□30 - TOP RAIL HEIGHT : 900mm - 2 INTERMEDIATE HORIZONTAL RAILS - PIPE POST SPACING @ 1200 mm - INCLUDING FIXING AND ACCESSORIES - INCLUDING TOE PLATE OR CHANNEL - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-11 |  |  |  | STAINLESS STEEL HANDRAIL (WOODEN GRIP) - AS PER ASTM A500-01a & ASTM A53/A53M-01 - ROUND OR SQUARE : POST - DIA. Φ32mm / SQUARE □40, THK.4 mm : INTERMEDIATE RAIL-DIA. Φ32mm, SQUARE□30 - TOP RAIL HEIGHT : 900mm - 2 INTERMEDIATE HORIZONTAL RAILS - PIPE POST SPACING @ 1200 mm - 45x150mm, HARDWOOD GRIP
N-12 |  |  |  | LADDER (H ≤ 2.5m) - LADDER : WIDTH - 400 mm : SIDE RAIL - ANGLE L60/8 or L75/10 : RUNG - Φ25 RIBBED BAR @280 - HOT DIP GALVANIZED AND INORGANIC ETHYL ZINC SILICATE(1COAT) - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-13 | CAGED LADDER(2.5m < H ≤ 10m) | W/ PAINT (OR) HOT DIP GALVANIZED. | 0.1% | CAGE LADDER (2.5m < H ≤ 10m) - LADDER : WIDTH - 400 mm : SIDE RAIL - ANGLE L60/8 or L75/10 : RUNG - Φ25 RIBBED BAR @280 - CAGE : DIAMETER 700 mm : CAGES STARTING 2.5m ABOVE G.L OR F.L : HORIZONTAL HOOP - F.B 55x6 mm @1.5m : VERTICAL HOOP - 5 EQUALLY SPACED - HOT DIP GALVANIZED AND INORGANIC ETHYL ZINC SILICATE(1COAT) - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING | All ladder supports shall be shaped steel and shall be spaced vertically at a maximum of 3 meters. Steel ladders shall be fabricated with dimensions, spacings, details, and anchorage as indicated in the Engineering Drawings and in compliance with ANSI A14.3. Each ladder shall be supported at topand bottom and at intermediate points spaced no more than 1.53 m on center. Welded or bolter steel brackets shall be designed for adequate support and anchorage, and to hold the ladder 150 mm (6 in.) from the wall surface and other obstructing construction. Safety cage shall be required when the ladder is higher than 6 m. The bottom of the safety cage to finished floor shall be 2m minimum. |  |  | - | -
N-14 | CAGED LADDER(10.0m < H) | W/ PAINT (OR) HOT DIP GALVANIZED. | 0.2% | CAGE LADDER (10.0m < H) - LADDER : WIDTH - 400 mm : SIDE RAIL - ANGLE L60/8 or L75/10 : RUNG - Φ25 RIBBED BAR @280 - CAGE : DIAMETER 700 mm : CAGES STARTING 2.5m ABOVE G.L OR F.L : HORIZONTAL HOOP - F.B 55x6 mm @1.5m : VERTICAL HOOP - 5 EQUALLY SPACED - HOT DIP GALVANIZED AND INORGANIC ETHYL ZINC SILICATE(1COAT) - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING | All ladder supports shall be shaped steel and shall be spaced vertically at a maximum of 3 meters. Steel ladders shall be fabricated with dimensions, spacings, details, and anchorage as indicated in the Engineering Drawings and in compliance with ANSI A14.3. Each ladder shall be supported at topand bottom and at intermediate points spaced no more than 1.53 m on center. Welded or bolter steel brackets shall be designed for adequate support and anchorage, and to hold the ladder 150 mm (6 in.) from the wall surface and other obstructing construction. Safety cage shall be required when the ladder is higher than 6 m. The bottom of the safety cage to finished floor shall be 2m minimum. |  |  | - | -
N-15 | STEEL BOLLARD | GUARD POST, CONCRETE FILL. | 0.02836% | BOLLARD - REMOVABLE(DE-MOUNTED) - STEEL PIPE H 1000MM Φ 150 MM & REMOVAL - STEEL PIPE FILLIED CONCRETE & FOUNDATION - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING |  |  | 스피드셔터 설치 내외부 차량충돌 방지용 가드 포스트 설치 | - | - | 전체 적용
N-16 |  |  |  | BOLLARD -FIXED - STEEL PIPE H 1000MM Φ 150 MM & REMOVAL - STEEL PIPE FILLIED CONCRETE & FOUNDATION - PAINT : EPOXY HIGH SOLID (125㎛) AFTER MECHANICAL CLEANING - INCLUDING FIXING AND ACCESSORIES - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
N-17 |  |  |  | DOWEL BAR - PLAIN STEEL DOWEL ROUND BARS DIA. 20mm, L 600mm, @300 - FOR SEPARATION JOINT - INCLUDING DOWEL CAP FILLED WITH COMPRESSIBLE MATERIAL FOR SLIP PURPOSE
N-18 | STEEL FORM | FOR CEP | 0.008219% | STEEL FORM - FOR CEP(Condensate Extraction Pump) STEEL PIPE CAN STRUCTURE FOR STEAM TURBINE BUILDING - STEEL PIPE DIA 1000mm x 10t, L=9m - STEEL PLATE 1000 x 1000 x 10t WITH ANCHOR BOLT - INCLUDING ANCHORING - INCLUDING TAR EPOXY COATING (250 micron) - INCLUDING FRAME AND ACCESSORIES - INCLUDING WEDLING STEEL PIPE ON STEEL PLATE |  |  |  | - | -
O-01 | ISOLATION JOINT (SEPARATION JOINT) | FOR EQUIPMENT FOUNDATION | 0.03133% | ISOLATION JOINT - FOR AROUND TG FDN. - THK. 50 x 50 OIL RESISTANT SEALANT W/ BACKING ROD FORM - AS PER BS 6093 - INCLUDING PREMOULDED FILLER |  |  |  | - | -
O-02 |  |  |  | EXPANSION JOINT - FOR EXT. / INT. FLOOR AND WALL - THK. 25 x 25 OIL RESISTANT SEALANT W/ BACKING ROD FORM - AS PER BS 6093 - INCLUDING PREMOULDED FILLER
O-03 |  |  |  | EXP. JOINT COVER W=200 - FOR 25mm FLOOR EXP. JOINT COVER - INCLUDING FIXING BY NON-CORRODING & HEAVY DUTY ALUMINUM PROFILE WITH RUBBER INSERT - INCLUDING PREMOULDED FILLER
O-04 | ISOLATION JOINT (SEPARATION JOINT) | FOR SLAB+TIE GIRDER, | 0.05345% | SEPARATION JOINT - FOR AROUND GRADE SLAB - THK. 12 x 12 / SEALANT W/ BACKING ROD FORM - AS PER BS 6093 - INCLUDING PREMOULDED FILLER |  |  |  | - | -
O-05 |  |  |  | CONTRACTION JOINT (FOR FLOOR) - FOR FLOOR OF HEAVY DUTY TRAFFIC - THK. 6 x 6, OIL RESISTANT SEALANT W/ BACKING ROD FORM - INCLUDING SAW CUTTING OF CONC.
O-06 |  |  |  | CONTRACTION JOINT (FOR WALL) - FOR VERTICAL & HOR. WALL JOINT - THK.10 x 10, 2-PART POLYSULPHIDE BASED SEALANT W/ BACKING ROD FORM
O-07 |  |  |  | PREMOULDED FILLER - THK. 50mm - FOR ISOLATION JOINT
O-08 |  |  |  | PREMOULDED FILLER - THK. 25mm - FOR EXPANSION JOINT
O-09 |  |  |  | PREMOULDED FILLER - THK. 12mm - FOR SEPARATION JOINT
O-10 |  |  |  | EMERGENCY MANHOLE COVER - POWER OPERATED - SIZE 800 x 800 - INCLUDING FRAME & ALL ACCESSORIES
O-11 |  |  |  | FIRE RATED MANHOLE COVER - 1.5 HOURS FIRE RESISTANCE - SIZE 800 x 800
O-12 |  |  |  | CORNER PROTECTION H=1.2M - PLASTIC OR ALUMINUM - PROTECTION OF EXPOSED EDGE OF CONC./ PLASTER UP TO 1.2M FROM FLOOR LEVEL
O-13 |  |  |  | STAIR NOSING - AL W/ PLASTIC OR RUBBER INSERT - W=50mm - INCLUDING ALL ANCHORS
O-14 |  |  |  | BLIND - INCLUDING BLIND BOX AND ALL HARDWARES
O-15 |  |  |  | ROOM DESIGNATION SIGN - INTERNAL / EXTERNAL - SIZE : 260 x 100 x 4mm - ALUMINIUM ANODIZED PLATE W/ SPECIALLY TREATED SURFACE - 4 HORIZONTAL GROOVES, 10mm WIDE AT LOWER END OF PLATE TO TAKE PLASTIC STRIP - DESIGNATION PRINTED IN ENGLISH & LOCAL LANGUAGE - ROOM NUMBER ENGRAVED AT UPPER PORT - INCLUDING FIXING BY NON-CORRODING SCREW ON WALL
O-16 |  |  |  | SHOWER TRAY - ACRYLIC, SIZE : 900x900x150, FOR SHOWER - INCLUDING FIXING & ACCESSORIES
O-17 | VANITY TOP | L=750MM (1 BOWL) | 0.006473% | VANITY TOP - L=750MM (1 BOWL) - ACRYLIC, 4" FRONT/BACK SPLASH - FOR TOILET, WITHOUT BOWL - INCLUDING FIXING & ACCESSORIES |  |  | <소변기, 대변기 선반> THK.20 인조대리석 (W=200) <세면대 수전1개> 그라나이트 아이스버그 G113, 12T 800x560 | - | - | 현대차 사양 적용
O-18 | VANITY TOP | L=1500MM (2 BOWL) | 0.1027% | VANITY TOP - L=1500MM (2 BOWL) - ACRYLIC, 4" FRONT/BACK SPLASH - FOR TOILET, WITHOUT BOWL |  |  | <세면대 수전2개> 그라나이트 아이스버그 G113, 12T 1500x600 | - | - | 현대차 사양 적용
O-19 |  |  |  | MIRROR - 750Wx800Hx5T - FOR TOILET - INCLUDING FIXING & ACCESSORIES
O-20 |  |  |  | MIRROR - 1500Wx800Hx5T - FOR TOILET - INCLUDING FIXING & ACCESSORIES
O-21 |  |  |  | TOWEL BAR - STAINLESS STEEL - INCLUDING FIXING & ACCESSORIES
O-22 |  |  |  | SOAP DISPENSER - STAINLESS STEEL - INCLUDING FIXING & ACCESSORIES
O-23 |  |  |  | ROLLER PAPER HOLDER - STAINLESS STEEL - BALL-JOINT TYPE - INCLUDING FIXING & ACCESSORIES
O-24 |  |  |  | NON-SLIP NOSING - STAINLESS STEEL NON-SLIP NOSING - FOR COVERING OF EXPOSED EDGE FOR P.V.C. TILE - INCLUDING FIXING BY SCREW
O-25 |  |  |  | SST'L DIVIDING STRIP - GRADE 316L OR BETTER - EMBEDDED ITEMS SUCH AS PLATE, BENT PLATE, ANCHOR BOLTS & NUTS, ANGLE, SLEEVE, FIXING ELEMENTS, ETC. - FOR OUTSIDE CONDITION - FOR INSIDE CONDITION W/ SEA WATER WETTING, CHEMICALS, ETC. - INCLUDING MATERIAL, EQUIPMENT FOR ERECTION - INCLUDING AS PER APPROVED SHOP DRAWING
P-01 |  |  |  | RCC PAVE PLINTH PROTECTION (FOOTWAY) - THK. 100MM, CONCRETE WIDE 1500MM - SURROUNDING THE BUILDING - INCLUDING ONE LAYER OF WIRE MESH REINFORCEMENT
P-02 |  |  |  | INTERLOCKING PAVING - BLOCK THK. 80mm (MIN.) - SAND BEDDING THK. 50mm - COMPACTION THK. 300mm - COMPACTION OF FORMATION SAME AS ROAD - INCLUDING CONCRETE KERB AT EDGE - CONFORMING TO ASTM C 936, HEAVY/MEDIUM DUTY TYPE - LEVELING BASE WITH SOIL STERILIZER - LAYING ON SAND BEDDING OVER AN AGGREGATE BASE/SUB-BASE MATERIAL - COLOUR MATCHING WITH ADJACENT BUILDINGS
P-03 | CHAINLINK FENCE |  | 0.06824% | CHAIN LINK FENCE - 2.4M HIGH GALVANIZED STEEL WIRE PVC - INCLUDING APPROXIMATELY 50mm DIAMOND MESH PATTERN AND 45 DEGREE TO VERTICAL - MIN. BREAKING STRENGTH OF MESH WIRE : 585kg - MIN. THICKNESS OF PVC : 0.38mm - TO KEEP COLOUR WITH GREEN - INCLUDING FOUNDATION |  |  |  | - | -
P-04 | CHAINLINK GATE |  | 0.01438% | CHAIN LINK GATE - HEIGHT 2.4m / WIDTH 6.0m - FOR GPRS AREA, OUTDOOR STORAGE AREA - DOUBLE WING GATE - PLASTIC COATED GALVANIZED CHAIN LINK MESH ON A PLASTIC COATED GALVANIZED STEEL FRAME - INCLUDING THREE STRANDS OF GALVANIZED BARBED WIRE ACROSS THE TOP ON CRANKED GALVANZIED EXTENSION POSTS. - INCLUDING A VERTICAL DROP BOLT ON EACH LEAF - INCLUDING ALL HARDWARE AND PAD LOCK (GALVANIZED) - INCLUDING FOUNDATION |  |  |  | - | -
Q-01 |  |  |  | DRIVEN PC PILE - SQUARE 400 X 400 mm, L =20m - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE V - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK
Q-02 | PHC PILE (D400) | INCLUDING PRE-BORING | 0.7231% | DRIVEN PHC PILE (D400) - 말뚝길이 : 본당 40m - PHC 말뚝 자재비, 천공, 항타, 두부보강, 두부정리, 말뚝이음, 하차비 (Φ400x65t) 포함 - 시멘트 페이스트 채움 (W/C=83%) 포함 - 케이싱 자재비 (강관 457.2x9t, 99.5kg/m) 포함 - 고재처리 (케이싱) 포함 - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE V - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK |  |  | * 파일 설계 관련사항 기술 - 파일 시공순서, 파일 종류별 비교, 파일 재하시험, 파일 기초상세, 파일 오차 기준, 파일 보강방법 | - | -
Q-03 | PHC PILE (D500) | INCLUDING PRE-BORING | 15.77% | DRIVEN PHC PILE (D500) - 말뚝길이 : 본당 40m - PHC 말뚝 자재비, 천공, 항타, 두부보강, 두부정리, 말뚝이음, 하차비 (Φ500x80t) 포함 - 시멘트 페이스트 채움 (W/C=83%) 포함 - 케이싱 자재비 (강관 558.8x9t, 122.0kg/m) 포함 - 고재처리 (케이싱) 포함 - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE V - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK |  |  | * 파일 설계 관련사항 기술 - 파일 시공순서, 파일 종류별 비교, 파일 재하시험, 파일 기초상세, 파일 오차 기준, 파일 보강방법 | - | PHC PILE (D500) : Building 강관말뚝 (D508×12T) : GTG, STG
Q-04 | PHC PILE (D600) | INCLUDING PRE-BORING | 6.626% | DRIVEN PHC PILE (D600) - 말뚝길이 : 본당 40m - PHC 말뚝 자재비, 천공, 항타, 두부보강, 두부정리, 말뚝이음, 하차비 (Φ600x90t) 포함 - 시멘트 페이스트 채움 (W/C=83%) 포함 - 케이싱 자재비 (강관 700.0x9t, 153.0kg/m) 포함 - 고재처리 (케이싱) 포함 - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE V - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK |  |  | * 파일 설계 관련사항 기술 - 파일 시공순서, 파일 종류별 비교, 파일 재하시험, 파일 기초상세, 파일 오차 기준, 파일 보강방법 | 강관말뚝 (D609.5×12T) | -
Q-05 |  |  |  | DRIVEN STEEL PILE - STEEL PILE DIA 609.6 x T12MM, L=20m - INSTALLATION TYPE FOR PILE : DRIVING - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE JONTS, TOES, HEAD REINFORCEMENT IF REQUIRED - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK
Q-06 |  |  |  | BORING PC PILE - DIA 400mm, L =20m - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE I - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK - INCULDING PRE-BORING AND ALL ACCESSORY WORK
Q-07 |  |  |  | BORED CAST IN-SITU PILE - 말뚝길이 : 본당 40m - DIA 600mm (STRUCTURAL PROPERTIES : GRADE 80 AND CLASS C) - 현장타설 말뚝 천공 / 말뚝 조성(철근망 근입, 콘크리트 타설) / 말뚝 두부보강 / 말뚝 두부정리 포함 - SLURY 공급설비, SLIME처리, CASING설치 및 인발 등 부대공사 포함 - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE I - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK - INCULDING PRE-BORING AND ALL ACCESSORY WORK
Q-08 |  |  |  | BORED CAST IN-SITU PILE - DIA 400mm, L =20m - INCLUDING MOBILIZATION, SHIFTING AND DEMOBILIZATION OF AUGER / PILE RIG / CRANE / ANY RELATED MACHINE FOR THE PILING WORK. - SOCKETING INTO ROCK LAYER - INCLUDING MATERIAL LOADING / UNLOADING / CONTROL / HANDLING - INCLUDING LEADING. LIFTING, INSTALLATION OF MATERIALS - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING ALL NECESSARY TESTS / CERTIFICATES - ALL MATERIALS AND WORKS INCLUDING DRILLING, CONCRETING AND REINFORCEMENT WORKS AND ETC - INCLUDING THE FABRICATION AND INSTALLATION OF REINFORCEMENT CAGE - TEMPORARY STEEL CASING TO STABILIZE THE BOREHOLE - INCLUDING VERTICALITY CHECK FOR ALL PILES - INCLUDING TREATMENT AND DISPOSAL OF SLIME, MUCK AND SOIL DURING DRILLING - SONIC LOGGING TUBES : FOUR (4) STEEL PIPES OF INTERNAL DIA. NOT LESS THAN 50mm FOR ENTIRE LENGTH OF PILE TO BE INSTALLED IN ALL PILES - INCLUDING PILE HEAD CUTTING AT PILE CUT OFF LEVEL AND CONNECTION WITH PILE CAP - CONCRETE ASTM C150 TYPE V, f'c = 35MPa - RE-BAR ASTM A615 GRADE 60 - INCLUDING PVC PIPE FOR CAPPING RE-BAR TO SERVE PILE HEAD CUTTING'S CONVENIENCE - INCLUDING ANY TEMPORARY ASSOCIATED WORK
Q-09 |  |  |  | BORED CAST IN-SITU PILE - 말뚝길이 : 본당 40m - DIA 800mm (STRUCTURAL PROPERTIES : GRADE 80 AND CLASS C) - 현장타설 말뚝 천공 / 말뚝 조성(철근망 근입, 콘크리트 타설) / 말뚝 두부보강 / 말뚝 두부정리 포함 - SLURY 공급설비, SLIME처리, CASING설치 및 인발 등 부대공사 포함 - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE I - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK - INCULDING PRE-BORING AND ALL ACCESSORY WORK
Q-10 |  |  |  | BORED CAST IN-SITU PILE - 말뚝길이 : 본당 40m - DIA 1000mm, (STRUCTURAL PROPERTIES : GRADE 80 AND CLASS C) - 현장타설 말뚝 천공 / 말뚝 조성(철근망 근입, 콘크리트 타설) / 말뚝 두부보강 / 말뚝 두부정리 포함 - SLURY 공급설비, SLIME처리, CASING설치 및 인발 등 부대공사 포함 - COMPRESSIVE STRENGTH : f'c = 35MPa, RE-BAR ASTM A615M GRADE 60 - MAX. WATER-CEMENT RATIO : 0.4 - ORDINARY PORTLAND CEMENT COMFORMING TO ASTM C150 TYPE I - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING MOBILIZATION AND DEMOBILIZATION OF PILE RIG - LEADING, LIFTING, INSTALLATION OF PILE - INCLUDING PILE HEAD CUTTING, SHOE AND HEAD REINFORCING - INCLUDING PILE JONTS - INCLUDING PILE INTEGRITY TEST - INCLUDING ANY TEMPORARY ASSOCIATED WORK - INCULDING PRE-BORING AND ALL ACCESSORY WORK
Q-11 |  |  |  | SHEET PILE - INSTALLATION TYPE FOR PILE : DRIVEN - U-TYPE SHEET PILE (SP-IV 400 X 170 X15.5) - L=8M - INCLUDING ALL MATERIAL, EQUIPMENT AND LABOR - INCLUDING EQUIPMENT ASSEMBLING & DISMANTLING COST - INCLUDING ANY TEMPORARY ASSOCIATED WORK - REPLACEMENT OF REJECTION PILES AT NO EXTRA - INCLUDING WALE, STRUT, POST PILE, JACK
R-01 |  |  |  | HARD WOOD DESK - 1600 x 700 x 800 mm - COMMON DESK - INCLUDING DRAWERS (MATCHING THE DESK) & GLASS TOP
R-02 |  |  |  | HARD WOOD DESK - 1300 x 1300 x 800 mm - CANTEEN TABLE
R-03 |  |  |  | SIDE TABLE - 1600 x 500 mm - INCLUDING DRAWERS (MATCHING THE DESK) & GLASS TOP
R-04 |  |  |  | CHAIR - HIGH BACKED EXECUTIVE - ADJUSTABLE SWIVEL
R-05 |  |  |  | CHAIR - ADJUSTABLE SWIVEL
R-06 |  |  |  | CANTEEN CHAIR - NON-SWIVEL
R-07 |  |  |  | COUCH - REST ROOM
R-08 |  |  |  | VISITOR - NON-SWIVEL
R-09 |  |  |  | SMALL FOR COMPUTER TABLE -SWIVEL
R-10 |  |  |  | CORRESPONDENCE TRAY
R-11 |  |  |  | WASTE BIN
R-12 |  |  |  | WALL BOARD
R-13 |  |  |  | SECRETARIAL WORK STATION
R-14 |  |  |  | COMPUTER TABLE - 700 x 1600 x 800 mm
R-15 |  |  |  | SIDE STORAGE UNIT - 800 x 425 x 725 mm
R-16 |  |  |  | CONFERENCE ROOM PACKAGE - TABLE, CHAIRS, WHITE BOARD - LAMINATED OR WOOD VENEER - HIGH QUALITY - LARGE TABLE FOR 20 PERSON + 20 SEATING - 1 BEAM PROJECTOR & 1 SCREEN - SIZE TO SUIT THE CONFERENCE ROOM
R-17 |  |  |  | MANAGEMENT OFFICE PACKAGE - PLANT MANAGER OFFICE - TABLE, SIDE TABLE, STDE STORAGE UNIT & HIGH BACKED CHAIR - SPECIAL SELECTION OF HIGHER QUALITY MODERN OFFICE PACKAGE
R-18 |  |  |  | TRAINING ROOM PACKAGE - CHAIR WITH FOLDING TABLE, WHITE BOARD - SEATING FOR 40 PERSONS - TO SUIT THE TRAINING ROOM
R-19 |  |  |  | OFFICE STORAGE ROOM PACKAGE - FILING CABINETS, STORAGE SHELVES, DRAWING HOLDERS - TO SUIT THE STORAGE ROOM
R-20 |  |  |  | COFFEE SHOP & KITCHEN - 2 GAS STOVE W/ 4 BURNER & 1 OVEN - 3 SECTIONAL WASHING TANK WITH RACK - 1 REFRIDGERATING CABINET (1600 x 725 x 1950 mm) - 4 PROCESS TABLE (1300 x 800 x 860 mm) - STATIONARY RACK (1500 x 500 x 1200 mm) - COUNTER FOR SERVER & TRAY
R-21 |  |  |  | RECEPTION AREA - RECEPTION DESK, SOFA SEATS & COFFEE TABLE - FOR 6~10 PERSONS -TO SUIT DESIGNATED AREAS
R-22 |  |  |  | BUILT-IN CUPBOARD - FOR OFFICE - HEIGHT : UP TO CEILING (≒CUPBOARD 2.3m+COVER STRIP 0.5m) - SIZE : 500 x 2600 x 1800 mm - COMPONENTS : CUPBOARDS, WARDROBES, SHELVES & DRAWS -COMPONENT DESIGN BY VENDOR
R-23 |  |  |  | TEA KITCHENS - COOKTOP & HOOD - CUPBOARD W/STAINLESS STEEL SINK
R-24 |  |  |  | OTHERS(FURNITURE) - WOOD LOCKER (500 x 500 x 1800 mm)
<검토사항> 1. 방음설계 Case별 검토 후 물량 2. 방진설계 방진패드 설치고려 X 3. 장애인편의시설 설계 - 적용여부 검토 4. 용도별 마감기준 마감 타입별 조합이 정해져있는듯 5. 방풍실 적용여부 방풍실 미적용 6. 기계실, 전기실 천정재 PE흡음재 / 고밀도부직포 적용여부 - 미적용